## CMS Sweeps
Site: | Owner | Turbines | MB Sweep | Next MB Sweep | S1 Sweep | Next S1 Sweep | S2 Sweep | Next S2 Sweep | S3 Sweep | Next S3 Sweep | Last Login | Notes: | Component: | Frequency (Days):
Asa Branca | ESSEN |  | 2025-12-01 | 2026-03-01 | 2026-01-06 | 2026-04-06 | 2025-07-29 | 2026-01-25 |  | 2026-01-25 | 2026-09-18 |  | ZF S1+S2 | 30
Beech Ridge II | A | 20 | 2026-07-30 | 2026-09-28 | 2026-07-20 | 2026-10-18 | 2026-08-28 | 2026-12-26 | 2026-09-22 | 2027-03-21 | 2026-09-22 |  | 1st Planetary Stage | 90
Bethel | A | 120 | 2026-05-01 | 2026-06-30 | 2025-09-02 | 2025-12-01 | 2025-08-04 | 2025-12-02 | 2025-07-21 | 2026-01-17 | 2026-09-22 |  | 2nd Planetary Stage | 120
Bishop Hill III | WEC | 53 | 2025-08-04 |  | 2025-08-07 |  | 2025-08-18 |  | 2025-08-21 |  | 2025-09-15 |  | High Speed Stage | 180
Blooming Grove | WEC | 94 | 2025-08-04 |  | 2025-08-07 |  | 2025-08-18 |  | 2025-08-21 |  | 2025-09-15 |  | SKF + Timken MBs | 7
Chapada I | ESSEN |  |  | 1900-03-30 | 2025-07-29 | 2025-10-27 |  | 1900-06-28 |  | 1900-06-28 | 2026-09-18 |  | MB | Varies
Chapada II+III | ESSEN |  |  | 1900-03-30 |  | 1900-03-30 |  | 1900-06-28 |  | 1900-06-28 | 2026-08-17 |  | CMS Server Login | 3
Chickasaw | A | 58 | [8 empty] | 2026-09-11
Coyote | WEC | 39 | 2025-08-04 |  | 2025-08-01 |  | 2025-08-18 |  | 2025-08-22 |  | 2025-09-15
Deuel Harvest | A | 109 | 2026-06-15 | 2026-07-15 | 2026-07-20 | 2026-10-18 | 2026-09-22 | 2027-01-20 | 2026-06-19 | 2026-12-16 | 2026-09-22
Diversion | AEP | 59 | [8 empty] | 2026-09-11
Gordon Butte | A | 9 | 2026-07-30 | 2026-08-29 | 2026-07-20 | 2026-10-18 | 2026-09-22 | 2027-01-20 | 2026-07-06 | 2027-01-02 | 2026-09-22
Jayhawk | WEC | 70 | 2025-08-04 |  | 2025-08-07 |  | 2025-08-18 |  | 2025-08-22 |  | 2025-09-15
Number Three (GE) | WEC | 5 | 2026-08-31 | 2026-09-30 | 2026-08-03 | 2026-11-01 | 2026-09-22 | 2027-01-20 | 2026-08-17 | 2027-02-13 | 2026-09-22
Plymouth | A | 73 | [8 empty] | 2026-09-22
Red Barn | WEC | 28 | [8 empty] | 2026-09-22
Rock Creek | A | 32 | [8 empty] | 2026-09-11
Santa Rita East | A | ` | 2025-11-21 |  | 2025-12-01 |  |  | 2025-12-01 |  | 2025-12-01 | 2025-12-29
Tatanka | WEC | 56 | 2025-08-05 |  | 2025-08-08 |  | 2025-08-18 |  | 2025-08-22 |  | 2025-09-15
Thunderhead | WEC | 108 | 2025-08-05 |  | 2025-08-08 |  | 2025-08-18 |  | 2025-08-22 |  | 2025-09-15
Upstream | WEC | 82 | 2025-08-05 |  | 2025-08-08 |  | 2025-08-18 |  | 2025-08-22 |  | 2025-09-15
3041238
Formulas:
Next MB Sweep = Table11[[#This Row],[MB Sweep]]+90
Next S1 Sweep = Table11[[#This Row],[S1 Sweep]]+90
Next S2 Sweep = Table11[[#This Row],[S2 Sweep]]+180
Next S3 Sweep = Table11[[#This Row],[S2 Sweep]]+180

## Events
Site | Case Status | WTG | Case Title | Event | Location | Event Date | Follow Up Date | Priority | Disposition | Action | WO Tracking2 | EAM WO Status | WO Status | Estimated Replacement Date: | Date Resolved | Notes | Notes Archive | Case outcome | Detection Time:
Bethel | Resolved | 1 | Gen Bearing Damage | Alarm | Generator Outboard | 2023-04-17 |  | 3 | Add grease to both gen bearings, increasing trend | Monitor | 3113598 | Closed | Closed |  | 2023-09-08 |  |  | Defect Confirmed - Repair Complete | 144
Plymouth | Resolved | 1 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-04-10 |  | 3 | Please inspect keyphasor system using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3110510 | Closed | Closed |  | 2023-07-08 |  |  | Defect Confirmed - Repair Complete | 89
Plymouth | Active | 1 | Timken Main Bearing BS2X Issue | Warning | Main Bearing | 2024-09-10 |  | 2 | 9/26/24 - Turbine derated to 50%. 9/10/24 - Recommend borescoping this main bearing within 2 weeks from 9/10/24 with focus on outer race and rollers. | Repair Pending | 3420487 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45545
Plymouth | Resolved | 1 |  | Instrumentation | CMS Monitor | 2022-06-03 |  |  | Replace 60M100 monitor | CMSTRBLSHOOT | 2941638 | Cancelled | Cancelled |  | 2022-08-29 | 8/29 - do not replace monitor if 319 event left state |  |  | 87
Santa Rita East | Resolved | 1 |  | Particle Count | 1st Planetary Stage | 2022-03-16 |  | 5 |  | Particle Counter | [5 empty] | 3/16 - looking back at particle counter data shows rapid increase in non-ferrous debris July-October 2021, plateaued since. No notable signs of gearbox damage in CMS, potential oil contamination or housing damage? Monitor for signs of damage in CMS, 4/4 - non ferrous counts continue to increase, 6/3 - no smoking gun in CMS, Stage 3 FFT shows pinion fault sidebands, no progression, 8/8 - non ferrous debris counts continue to increase, gearbox borescoped 5/20/22 with no damage found, monitor for continued debris generation, 11/3 - reduce to cat 1, limited debris generation |  | Case In Progress | -44636
Santa Rita East | Resolved | 1 |  | Alarm | Generator Inboard | 2022-01-04 |  | 6 |  | Monitor | [5 empty] | 1/12 - Sudden spike to alarm thresholds on 1/4, return to apparently normal operation. CMS Gen Bearing check if alarm is hit again. Monitor for failure 1/31 - signal has reduced to below alarm levels, FFT shows signs of damage to both inner and outer races, 4/25 - reduce to cat 2, 6/3 - no progression, 9/19 - recent progression, 11/3 - limited progression, reduce to cat 1 |  | Case In Progress | -44565
Maverick | Active | 1 | Potential Main Bearing Issue | Sweep | Main Bearing | 2023-10-03 |  | 1 | 2/22/24 - Turbine to be DNR'd and reborescoped before repair. 1/9/24 - Derated to 60%. 10/27/24 - Derated to 50%. 10/6/23 - Borescope found excessive damage found on rolling elements and aggressive wear seen on cage fingers. 10/2/23 - Recommend thrust derating and performing a borescope of the main bearing at the next possible opportunity. | Final Report Needed | 3303924 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45202
Upstream | Active | 1 | S1 PS BRG Damage | Warning | 1st Planetary Stage | 2021-12-12 |  | 1 | CMS indicated damage to S1 Planetary. Continue to monitor via CMS and particle counter | Longterm Watchlist | 2928225 | Closed | Closed | Q4 2024 |  | 6/17 - borescope found corrosion and micropitting on S1 PS BRG RS, indents on S1 PC BRGs, projected failure Q1/Q2 2023, planning to move particle counter from 16 to 1 after 16 is replaced, CMS indicates damage to stage 2 as well, 7/5 - additional Ring Fault alarm on 6/26, indicating progression, waiting on particle counter install, 9/6 - particle counter installed, 0-100 micron debris generation, monitor larger bins, 9/29 - S1 Direct now below the warning setpoint, 10/19 - 43mg debris detected, limited progression, 12/19 - 69mg detected, 1/10 - progression has slowed, | 12/29 - potential issue with stage 1 carrier bearing, monitor, 3/25 - progression in stage 1 direct, FFT shows GS carrier faults, 4/6 - Nanjing retro, monitor for progression, 5/5 - progression continues, FFT shows strong 3X harmonics throughout the spectrum, indicating damage to stage 1 carriers and ring gear, | Defect Confirmed - Awaiting Repair | -44542
Sundance | Resolved | 2 | IONet Issue | Instrumentation | CMS Monitor | 2023-07-25 |  | 5 | ​CMS monitor not receiving power signal, please perform toolbox download to CBM card. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3161674 | Closed | Closed |  | 2023-08-31 |  |  | Defect Confirmed - Repair Complete | 37
Bethel | Resolved | 2 |  | Alarm | Helical High Speed Stage | 2021-12-28 |  | 3 |  | Borescope | Create WO |  | #N/A |  | 2023-01-25 | 1/31 - stage 3 direct peaked above the alarm setpoint in early January, FFT shows peak at HSS DnWind Rear ORBP, recommending Borescope inspection focusing on HSS DnWind Rear bearing |  | Case In Progress | 393
Upstream | Resolved | 2 |  | Instrumentation | Generator Outboard | 2022-04-13 |  |  | Verify power supply and reboot | CMSTRBLSHOOT | 2920032 | Closed | Closed |  | 2022-09-14 |  | 7/5 - bad harness from sensor to TT OL, Dan is working on it? |  | 154
Bethel | Resolved | 2 | HSS Bearing Damage | Case Tracking | Helical High Speed Stage | 2023-01-26 |  | 3 | Check HSS bearing for damage | CMSHSS | [7 empty] | Case In Progress | -44952
Plymouth | Resolved | 2 | 1st Planetary Stage Accelerometer Issue | Instrumentation | 1st Planetary Stage | 2024-07-08 |  | 4 | 7/8/24 - Please investigate 1st planetary stage sensor wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | 3380402 | Closed | Ready to Schedule |  | 2024-07-16 |  |  | Defect Confirmed - Repair Complete | 8
Deuel Harvest | Active | 2 | Main Bearing BS2X, Rolling Element Issue | Sweep | Main Bearing | 2024-04-24 |  | 2 | 5/28/24 - Borescope shows moderate amount of indentstions with DLC delamination to the rollers. Main bearing can continue to operste as scope does not show evidence of imminent failure, and grease shows minmal wear metal, added to weekly monitoring. 4/24/24 - CMS indicates damage to rolling elements. Please perform main bearing borescope/inspection, take a grease sample, check vibration/sensors are tightly mounted. | Repair Pending | 3337119 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45406
Plymouth | Active | 2 | Timken Main Bearing Rolling Element Issue | Warning | Main Bearing | 2024-10-01 |  | 2 | 10/1/24 - Recommend borescoping this main bearing within 2 weeks from 10/1/24 with focus on outer race and rollers. Also recommending a 50% derate on this turbine to prolong bearing life. | Repair Pending | 3440359 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45566
Sundance | Active | 2 | Potential NTN Main Bearing Outer Race/Rolling Element Issue | Sweep | Main Bearing | 2024-03-19 |  | 2 | 5/6/24 - Turbine derated to 50%. 3/19/24 - Recommend main bearing borescope + grease purge with 2 weeks from 3/19/24. | Final Report Needed | 3319476 | Closed | Closed |  | 2024-04-28 |  |  | Defect Confirmed - Repair Complete | 40
Upstream | Resolved | 2 | Generator Outboard ORBP | Alarm | Generator Outboard | 2023-10-31 | 2024-04-20 | 3 | 3/19/24 - Component replaced as result of gen bearing campaign, CMS data received. 10/31/2023 - shows signature of gen outboard orbp issue continue to monitor via cms and particle counters, 11/1/23 - Please perform an auditory and visual inspection of the generator bearings: EAM - Found grease zerk was off, reconnected, is making an auditable noise when rotating, sensor is good, grease looks normal. - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection | Final Report Needed | 3217119 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -45230
Santa Rita East | Resolved | 3 |  | Alarm | Helical High Speed Stage | 2021-10-12 |  | 5 |  | Monitor | 2616804 | Closed | Closed |  |  |  | Alarms in stage 2 and 3 indicate damage that started on 9/30 in stage 2&3, 12/28 - waiting for inspection images in HUVR, several new events for both stage 2 and stage 3 planet and pinion faults, | Case In Progress | -44481
Bethel | Resolved | 3 | HSS Bearing Damage | Case Tracking | Helical High Speed Stage | 2023-02-09 |  | 3 | Check HSS Bearings for damage | Monitor | [7 empty] | Case In Progress | -44966
Deuel Harvest | Resolved | 3 |  | EOW | 1st Planetary Stage | 2022-10-13 |  | 1 |  | EOW Claim | [8 empty] | -44847
Deuel Harvest | Resolved | 3 |  | EOW | Main Bearing | 2022-10-13 |  | 1 |  | EOW Claim | [8 empty] | -44847
Bethel | Active | 3 | Main Bearing raceway damage | Case Tracking | Main Bearing | 2023-01-25 |  | 1 | (DNR) Main Bearing raceway damage, 50% power derate to extend life, scope confirmed failure, shutdown | Final Report Needed | 3096734 | Closed | Closed |  |  | CMSMB |  | Defect Confirmed - Awaiting Repair | -44951
Maverick | Resolved | 3 |  | Instrumentation | CMS Monitor | 2022-03-28 |  |  | Check CMS PLC monitor, may need replacement | CMSTRBLSHOOT | 2892344 |  | Cancelled |  | 2022-05-09 |  |  |  | 42
Upstream | Resolved | 3 |  | Warning | Generator Outboard | 2021-08-16 |  | 2 |  | Pending Replacement | 2575724 | Closed | Closed |  |  | 2022-03-25 |  | True Positive | -44424
Plymouth | Resolved | 3 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-11 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988827 | Cancelled | Cancelled | [5 empty] | -44784
Plymouth | Resolved | 3 | CMS Monitor Netcom/Keyphasor Issue | Instrumentation | CMS Monitor | 2024-08-05 |  | 3 | 8/5/24 - Not receiving data via Onyx Insight, please investigate if monitor is netcom or not receiving a speed signal. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3397301 | Closed | Closed |  | 2024-09-05 |  |  | Defect Confirmed - Repair Complete | 31
Bethel | Active | 3 | Generator Outboard IRBP | Warning | Generator Outboard | 2024-01-08 |  | 6 | 1/8/24 - Monitoring For direct increase. | Monitor | [7 empty] | Case In Progress | -45299
Upstream | Active | 3 | CMS troubleshoot data issue | Instrumentation | CMS Monitor | 2024-07-31 |  | 5 | 7/31/24 - CMS data not properly populating request for controller download | CMSTRBLSHOOT | 3395605 | Closed | Closed |  |  |  |  | Case In Progress
Sundance | Active | 3 | Main Bearing ORBP | Sweep | Main Bearing | 2023-12-15 |  | 2 | 3/28/24 - Turbine has been placed on DNR list. 1/17/24 - Secondary borescope scheduled to determine derate effectivness. 12/20/23 - Turbine continues to show large impacting during turbine startup and temps have degun to deviate, turbine derated to 35%. 12/15/2023 - Spectrum data shows main bearing outer race signature with direct increasing. Recommended action is to thrust derate, and inpection/borescope this main bearing | Final Report Needed | 3255284 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45275
Maverick | Active | 3 | Main Bearing BS2X | Sweep | Main Bearing | 2023-09-25 |  | 6 | 9/25/23 - Long standing BS2X signature, continue to monitor for progression. | Monitor | [7 empty] | Case In Progress | -45194
Upstream | Resolved | 3 | S2 PC + PS BRG Damage | Warning | 1st Planetary Stage | 2023-05-29 | 2024-12-05 | 3 | 11/19/24 - Recently replaced. Currently down due to split. 9/20/24 - potential S2 gearing failure indicated by CMS gearbox borescope requested. 6/30/23 - Early damage to the 2nd planetary stage bearings, debris counts are consistently increasing since the installation of the particle counters. Recommending scheduling gearbox replacement in ~Q3-4 of 2024. Placed on the MCFL. | Longterm Watchlist | 3434572 | Closed | Closed | Q4 2024 |  |  | 7/5 - CMS does not have data past 6/21 but turbine is online - reboot, send configuration? | Defect Confirmed - Awaiting Repair | -45075
Deuel Harvest | Resolved | 4 |  | Warning | 2nd Planetary Stage | 2021-12-21 |  | 1 |  | Monitor | [7 empty] | Case In Progress | -44551
Plymouth | Active | 4 | Timken Main Bearing Rolling Element Issue | Warning | Main Bearing | 2024-04-22 |  | 3 | 7/10/24 - Turbine DNRd. 5/16/24 - Borescope shows some signs of roller element damage and DLC delamination. 4/22/24 - Recommend main bearing borescope + grease purge within 2 weeks from 4/22/24. Derated to 50% | Final Report Needed | 3336463 | Closed | Closed |  | 2024-07-22 |  |  | Defect Confirmed - Repair Complete | 91
Upstream | Active | 4 | ZF Flash S2 Carrier Bearing Issue | Sweep | 2nd Planetary Stage | 2023-09-08 |  | 3 | Currently derated. 11/3/23 - minor spalling found in S2 planetary stage continue to monitor via CMS and oil particle data. Put on MCFL recommended replacement in Q3-4, 2024. 9/8/23 - Recommend gearbox borescope with focus on 2nd planetary stage within 3 months from 9/8/23. | Longterm Watchlist | 3187800 | Closed | Closed | Q4 2024 |  | 11/3/2023 - borescope shows spalling on 2PC BRG GS |  | Case In Progress | -45177
Maverick | Resolved | 4 |  | Instrumentation | Helical High Speed Stage | 2021-10-01 |  |  |  |  | 2606970 |  | Closed |  | 2021-12-13 | Check sensor and wirings, sensor may need to be replaced |  |  | 73
Bethel | Resolved | 5 |  | Warning | Helical High Speed Stage | 2021-10-13 |  | 3 |  | Borescope | Create WO |  | #N/A |  | 2023-01-25 | 1/31 - Timeseries shows stage 3 direct has remained at the alarm setpoint throughout 2021, recently trending down, indicating damage has already been sustained to the HSS DnWind Rear bearing in stage 3, 0.4g peak at ORBP |  | Case In Progress | 469
Sundance | Resolved | 5 |  | Instrumentation | CMS Monitor | 2022-05-12 |  |  | Replace 60M100 Monitor - file warranty claim for replacement | CMSTRBLSHOOT | 2930916 | Closed | Closed |  | 2022-08-23 | 8/23 - left condition, no replacement needed |  |  | 103
Upstream | Active | 5 | Stage 2 ORBP/IRBP Issue | Sweep | 2nd Planetary Stage | 2024-05-30 | 2025-03-08 | 2 | 10/30/24 - Request made for borescope due to CMS S2 Planetary ORBP/IRBP defect siganture. 5/30/24 - Particle counter data shows slight increase in accumulation. S1 IRBP signature also seems to be present however could just be parking marks as it has been on the spectrum foran extended period of time. Stage 2 spectrum shows IRBP/ORBP defect signature. | CMSGBXBORE | 3453801 | [6 empty] | Defect Confirmed - Awaiting Repair | -45442
Upstream | Active | 5 | secondary stage ORBP issue | Alarm | 2nd Planetary Stage | 2024-10-04 |  | 2 | 10/4/24 - CMS indicates second planetary ORBP issue | CMSGBXBORE | 3442169 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45569
Santa Rita East | Resolved | 6 |  | Warning | 2nd Planetary Stage | 2022-05-27 |  | 6 |  | Monitor | [7 empty] | Case In Progress | -44708
Bethel | Resolved | 6 | Generator Outboard ORBP + IRBP | Warning | Generator Outboard | 2023-09-18 |  | 6 | 4/1/24 - Direct increase noticed, recommend performing auditory and visual inspection of generator grease and bearings. Also recommend adding grease to bearing.. 9/18/23 - Awaiting direct increase. | CMSGENB | 3326966 | Closed | Ready to Schedule |  | 2024-09-19 |  |  | Defect Confirmed - Repair Complete | 367
Upstream | Resolved | 6 |  | Alarm | 1st Planetary Stage | 2022-05-01 |  | W |  | Pending Replacement | 2935724 | Closed | Closed |  | 2022-06-22 | 5/5 - GFED signal peaked on 5/1, direct signal isn't too concerning, potential bearing fault harmonics at 38.3X, carrying sidebands at 0.7Hz/3.188X, monitor, 5/18 - additional events in all 3 stages, max vibration on 5/13, exception report and borescope, no derate, 5/23 - Borescope found S2 PC BRG roller spalling, S1 fractured planet tooth, probable spalling on S1 bearings, 6/17 - tower is offline for replacement |  | True Positive | 52
Thunderhead | Active | 6 | Main Bearing Sensor Issue | Instrumentation | CMS Monitor | 2024-08-26 |  | 5 | Main bearing sensor is at 0.6 V. Please troubleshoot sensor. | CMSTRBLSHOOT | 3410667 | Closed | Closed |  |  |  |  | Case In Progress
Plymouth | Active | 6 | Potential Timken Main Bearing Issue | Warning | Main Bearing | 2024-03-18 |  | 1 | 4/13/24 - currently undergoing repair. 3/19/24 - Roller damage found, turbine DNR'd until replacement. 3/18/24 - Recommend main bearing borescope + grease purge at next possible opportunity. | Final Report Needed | 3318172 | Closed | Closed |  | 2024-05-21 |  |  | Defect Confirmed - Repair Complete | 64
Bethel | Active | 7 | Main Bearing Damage | Case Tracking | Main Bearing | 2023-02-01 | 2024-09-25 | 2 | 1/8/24 - Borescope found inner race parking marks, continue to monitor for signature progression. 2/1/23 - Main Bearing raceway damage | Monitor | 3088012 | Closed | Closed |  |  |  |  | Case In Progress | -44958
Santa Rita East | Resolved | 7 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-04-26 |  | 3 | CMS monitor is not receiving a speed signal from the generator encoder. Please inspect PEM and encoder using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3116889 | Closed | Closed |  | 2023-05-02 |  |  | Defect Confirmed - Repair Complete | 6
Deuel Harvest | Resolved | 7 |  | Alarm | Generator Inboard | 2021-08-10 |  | 2 |  | Monitor | [5 empty] | 2021-12-27 |  | False Positive - Sensor Issue | -44418
Deuel Harvest | Resolved | 7 |  | Warning | Main Bearing | 2021-09-16 |  | 1 |  | EOW Claim | [6 empty] | 2/2 - 0.1g peak at ball spin 1X, monitor, 2/23 - low concern, continue to monitor, 4/5 - FFT shows moderate haystack and peak at outer race frequency, no harmonics yet, 8/9 - ORBP signal has reduced to lower operation, 9/21 - EOW found IRBP indents, claim pending, 11/28 - no progression, temps good | Case In Progress | -44455
Santa Rita East | Resolved | 7 |  | Instrumentation | Keyphasor | 2022-10-11 |  |  | Use attached keyphasor guide to troubleshoot | CMSTRBLSHOOT | 3033100 | Closed | Closed |  |  | 2022-11-02 |  |  | -44845
Santa Rita East | Resolved | 7 |  | Instrumentation | 1st Planetary Stage | 2021-10-15 |  |  |  |  | 2616793 |  | Closed |  |  | 2022-01-10 |  |  | -44484
Upstream | Resolved | 7 |  | Change 1 | 1st Planetary Stage | 2022-05-30 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 | 6/17 - Stage 1 direct signal shows increase to warning setpoint since March 2022, stage 1 bearing fault harmonics appear to carry mesh fault sidebands, potential S1 PC BRG GS roller damage, 8/16 - Stage 2 changealert, monitor for progression, 11/9 - reduce to cat 1, 11/29 - early stage 2 bearing damage, 12/19 - signal reduced |  | Case In Progress | 239
Plymouth | Resolved | 7 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-11 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988828 | Cancelled | Cancelled | [5 empty] | -44784
Plymouth | Active | 7 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2024-09-09 |  | 4 | 9/9/24 - Monitor is currently not communicating, please ensure monitor is powered and ethernet is plugged into Port A. | CMSTRBLSHOOT | 3420050 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45544
Plymouth | Active | 7 | Main Bearing Issue | EOW | Main Bearing | 2023-11-21 |  | 3 | 4/13/24 - currently undergoing repair. 4/18/24 - Turbine DNRd for CMS signature progression. 4/8/24 - Turbine derated to 50%. 3/18/24 - Awaiting GE disposition on warranty case. 11/21/23 - EOW borescope found indentations on inner race and rolling elemets. Spalling on outer race. | Final Report Needed |  |  |  |  | 2024-06-26 |  |  | Defect Confirmed - Repair Complete | 218
Maverick | Active | 7 | Timken Main Bearing BS2X Signature | Sweep | Main Bearing | 2024-04-29 |  | 2 | 8/30/24 - Turbine DNR'd5/28/24 - Borescope found burnt grease, outer race damage and roller cracking beginning. Recommend replacement within 1-3 months from 5/2024. 4/30/24 - Turbine derated to 50%. 4/29/24 - Recommend main bearing borescope + grease purge within 2 weeks from 4/29/24. Turbine also to be derated to 50% | Final Report Needed | 3343357 | Closed | Closed |  | 2024-08-30 |  |  | Defect Confirmed - Repair Complete | 123
Santa Rita East | Resolved | 7 | SKF Main Bearing Issue | GE Alert | Main Bearing | 2022-10-11 |  | 1 |  | Final Report Needed | 3033134 | Closed | Closed |  | 2023-03-14 | 10/11 - instrumentation for missing KPH signal, Direct signal is spiking, check keyphasor and borescope main bearing, 11/3 - borescope found bronze grease with heavy indenting, spalling on rollers, offline |  | Defect Confirmed - Repair Complete | 154
Santa Rita East | Active | 7 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-12-04 |  | 3 | 12/4/23 - CMS monitor is not receiving a speed signal from keyphasor/PEM/Generator encoder circuit. Keyphasor circuit currently reading 0.1V. Please ensure input is on KPH2 and ensure PEM is wired correctly. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3233040 | Ready to Schedule | Ready to Schedule | [5 empty] | -45264
Upstream | Resolved | 7 | 1st Stage Planetary gearing Issue | Alarm | 1st Planetary Stage | 2023-11-21 | 2024-07-08 | 2 | 3/26/4-repair complete. 11/29/24 - Inspection found broken tooth, will continue to run but with caution and continue to monitor if signature increases. and added to MCFL. 11/21/23 - CMS shows signs of 1st stage planetary gearing issue. Recomended shutting down turbine and borescope within 24-72 hours. | Final Report Needed | 3228026 | Closed | Closed |  |  | 11/29/23 - found broken tooth, will continue to run but with caution and continue to monitor if signature increases. (Added to mcfl long term watchlist). |  | Defect Confirmed - Repair Complete | -45251
Bethel | Active | 8 | Generator Outboard ORBP | Alarm | Generator Outboard | 2023-06-27 | 2024-10-02 | 6 | Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | Monitor | 3148573 | Closed | Closed |  |  |  |  | Case In Progress | -45104
Bethel | Resolved | 8 | Main Bearing Accelerometer Issue | Instrumentation | Main Bearing | 2023-08-31 |  | 5 | 8/31/23 - Sensor giving erroneous readings, please replace main bearing sensor. | CMSTRBLSHOOT | 3182538 | Closed | Ready to Schedule |  | 2024-06-20 |  |  | Defect Confirmed - Repair Complete | 294
Bethel | Resolved | 8 |  | Warning | Generator Outboard | 2021-02-20 |  | 5 |  | Monitor | [5 empty] | 2023-01-25 |  | Case In Progress | -44247
Santa Rita East | Resolved | 8 |  | Warning | 1st Planetary Stage | 2021-10-26 |  | 1 |  | GBXPARTTS | 3056303 | Closed | Closed |  |  | 6/3 - damage has been progressing since Winter 2021, wait for evidence of damage in high res spectra or increase in debris generation, 6/29 - stage 1 direct has reduced to normal levels since 6/17, 7/18 - additional peak on 7/13, S1 PC BRG roller fault peaks with harmonics in the envelope, 8/8 - alarm level peaks have reduced in July, limited damage indications in the envelope, 8/30 - tower offline for TA pin drift, 10/10 - instrumentation case open, 12/13 - no flow rate through particle counter, troubleshoot sump, | Stage 1 vibration peaks have increasing amplitude, borescope on 10/1 found no additional damage since EOW, continue to monitor, 12/28 - vibrations have reduced to below the warning level 1/13 - continue to monitor, 2/21 - Frequent peaks in the direct timeseries, max 10g, continue to monitor, 3/17 - peaks continue in stage 1 to alarm setpoint, stage 2 peaks to warning setpoint, potential damage to stage 1 bearings, 4/25 - stage 1 direct peaking above alarm setpoint since 3/17, | Case In Progress | -44495
Santa Rita East | Resolved | 8 |  | Warning | Generator Outboard | 2021-04-08 |  | 5 |  | Monitor | [6 empty] | Likely damage to DE gen bearing, monitor for failure, 12/28 - 0.4g peak at the orbp fault frequency, timebase impacts are less than 5g 1/13 - continue to monitor for failure, | Case In Progress | -44294
Santa Rita East | Resolved | 8 |  | Instrumentation | 1st Planetary Stage | 2022-09-20 |  |  | Shorted sensor wiring | CMSTRBLSHOOT | 3032258 | Closed | Closed |  |  | 2022-10-10 |  |  | -44824
Bethel | Active | 8 | 1st Planetary Stage Sensor Issue | Instrumentation | 1st Planetary Stage | 2024-06-24 |  | 5 | 6/24/24 - 1st Planetary Stage sensor is currently reading erroneous readings and bias voltage, recommend inspecting wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | 3370716 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45467
Sundance | Resolved | 8 | Generator Inboard Sensor Issue | Instrumentation | Generator Inboard | 2023-03-27 |  | 5 | Data suggests possible sensor issue, recommend inspecting sensor and harness for looseness and ensuring the cabling is not near other power cables. Check grease quality and grounding brushes as well. | CMSTRBLSHOOT | 3103302 | Closed | Closed |  | 2023-08-31 |  |  | Defect Confirmed - Repair Complete | 157
Maverick | Resolved | 8 | Generator Inboard ORBP | Warning | Generator Inboard | 2023-09-05 |  | 3 | 9/5/23 - Recommend investigating/taking samples of bearing noise and grease quality. Upload results to HUVR. | Monitor | 3185554 | Closed | Closed |  |  |  |  | Case In Progress | -45174
Bethel | Resolved | 9 | Main Bearing sensor issue | Instrumentation | Main Bearing | 2023-01-25 |  | 5 | 1/8/24 - ​Sensor possibly reading electrical noise, please ensure cabling is not near high voltage cabling. | CMSTRBLSHOOT | 3072180 | Closed | Closed |  | 2024-01-29 |  |  | Defect Confirmed - Repair Complete | 369
Upstream | Resolved | 9 |  | Warning | 1st Planetary Stage | 2022-12-16 |  | 5 |  | Monitor | [6 empty] | 12/19 - borescoped in September, no damage found in S1 or S3, original case resolved, increase to above previous levels in both S1 and S2, potential S2 bearing damage, monitor, 1/9 - S1 and S2 remain elevated, no fault indicators |  | -44911
Upstream | Resolved | 9 |  | Warning | 2nd Planetary Stage | 2021-10-30 |  | 2 |  | Gearbox Replaced, CMS updated | [6 empty] | 11/30 - gearbox failed 10/30, replaced 11/4. | True Positive | -44499
Santa Rita East | Resolved | 9 |  | Change 1 | 2nd Planetary Stage | 2022-11-08 |  | 5 | [10 empty] | -44873
Upstream | Resolved | 9 |  | Instrumentation | Main Bearing | 2021-11-18 |  |  | Verify power supply and reboot | CMSTRBLSHOOT | 2647023 |  | Closed |  | 2022-09-14 | Likely open sensor wiring - main bearing, 7/6 - Processor hardware disagnostic event, need to replace 60M100 monitor, adding additional case, 9/6 - found sensor unplugged on 8/29, monitor is lost comms |  |  | 300
Deuel Harvest | Active | 9 | Main Bearing Issue | EOW | Main Bearing | 2023-10-09 | 2025-04-01 | 2 | 10/19/23 - Signature progression noted since EOW inspection in Oct 2022, recommending reborescope to determine current status. | Repair Pending | 3208994 |  | Closed |  |  |  |  | Case In Progress | -45208
Deuel Harvest | Resolved | 10 |  | Warning | 2nd Planetary Stage | 2022-01-29 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44590
Deuel Harvest | Resolved | 10 |  | EOW | Main Bearing | 2022-09-19 |  | 1 |  | EOW Claim | [5 empty] | 9/21 - EOW raceway damage throughout |  | False Negative | -44823
Santa Rita East | Resolved | 10 |  | Instrumentation | Keyphasor | 2021-10-15 |  |  | Reconnect Sensor + use troubleshoot guide | CMSTRBLSHOOT | 2616794 |  | Closed |  | 2022-05-27 | 12/28 - Tachometer, pulse expander, rebf card and checked wiring, still offline, unplugged to clear fault. SOLUTION NEEDED, requested techs to reconnect the sensor next climb, 5/27 - Angel replaced pulse extender to clear tachometer fault, closing work order |  |  | 224
Upstream | Resolved | 10 |  | Warning | Helical High Speed Stage | 2022-01-18 |  | 5 |  | Monitor | [5 empty] | 2/8 - occasional peaks to the warning setpoint, FFT shows 0.1g sidebands (Mode 2) and 0.5g sidebands (Mode 5) between 2X and 3X GMF, 3/4 - monitor for increasing trend in timeseries, 4/13 - 2X GMF peak indicates misalignment, potential HSS bearing issue due to high frequency harmonics, 5/5 - limited progression, borescope will be needed to check HSS bearings, 8/18 - limited progression, |  | Case In Progress | -44579
Upstream | Resolved | 10 |  | Warning | Generator Inboard | 2021-04-27 |  | 1 |  | Monitor | [5 empty] | 2022-10-19 |  | False Positive - No Inspection | -44313
Plymouth | Resolved | 10 |  | Instrumentation | CMS Monitor | 2022-06-03 |  |  | Replace 60M100 monitor | CMSTRBLSHOOT | 2941642 | Cancelled | Cancelled |  | 2022-08-29 | 8/29 - do not replace monitor if 319 event left state |  |  | 87
Plymouth | Resolved | 10 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-11 |  | 5 | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988829 | Closed | Closed |  |  |  |  | True Positive | -44784
Plymouth | Active | 10 | Main Bearing Accelerometer Issue | Instrumentation | Main Bearing | 2024-09-09 |  | 4 | 9/9/24 - ​Main bearing sensor reading erroneous data, please investigate wirings and connections. | CMSTRBLSHOOT | 3420052 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45544
Plymouth | Active | 10 | Timken Main Bearing BS2X Issue | Warning | Main Bearing | 2024-06-06 |  | 2 | 6/6/24 - Turbine is showing signature progression, recommend derating turbine to 50% and borescoping the main bearing of this turbine with focus on rolling elements. | Final Report Needed | 3364665 | Closed | Closed |  | 2024-09-26 |  |  | Defect Confirmed - Repair Complete | 112
Bethel | Active | 11 | S1 DnWind Planetary Bearing | Sweep | 1st Planetary Stage | 2023-10-30 |  | 6 | 10/30/23 - Borescope for HSS bearing found damage to S1 DnWind planetary bearings, continue to monitor | Monitor | [7 empty] | Case In Progress | -45229
Bethel | Active | 11 | HSS Bearing Damage | Case Tracking | Helical High Speed Stage | 2023-02-06 |  | 6 | 10/30/23 - Borescope found no damage, continue to monitor. 2/6/23 - Check HSS bearing for damage | Monitor | 3080380 | Closed | Closed |  |  |  |  | Case In Progress | -44963
Bethel | Resolved | 11 | Generator Outboard IRBP | Warning | Generator Outboard | 2023-09-18 |  | 6 | 4/1/24 - Closing due to inactivity. 9/18/23 - Awaiting direct increase. | Monitor | [7 empty] | Case In Progress | -45187
Bethel | Resolved | 11 |  | Alarm | Generator Outboard | 2022-01-04 |  | 5 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - NDE bearing shows signs of damage to the inner and outer race - timebase impacts 5-10g, 0.8g peak at IRBP, 0.5g peak at ORBP |  | Case In Progress | 386
Bethel | Resolved | 11 |  | Warning | Helical High Speed Stage | 2022-01-19 |  | 5 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - warning events in all three stages of the gearbox, monitor closely for increases |  | Case In Progress | 371
Deuel Harvest | Resolved | 11 |  | EOW | Main Bearing | 2022-08-16 |  | 1 |  | EOW Claim | [7 empty] | False Negative | -44789
Santa Rita East | Resolved | 11 | IONet Issue | Instrumentation | CMS Monitor | 2023-04-26 |  | 5 | CMS monitor is missing it's power signal, please perform toolbox CBM download. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3116880 | Closed | Closed |  | 2023-04-27 |  |  | Defect Confirmed - Repair Complete | 1
Upstream | Resolved | 11 |  | Warning | Main Bearing | 2022-07-02 |  | 5 |  | Monitor | [8 empty] | -44744
Maverick | Active | 11 | Main Bearing Outer Race Issue | Warning | Main Bearing | 2024-01-16 |  | 1 | 3/22/24 - Turbine DNR'd for overtemp. 2/28/24- Turbine now derated to 30% 2/8/24 - Turbine derated to 50%. 1/16/24 - Recommend main bearing borescope and thrust derate at next possible opportunity. | Final Report Needed | 3255028 | Closed | Closed |  | 2024-03-22 |  |  | Defect Confirmed - Repair Complete | 66
Maverick | Resolved | 11 |  | Keyphasor Issue | Keyphasor | 2022-03-28 |  |  | Use Keyphasor troubleshoot guide | CMSTRBLSHOOT | 2892345 |  | Cancelled |  | 2022-10-24 | 10/24 - kph is functioning properly |  |  | 210
Maverick | Resolved | 11 | S1 Planetary Bearing Issue | EOW | 1st Planetary Stage | 2023-08-11 | 2024-12-18 | 6 | 8/11/23 - EOW borescope found very early spalling, continue to monitor via CMS and particle data. | Monitor | [7 empty] | Case In Progress | -45149
Santa Rita East | Resolved | 12 | IONet Issue | Instrumentation | CMS Monitor | 2023-04-26 |  | 5 | CMS monitor is missing it's power signal, please perform toolbox CBM download. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3116882 | Closed | CLosed |  | 2023-04-27 |  |  | Defect Confirmed - Repair Complete | 1
Upstream | Resolved | 12 |  | Warning | Helical High Speed Stage | 2021-05-13 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 |  | 5/25 - likely damage to HSS bearings, bearing fault harmonics between 2X and 3X GMF, may be sensor noise, 6/17 - likely mild misalignment, 8/18 - additional S3 alarm, | Case In Progress | 621
Deuel Harvest | Active | 12 | Generator Outboard ORBP/IRBP Issue | Alarm | Generator Outboard | 2024-11-19 |  | 3 | 11/19/24 - CMS indicated generator outboard ORBP/IRBP Issue, sent out for inspection | CMSGENB | 3466484 |  | Ready to Schedule |  |  |  |  | Case In Progress | -45615
Plymouth | Active | 12 | Timken Main Bearing BS2X Issue | Warning | Main Bearing | 2024-09-10 |  | 2 | 9/27/24 - Derated to 50%. 9/10/24 - Recommend borescoping this main bearing within 2 weeks from 9/10/24 with focus on outer race and rollers. | Repair Pending | 3420490 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45545
Upstream | Active | 12 | Generator Outboard | Alarm | Generator Outboard | 2024-05-30 |  | 4 | 5/30/24 - CMS shows early Generator outboardORBP signature. Continue to monitor. | Monitor | [7 empty] | Case In Progress | -45442
Maverick | Resolved | 12 |  | Instrumentation | 2nd Planetary Stage | 2022-03-28 |  |  | Check for open wiring | CMSTRBLSHOOT | 2892530 |  | Cancelled |  | 2022-10-26 |  |  |  | 212
Deuel Harvest | Resolved | 13 |  | Warning | 2nd Planetary Stage | 2022-01-01 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44562
Deuel Harvest | Resolved | 13 | Elevated gen bearing vibration | Warning | Generator Inboard | 2021-10-26 |  | 2 | Potential DE Generator bearing issue, recommend inspecting and adding grease to both generator bearings. If abnormal issues are found, please upload grease pictures and noise recording to HUVR. | CMSGENB | 2788980 |  | Ready to Schedule |  |  |  |  | Case In Progress | -44495
Santa Rita East | Resolved | 13 | IONet Issue | Instrumentation | CMS Monitor | 2023-04-26 |  | 5 | CMS monitor is missing it's power signal, please perform toolbox CBM download. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3116884 | Closed | Closed |  | 2023-04-27 |  |  | Defect Confirmed - Repair Complete | 1
Santa Rita East | Resolved | 13 |  | Instrumentation | 1st Planetary Stage | 2021-08-09 |  |  |  |  | 2476045 |  | Closed |  |  | 2021-12-10 |  |  | -44417
Plymouth | Resolved | 13 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-05-13 |  | 5 | Keyphasor (tachometer) is not reading shaft speed to CMS monitor. Please use attached troubleshoot guide to troubleshoot sensor | CMSTRBLSHOOT | 3084374 | Closed | Closed |  | 2023-04-20 |  |  | True Positive | 342
Bethel | Active | 13 | Main Bearing Inner Race Issue | Sweep | Main Bearing | 2024-01-11 |  | 3 | 9/11/24 - Main bearing continuously faulting out, turbine placed on DNR list. 1/24/24 - Minor inner race spalling, CMS will continue to monitor for damage progression. Added to MCFL. 1/11/24 - Please perform a full main bearing borescope and upload the report to HUVR. - Take a grease sample from in between the rollers - Check vibration and temperature sensors are tightly mounted https://invenergy.sharepoint.com/sites/ODR/Procedures/Procedure_Fleet_Main_Bearing_Inspection_current.pdf | Final Report Needed | 3252883 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -45302
Red Barn | Active | 13 | Generator Inboard ORBP | Warning | Generator Inboard | 2024-05-07 |  | 3 | 5/7/24 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact CMSEngineers_OSW@invenergyllc.com for support | Monitor | 3347480 | Closed | Closed |  |  |  |  | Case In Progress | -45419
Upstream | Resolved | 13 | Generator Ouboard ORBP/IRBP | Warning | Generator Outboard | 2023-09-14 | 2024-04-22 | 3 | 3/23/24 - Component replaced as result of gen bearing campaign, CMS data received. 9/14/23 - ORBP/IRBP present continue to monitor 10/25/23 - alert flagged, generator Outboard, direct is increasing & peaks @15.54, WO to add grease to bearings. | Final Report Needed | 3212063 | Closed | Closed |  | 2024-03-23 |  |  | Defect Confirmed - Repair Complete | 191
Maverick | Active | 13 | SKF Main Bearing BS2X | GE Alert | Main Bearing | 2022-12-27 |  | 1 | 2/15/24 - Turbine derated to 75%. 10/15/23 - GE recommended turbine be run full power, continue to monitor. 9/12/23 - Recommend main bearing borescope with focus on cage and rolling elements at next possible opportunity. 12/22/22 - Turbine currently running thrust derated. Warranty Claim #5939542-T13 (Rejected) | Monitor | 3189858 | Closed | Closed |  |  | 1/11/23 - borescope found some damage to rollers |  | Case In Progress | -44922
Deuel Harvest | Resolved | 14 |  | Warning | 1st Planetary Stage | 2022-06-29 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44741
Deuel Harvest | Resolved | 14 |  | Warning | Generator Outboard | 2022-04-05 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44656
Santa Rita East | Resolved | 14 |  | Change 1 | 2nd Planetary Stage | 2022-08-08 |  | 6 | [10 empty] | -44781
Sundance | Active | 14 | NTN Main Bearing ORBP | Sweep | Main Bearing | 2023-03-14 |  | 2 | 7/18/23 - Borescope showed signs on heavy spalling on the outer race, roller element damage, and cage wear. Placed on MCFL. 7/6/23 - Main bearing temperatures deviating greatly from neighboring turbines, recommend secondary borescope inspection be made. | Final Report Needed | 3153567 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -44999
Santa Rita East | Active | 14 | Main Bearing BS2X | Sweep | Main Bearing | 2024-08-29 |  | 2 | 8/29/24 - Recommend borescoping this main bearing within 2 weeks from 8/29/24 with focus on outer race and rollers. | Repair Pending | 3411535 | Closed | CLosed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45533
Upstream | Active | 14 | Main Bearing Direct trend increase | Alarm | Main Bearing | 2023-10-06 | 11/83429 | 6 | 10/06/23 - notice direct signautre increase continue to monitor for now, 10/24 Noticed flagged again in MB direct signature continues to increase | Monitor | [7 empty] | Case In Progress | -45205
Bethel | Active | 15 | Main Bearing damage | Case Tracking | Main Bearing | 2023-02-01 |  | 1 | 9/27/23 - Significant outer race damage and raceway edge chipping present. Turbine should be DNRd until main bearing replacement 9/25/23 - Recommend main bearing borescope within 2 weeks. The turbine should remain in load shutdown until inspection can be completed. 2/1/23 - Main Bearing ORBP harmonics with evidence of progression | Final Report Needed | 3179621 |  | Closed |  |  | Add the MCFL |  | Defect Confirmed - Awaiting Repair | -44958
Bethel | Resolved | 15 |  | Warning | Helical High Speed Stage | 2021-10-10 |  | 6 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - Stage 3 direct has remained at or below the warning setpoint for the past year, FFT floor is high, around 0.05, small peaks at Ball Spin 1X, 2X and ORBP, potential roller damage to HSIS UpWind Bearing |  | Case In Progress | 472
Bethel | Resolved | 15 |  | Warning | Generator Outboard | 2022-01-29 |  | 5 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - Generator Outboard has recently increased to the warning setpoint, 10g impacts in timebase, 2g peak at ORBP, monitor closely for increases to the alarm |  | Case In Progress | 361
Deuel Harvest | Resolved | 15 |  | Instrumentation | Main Bearing | 2022-09-02 |  |  | open sensor wiring | CMSTRBLSHOOT | 3011542 | Cancelled | Cancelled |  | 2022-09-21 |  |  |  | 19
Upstream | Resolved | 15 |  | Warning | 2nd Planetary Stage | 2021-09-09 |  | 1 |  | Monitor | 2284643 |  | Closed |  |  |  | 11/18 - 2X and 3X peaks with 0.02g sidebands, 11/30 - Stage 2 SER Planet Fault GFR SR1 spikes are increasing, still below alarm setpoint 1/11 - continue to monitor, 3/4 - 0.04g @ Stage 1 Carrier GS, higher amplitude peak in direct timeseries, be prepared for increasing amplitude/progressing damage, 3/25 - evidence of damage to stage 2 gears, 4/12 - no significant progression, continue to monitor, 5/25 - likely damage to S2 PC BRG GS outer race, 6/17 - recent alarm-surpassing peak in the Stage 2 SER Planet Fault GFR SR1, suspect damage to S2 PC BRG GS outer race, CMS shows damage to S1 PC BRG GS rollers, 8/18 - spike in S2 SER Planet Fault GFR SR1, wait for direct peak, 9/6 - additional S2 SER Planet Fault GFR SR1 warning, S2 Planet fault is aparent in Mode 3, | True Positive | -44448
Santa Rita East | Resolved | 15 | IONet Issue | Instrumentation | CMS Monitor | 2023-04-26 |  | 5 | CMS monitor is missing it's power signal, please perform toolbox CBM download. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3116887 | Closed | Closed |  | 2023-04-27 |  |  | Defect Confirmed - Repair Complete | 1
Plymouth | Resolved | 15 | CMS Monitor Netcom/Keyphasor Issue | Instrumentation | CMS Monitor | 2024-09-09 |  | 4 | 9/9/24 - CMS monitor is currently not communicating, please ensure monitor is powered and ethernet is plugged into Port A. | CMSTRBLSHOOT | 3420060 | Closed | Closed |  | 2024-09-27 |  |  | Defect Confirmed - Repair Complete | 18
Sundance | Active | 15 | Potential NTN Main Bearing Outer Race/Rolling Element Issue | Alarm | Main Bearing | 2024-11-27 |  | 2 |  | CMSMBBORE | 3469952 |  | Ready to Schedule |  |  |  |  | Case In Progress | -45623
Maverick | Resolved | 15 | Main Bearing Raceway Damage | GE Alert | Main Bearing | 2022-10-11 |  | 2 |  | CMSMBCHECK | 3032633 | Cancelled | Closed |  |  | 10/11 - GE requested scope for MB ORBP, 10/26 - increasing direct trend continues, limited tiny fault harmoincs occasionally, 12/5 - signal has reduced, limited fault indicators |  |  | -44845
Bethel | Resolved | 16 |  | Warning | 1st Planetary Stage | 2022-01-29 |  | 6 | [6 empty] | 2023-01-25 |  |  | Case In Progress | 361
Bethel | Resolved | 16 | Gen Bearing Damage | Case Tracking | Generator Outboard | 2023-01-25 |  | 2 | Add grease to both gen bearings | Monitor | 3072183 | Closed | Closed |  | 2023-09-11 |  |  | Defect Confirmed - Repair Complete | 229
Bethel | Resolved | 16 |  | Warning | Generator Outboard | 2021-10-08 |  | 3 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - NDE bearing shows signs of damage, signal remains between warning and alarm setpoint, 10-15g impacts in the timebase, 1.5g peak at ORBP, 0.7g peak at IRBP |  | Case In Progress | 474
Deuel Harvest | Resolved | 16 | Main Bearing Sensor Issue | Instrumentation | Main Bearing | 2022-06-10 | 2023-03-12 | 5 | Replace main bearing sensor | CMSTRBLSHOOT | 2943943 | Cancelled | closed | [5 empty] | -44722
Deuel Harvest | Resolved | 16 |  | Alarm | Main Bearing | 2022-06-12 |  | 1 |  | EOW Claim | [8 empty] | -44724
Deuel Harvest | Resolved | 16 |  | Instrumentation | CMS Monitor | 2022-04-05 |  |  | wait | [5 empty] | 2022-06-08 |  |  |  | 64
Santa Rita East | Resolved | 16 |  | Alarm | Helical High Speed Stage | 2021-12-10 |  | 1 |  | GBXPARTTS | 3056328 | Closed | Closed |  |  |  | Rowdy borescoped in late September, contacted him for photo of stage 3, vibrations have remained above alarm setpoint for full operating life, monitor for sudden changes, 12/28 - vibrations have dipped below the alarm setpoint for the first time in a year, timebase averages at 5g 1/13 - vibration floor ~0.075g, Sudden drop in Dei Intermediate and HSS Rotational on 12/11/21, may be related to Gen alignment, reduce to cat 2, 1/31 - Direct vibration increased above the alarm setpoint on 1/14, 0.2g Pinion fault sidebands present at 2X GMF, 4/4 - FFT shows sidebands around 2X GMF, elevated 2X GMF indicates misalignment, no progression in the last year | Case In Progress | -44540
Santa Rita East | Resolved | 16 | S1 Planetary Accelerometer Issue | Instrumentation | 1st Planetary Stage | 2023-03-15 |  | 4 | S1 Planetary Accelerometer giving erroneous reading, please inspect sensor for loose connection. | CMSTRBLSHOOT | 3098845 | Closed | Closed |  | 2023-03-17 |  |  | Defect Confirmed - Repair Complete | 2
Santa Rita East | Resolved | 16 | High Speed Stage Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2023-02-22 |  | 4 | HSS sensor is reading erroneous readings, please replace sensor. | CMSTRBLSHOOT | 3086237 | Closed | Closed |  | 2023-02-27 |  |  | Defect Confirmed - Repair Complete | 5
Plymouth | Resolved | 16 |  | Alarm | Generator Inboard | 2022-05-02 |  | 1 |  | Gen Replacement | [5 empty] | 7/1/22 |  | True Positive | -44683
Maverick | Active | 16 | Timken Main Bearing BS2X Signature | Sweep | Main Bearing | 2024-03-26 |  | 2 | 4/22/24 - Borescope completed, found roller spalls and raceway indents. Turbine DNR'd. 3/26/24 - Recommend main bearing borescope and 50% power derate at next opportunity. | Final Report Needed | 3323494 | Closed | Closed |  | 2024-04-23 |  |  | Defect Confirmed - Repair Complete | 28
Plymouth | Active | 16 | Timken Main Bearing Rolling Element Issue | Warning | Main Bearing | 2024-03-18 |  | 2 | 4/13/24 - currently undergoing repair. 3/18/24 - Recommend main bearing borescope + grease purge within 2 weeks from 3/18/24. | Final Report Needed | 3318138 | Closed | Closed |  | 2024-06-11 |  |  | Defect Confirmed - Repair Complete | 85
Upstream | Active | 16 | S2 Sun and Planetary Damage | Warning | 2nd Planetary Stage | 2022-10-23 | 2025-03-04 | 3 | Progressing S2 Sun Damage, monitor debris | Monitor |  |  | Closed |  |  | 1/27 - no damage found in borescope, 2/7 - increased S2 Sun Fault GFED and GFR SR2 thresholds, 3/15 limited progression, warranty end 06/28/24 |  | Case In Progress | -44857
Bethel | Resolved | 17 | Generator Inboard ORBP | Warning | Generator Inboard | 2023-10-23 | 2024-05-28 | 3 | 1/3/24 - Continue to monitor. 10/23/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | Monitor | 3209850 | Closed | Closed |  |  |  |  | Case In Progress | -45222
Bethel | Resolved | 17 | Gen Bearing Damage | Warning | Generator Outboard | 2023-01-26 |  | 1 | Replace NDE bearing (did not swap DE bearing) | CMSGENB | 3072465 | Closed | Closed |  | 2023-04-12 | 1/31 - spike to 60g, increased priority on work order |  | Defect Confirmed - Repair Complete | 76
Deuel Harvest | Resolved | 17 |  | Alarm | Helical High Speed Stage | 2022-08-31 |  | 2 |  | Monitor | [5 empty] | 2023-01-17 | 9/2 - GFED signal has taken off, potential coupler misalignment, increase in S3 direct as well, limited fault indicators in the spectra, monitor for damage indicators, | True Positive - Other Method | -44804
Upstream | Resolved | 17 |  | Alarm | Generator Outboard | 2021-01-12 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 |  | 2/8 - damage sustained to NDE bearing December 2020-March 2021, vibrations have reduced since | Case In Progress | 742
Upstream | Resolved | 17 |  | Warning | Helical High Speed Stage | 2021-04-19 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 |  | 11/18 - warning level spikes in October, 1/11 - low concern, 3/4 - 0.150g @ 0.422X, continue to monitor, 8/18 - 5g average vibration in timebase, misalignment in the mesh and potential HSS bearing fault, 11/29 - step down in direct signal | Case In Progress | 645
Plymouth | Resolved | 17 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-11 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988831 | Closed | Cancelled | [5 empty] | -44784
Bethel | Active | 17 | Main Bearing Inner Race Issue | Sweep | Main Bearing | 2024-01-16 | 2024-10-01 | 2 | 1/29/24 - Possible inner race crack forming, est. replacement date Q1-Q2 2025. CMS will continue to monitor. 1/16/24 - Recommend main bearing borescope within 1 month from 1/16/24. | Longterm Watchlist | 3254981 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45307
Thunderhead | Active | 17 | Generator Inboard Potential ORBP | Alarm | Generator Inboard | 2024-03-05 | 2025-03-05 | 3 | 3/5/24 - CMS indicates potential IDE generator bearing IRBP issue. | CMSGENB | 3334723 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45356
Sundance | Active | 17 | NTN Main Bearing Roller Element Issue | Sweep | Main Bearing | 2024-07-15 |  | 2 | 7/15/24 - Recommend borescoping this main bearing within 2 weeks from 7/15/24 with focus on outer race and rollers. | CMSMBBORE | 3386055 | Closed | Ready to Schedule |  |  |  |  | Miss - Defect Not Caught | -45488
Maverick | Resolved | 17 |  | Warning | Generator Inboard | 2022-06-23 |  | 6 |  | Monitor |  |  |  |  | 2022-11-15 | 6/23 - potential damage to HSS RS raceways, 11/15 - resolving |  | False Positive - No Action | 145
Deuel Harvest | Active | 17 | HSS Rotational | Alarm | Generator Inboard | 2023-04-05 |  | 3 | Please inspect generator and HSS coupler for possible misalignment. Please also perform an auditory and visual inspection of the generator bearings: Contact abarndt@invenergy.com for support | Monitor | 3108969 | Closed | Closed |  |  |  |  | Case In Progress | -45021
Upstream | Active | 17 | Potential Gearing issue | Alarm | 1st Planetary Stage | 2024-09-04 |  | 3 | 11/13/24 - Derate requested due to defect signature progression. 9/18/24 - Borescope does not show indication of issue, continue to monitor. 9/4/24 - CMS shows potential gearing issue. Request for Gearbox borescope. | CMSGBXBORE | 3419472 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45539
Bethel | Active | 18 | Main Bearing raceway and roller damage | Sweep | Main Bearing | 2023-02-01 |  | 1 | 2/21/23 - Main Bearing raceway damage, 50% power derate to preserve RUL, IR axial crack | Final Report Needed | 3094778 | Closed | Closed |  | 2023-09-22 | 3/8 - "grease was completely black and would recommend a full borescope to fully assess the damage" |  | Defect Confirmed - Repair Complete | 233
Bethel | Resolved | 18 |  | Warning | Helical High Speed Stage | 2021-10-10 |  | 6 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - signal remains at warning setpoint, FFT shows 0.45g sidebands near 2X GMF, pinion fault, recent borescope didn't find damage, monitor for increased |  | Case In Progress | 472
Bethel | Resolved | 18 |  | Warning | Main Bearing | 2021-08-27 |  | 6 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - monitor for signs of damage to main bearing |  | Case In Progress | 516
Santa Rita East | Resolved | 18 |  | Warning | 1st Planetary Stage | 2022-12-13 |  | 5 |  | Monitor | [8 empty] | -44908
Plymouth | Resolved | 18 | Netcom Monitor | Instrumentation | Keyphasor | 2023-04-10 |  | 3 | CMS monitor is currently showing no power or speed signal, nor collecting data. Please ensure ethernet is plugged into Port A and monitor appears lit and working properly. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3110862 | Closed | Closed |  | 2023-06-03 |  |  | Defect Confirmed - Repair Complete | 54
Plymouth | Resolved | 18 |  | Instrumentation | CMS Monitor | 2022-04-28 |  |  | Check Farm Client and Montior Configuration in the CMS server to diagnose issue before climbing. | CMSTRBLSHOOT | 2924754 | Cancelled | Cancelled | [5 empty] | -44679
Plymouth | Resolved | 18 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-11 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988832 | Cancelled | Cancelled | [5 empty] | -44784
Plymouth | Active | 18 | Timken Main Bearing BS2X Issue | Warning | Main Bearing | 2024-09-10 |  | 2 | 10/15/24 - Recommend borescoping this main bearing within 2 weeks from 10/15/24 with focus on outer race and rollers. Also recommending a 50% derate on this turbine to prolong bearing life. | CMSMBBORE | 3445901 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45545
Bethel | Active | 19 | Main Bearing Inner Raceway Damage | Case Tracking | Main Bearing | 2023-02-03 |  | 3 | 9/19/23 - Main bearing borescope found markings on inner race, continue to monitor via CMS and temps. 9/11/23 - Recommend main bearing borescope within 2 weeks with focus on inner raceway. | Monitor | 3188384 | Closed | Closed |  |  | 2/3 - limited growth in past 6 mo |  | Case In Progress | -44960
Deuel Harvest | Resolved | 19 |  | EOW | Main Bearing | 2022-08-16 |  | 1 |  | EOW Claim | [7 empty] | False Negative | -44789
Upstream | Resolved | 19 |  | Warning | 2nd Planetary Stage | 2022-11-19 |  | 5 |  | Monitor | [8 empty] | -44884
Santa Rita East | Resolved | 19 |  | Warning | 2nd Planetary Stage | 2021-09-09 |  | 6 |  | Monitor | [7 empty] | Case In Progress | -44448
Sundance | Resolved | 19 |  | Instrumentation | CMS Monitor | 2022-05-12 |  |  | Replace 60M100 Monitor - file warranty claim for replacement | CMSTRBLSHOOT | 2930918 | Closed | Closed |  | 2022-08-23 | 8/23 - left condition, no replacement needed |  |  | 103
Sundance | Resolved | 19 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255344 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Plymouth | Resolved | 19 | Main Bearing Accelerometer Issue | Instrumentation | Main Bearing | 2024-04-24 |  | 5 | 4/24/24 - Currently not receiving data from main bearing sensor, please check wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3337121 | Cancelled | Ready to Schedule |  | 2024-05-07 |  |  | Defect Confirmed - Repair Complete | 13
Plymouth | Resolved | 19 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-04-20 |  | 3 | Per GE request, please gen encoder and PEM. | CMSTRBLSHOOT | 3132478 | Closed | Closed |  | 2023-06-03 |  |  | Defect Confirmed - Repair Complete | 44
Maverick | Resolved | 19 |  | Keyphasor Issue | Keyphasor | 2022-03-28 |  |  | Use Keyphasor troubleshoot guide | CMSTRBLSHOOT | 2892346 |  | Closed |  | 2022-04-11 | 4/12 - everything looked good |  |  | 14
Bethel | Resolved | 20 | HSS Hydraulic Brake Issue | Warning | Other | 2023-06-28 |  | 1 | Recommend inspecting hydraulic brake for any possible dragging or rubbing, if nothing is found inspect HSS pinion for any tooth breakage within 48-72 hours from 6/28. If tooth breakage is found, derate turbine to 50%. | CMSHSS | 3149438 | Closed | Closed |  | 2023-06-28 |  |  | Defect Confirmed - Repair Complete | 0
Deuel Harvest | Resolved | 20 |  | Instrumentation | CMS Monitor | 2022-06-28 |  |  |  | Wait |  |  |  |  | 2022-07-19 |  |  |  | 21
Santa Rita East | Resolved | 20 |  | Change 1 | 2nd Planetary Stage | 2022-10-27 |  | 6 |  | Monitor | [8 empty] | -44861
Santa Rita East | Resolved | 20 |  | Warning | Main Bearing | 2022-01-24 |  | 1 |  | Replacement Complete | [5 empty] | 2022-10-10 |  | True Positive - Other Method | -44585
Santa Rita East | Resolved | 20 |  | Instrumentation | Helical High Speed Stage | 2022-11-03 |  |  | Open sensor wiring | CMSTRBLSHOOT | 3041728 | Closed | Closed |  |  | 2022-11-03 |  |  | -44868
Bethel | Active | 20 | 1st Planetary Stage Gearing Issue | Warning | 1st Planetary Stage | 2024-10-14 |  | 1 | 10/14/24 - Recommend full gearbox borescope within 24-72 hours from 10/14/24 with focus on the 1st planetary stage. Also recommend derating turbine to 50% until inspection can be performed. | Final Report Needed | 3445651 | Closed | Ready to Schedule |  | 2024-11-01 |  |  | Defect Confirmed - Repair Complete | 18
Sundance | Resolved | 20 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255351 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Maverick | Active | 20 | Main Bearing Issue | Sweep | Main Bearing | 2023-05-22 | 2024-10-28 | 2 | 4/25/24 - Continuing to monitor. 5/22/23 - Recommend main bearing borescope within 1 month from 5/22/23. Please also provide data on main bearing manufacturer. | Monitor | 3130547 | Closed | Closed |  |  |  |  | Case In Progress | -45068
Bethel | Resolved | 21 | DE gen bearing sensor issue | Instrumentation | Generator Inboard | 2023-01-26 |  | 4 | Replace sensor on DE gen bearing | CMSTRBLSHOOT | 3072462 | Closed | Closed |  | 2023-07-05 |  |  | Defect Confirmed - Repair Complete | 160
Bethel | Resolved | 21 |  | Warning | 1st Planetary Stage | 2022-01-30 |  | 6 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - DEI Intermediate, monitor for changes |  | Case In Progress | 360
Bethel | Resolved | 21 |  | Warning | Generator Inboard | 2021-11-24 |  | 5 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - timebase signal for DE gen bearings is sporadic and not normal, low peaks at Ball Spin 1X, 2X, ORBP (0.2g max) |  | Case In Progress | 427
Deuel Harvest | Resolved | 21 |  | Instrumentation | CMS Monitor | 2022-06-28 |  |  |  | Wait |  |  |  |  | 2022-07-19 |  |  |  | 21
Thunderhead | Resolved | 21 | Main Bearing Sensor Issue | Instrumentation | CMS Monitor | 2024-08-07 |  | 5 | Main bearing sensor is at -22.7 V. Please troubleshoot sensor. | CMSTRBLSHOOT | 3399245 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete
Maverick | Active | 21 | 1st Planetary Stage Bearing/gearing Issue | Particle Counter | 1st Planetary Stage | 2024-01-18 |  | 3 | 2/15/24 - Gearbox appears to have experienced a planetary gearing failure, turbine down until inspection can be made. 1/18/24 - Recommend gearbox borescope with focus on the 1st planetary stage within 2 months from 1/18/24. | Final Report Needed | 3255553 | Closed | Closed |  | 2024-02-19 |  |  | Defect Confirmed - Repair Complete | 32
Plymouth | Active | 21 | Timken Main Bearing BS2X Signature | Warning | Main Bearing | 2024-09-23 | 2024-10-02 | 2 | 9/27/24 - Turbine derated to 50%. 9/23/24 - Recommend borescoping this main bearing within 2 weeks from 9/23/24 with focus on outer race and rollers. | Repair Pending | 3435000 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45558
Bethel | Active | 21 | Generator Outboard ORBP | Warning | Generator Outboard | 2024-04-29 |  | 6 | 4/29/24 - Awaiting direct increase. | Monitor | [7 empty] | Case In Progress | -45411
Upstream | Resolved | 22 |  | Warning | Helical High Speed Stage | 2021-08-12 |  | 6 |  | Monitor | 2516237 | Cancelled | Cancelled |  | 2023-01-24 |  | 4/12 - FFT shows vibration floor increase around 12X shaft speed, no significant progression in timeseries trend, 6/17 - potential misalignment, 8/18 - matches site average, 10/19 - limited progression, 11/10 - reduce to cat 1 | Case In Progress | 530
Santa Rita East | Resolved | 22 |  | Warning | Helical High Speed Stage | 2021-03-18 |  | 5 |  | Monitor | [6 empty] | stage 3 peak at 2X GMF, continue to monitor for sideband growth, 12/28 - HSS Rotational alarms for both gen bearings, no signs of damage to the bearings, 0.3g peak at 1X rotation, potential alignment issue 1/13 - Potential damage to Stage 3 pinion, monitor stage 3 direct for increase to alarm, 1/31 - Stage 3 direct FFT shows 0.1g sidebands between 2x and 3x GMF, somewhat consistent disposition in the past 12 months, continue to monitor for increases, reducing the cat 2, 2/21 - adding to case studies list, 4/4 - 2X"sidebands" may be HSS bearing fault harmonics, | Case In Progress | -44273
Santa Rita East | Resolved | 22 |  | Alarm | Generator Inboard | 2022-07-12 |  | 6 |  | Monitor | [7 empty] | Case In Progress | -44754
Santa Rita East | Resolved | 22 |  | Alarm | Generator Inboard | 2022-03-11 |  | 1 |  | Monitor | [5 empty] | 2022-04-04 |  | False Positive - No Inspection | -44631
Sundance | Resolved | 22 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255353 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Plymouth | Active | 22 | Timken Main Bearing BS2X Issue | Case Tracking | Main Bearing | 2023-07-05 |  | 1 | 6/20/24 - Turbine DNR'd due to roller fracture. 5/30/24 - Signature progression has occurred, recommending 50% derate as well as borescope inspection. 7/7/23 - Main Bearing borescope did not show much damage, only surface frosting and possible banding. CMS will continue to monitor. | Final Report Needed | 3358125 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45112
Deuel Harvest | Active | 22 | Generator Outboard Accelerometer Short Circuit | Instrumentation | Generator Outboard | 2023-05-08 |  | 5 | ​Generator Outboard accelerometer is currently reading a short circuit, recommend inspecting wiring and connections. | CMSTRBLSHOOT | 3123710 | Closed | In Progress |  |  |  |  | Case In Progress | -45054
Maverick | Resolved | 22 |  | Processor Hardware Diagnostic Event | CMS Monitor | 2022-04-18 |  |  | Replace CMS monitor | CMSTRBLSHOOT | 2921113 | Cancelled | Cancelled |  | 2022-08-23 | 8/23 - left conditino, no replacement |  |  | 127
Deuel Harvest | Resolved | 23 |  | Instrumentation | CMS Monitor | 2022-02-02 |  |  | Wait | [5 empty] | 2022-04-05 |  | Failed PMT, 2/23 - not running |  | 62
Santa Rita East | Resolved | 23 |  | Warning | 2nd Planetary Stage | 2021-12-10 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44540
Bethel | Resolved | 23 | Generator Inboard IRBP | Warning | Generator Inboard | 2023-09-18 | 2024-03-20 | 6 | 4/1/24 - Closed due to inactivity. 9/18/23 - Awaiting direct increase. | Monitor | [7 empty] | Case In Progress | -45187
Santa Rita East | Resolved | 23 | 2nd Planetary Stage Planet Gearing Issue | Particle Counter | 2nd Planetary Stage | 2024-05-02 |  | 1 | 5/13/24 - Secondary borescope did not find suspected fractured tooth instead found debri run off damage.Turbine is currently under 50% derate. 5/2/24 - Please perform a full gearbox borescope with focus on the 2nd planetary stage at next possible opportunity. Turbine also to be derated to 50% | CMSGBXBORE | 3345783 | Closed | Closed |  | 2024-08-26 |  |  | Defect Confirmed - Repair Complete | 116
Sundance | Active | 23 | NTN Main Bearing Rolling Element Issue | Sweep | Main Bearing | 2024-02-06 |  | 2 | 4/17/24 - Turbine DNR'd. 2/6/24 - Turbine is currently power derated to 35% after borescoping for temperature issues. | Final Report Needed | 3268328 | Cancelled | Cancelled |  | 2024-04-03 |  |  | Defect Confirmed - Repair Complete | 57
Maverick | Resolved | 23 |  | Warning | Generator Outboard | 2022-05-05 |  | 6 |  | CMSGENB | 2929323 | Closed | Closed |  | 2022-11-16 | 5/9 - clear progression in timeseries, increase past warning to alarm setpoint. Impacts = 10g in timebase, ORBP harmonics MAX = 1g. Bearing is fine to run until impacts exceed 25-30g, ORBP peak exceeds 3-4g, inspect gen bearings, 5/31 - waiting on inspection findings, likely warranty claim, 6/23 - elevating work order priority, 8/23 - WO in progress, 10/26 - WO comments mention replacing coupler, top hat, and realignment - dramatic signal reduction, reduce to cat 1, 11/16 - resolve |  | False Positive - No Action | 195
Bethel | Active | 24 | HSS Bearing Damage | Case Tracking | Helical High Speed Stage | 2023-01-25 | 2024-09-25 | 2 | Check HSS bearing for damage | Monitor | 3080383 | Closed | Closed |  |  |  |  | Case In Progress | -44951
Upstream | Resolved | 24 |  | Change 1 | 1st Planetary Stage | 2022-10-13 |  | 1 |  | Monitor | [5 empty] | 2022-11-29 |  | False Positive - No Inspection | -44847
Santa Rita East | Resolved | 24 | Main Bearing Accelerometer Issue | Instrumentation | Main Bearing | 2023-01-23 |  | 5 | Main bearing sensor is currently reading a fluctuation in bias voltage, please inspect wiring and connections. Replace sensor if needed. Please reach out to Andrew Barndt if you have any questions. | CMSTRBLSHOOT | 3071067 | Closed | Closed |  | 2023-01-26 |  |  | Defect Confirmed - Repair Complete | 3
Santa Rita East | Resolved | 24 |  | Alarm | Main Bearing | 2021-10-10 |  | 1 |  | Monitor for Failure | 2616811 | Closed | Closed |  |  |  |  | Case In Progress | -44479
Santa Rita East | Resolved | 24 |  | Instrumentation | Main Bearing | 2022-04-04 |  |  | Open Sensor Wiring | CMSTRBLSHOOT | 2907702 | Closed | Closed |  |  | 2022-04-12 |  |  | -44655
Plymouth | Resolved | 24 | Potential Generator Inboard Issue | Sweep | Generator Inboard | 2023-03-03 |  | 3 | Grease and noise quality appeared normal, continue to monitor for progression. | Monitor | 3093053 | Closed | Closed |  |  |  |  | Case In Progress | -44988
Bethel | Resolved | 25 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-07-26 |  | 4 | 7/26 - CMS monitor not receiving speed signal, please troubleshoot using attached guide. | CMSTRBLSHOOT | 3162490 | Closed | Closed |  | 2023-10-27 |  |  | Defect Confirmed - Repair Complete | 93
Bethel | Active | 25 | Main Bearing raceway damage | Case Tracking | Main Bearing | 2023-02-03 |  | 3 | 2/28/24 - Turbine is down until repair. 2/3/23 -Roller - larger indentations in 3, 6, and 9 o clock. Q2 2024 est replacement date. | Final Report Needed | 3133989 | Closed | Closed |  |  | 2/3 - limited growth in past 6 mo |  | Defect Confirmed - Awaiting Repair | -44960
Deuel Harvest | Resolved | 25 |  | Warning | Generator Inboard | 2021-02-08 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44235
Sundance | Active | 25 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3201739 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Thunderhead | Active | 25 | instrumentation/Keyphasor | Instrumentation | CMS Monitor | 2024-05-28 |  | 5 | 5/28/24 - Gearbox sensor 1 is at -22V, and Keyphasor is showing as invalid | CMSTRBLSHOOT | 3356850 | Closed | closed |  |  |  |  | Case In Progress
Red Barn | Active | 25 | Non-Ferrous Debris Rising | Particle Counter | Particle Counter | 2024-04-13 |  | 6 | 4/13/24 - Non-ferrous debris had slight increase, ferrous debris as well. | Monitor | [7 empty] | Case In Progress | -45395
Sundance | Resolved | 25 |  | Warning | 2nd Planetary Stage | 2021-09-20 |  | 5 |  | Monitor | [5 empty] | 10/8 - ZF Flash revision, atypical peak at 19.063X(21.813Hz) on frequency spectrum, 1/5 - low concern, 1/25 - FFT peak, 2/16 - Peak at Stage 2 Carrier DnWind ORBP, 2/17 - Stage 2 GMF carrying planet/ring fault sidebands, max 0.01g, stage 2 also shows stage 3 GMF with gear fault sidebands, monitor, 6/1 - limited progression, 6/24 - some progression in stage 2 bearing damage, 8/26 - monitor for ORBP increases, HSS RS IRBP peak with pinion sidebands, 11/15 - limited progression, 12/6 - additional DEI warning, |  |  | -44459
Maverick | Active | 25 | Timken Main Bearing BS2X | Sweep | Main Bearing | 2023-04-18 |  | 1 | 10/27/23 - Turbine was repaired, repair report needed. 4/18/23 - Borescope found indents, possible pitting, and slight cage damage. Turbine is currently thrust derated, CMS will continue to monitor for progression. | Final Report Needed | 3114111 | Closed | Closed |  | 2023-10-27 |  |  | Defect Confirmed - Awaiting Repair | 192
Santa Rita East | Resolved | 25 | 1st Stage Planetary Gearing Issue | Alarm | 1st Planetary Stage | 2022-12-03 |  | 1 | Broken planetary gear. Turbine is down and awaiting replacement. | Final Report Needed | [7 empty] | Defect Confirmed - Repair Complete | -44898
Santa Rita East | Active | 25 | Potential Main Bearing Issue | Sweep | Main Bearing | 2023-12-04 |  | 2 | 1/9/23 - Possible minor surface damage on outer race and roller elements, continuing to monitor. 12/4/23 - Recommend main bearing borescope within 1 month from 12/4/23 | Monitor | 3233055 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45264
Bethel | Resolved | 26 | Generator Outboard ORBP | Warning | Generator Outboard | 2023-08-21 |  | 3 | 8/21/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | CMSGENB | 3176864 | Closed | Closed |  | 2023-10-23 |  |  | Defect Confirmed - Repair Complete | 63
Upstream | Resolved | 26 |  | Change 1 | 1st Planetary Stage | 2022-01-04 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44565
Bethel | Resolved | 26 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-05-10 |  | 5 | Verify PEM/Keyphasor is using KPH2 on the 60M100 | CMSTRBLSHOOT | 3125156 | Closed | Closed |  | 2023-06-26 |  |  | Defect Confirmed - Repair Complete | 47
Deuel Harvest | Resolved | 26 |  | Alarm | 1st Planetary Stage | 2021-08-15 |  | 3 |  | Monitor | [6 empty] | 11/17 - no data flow, controller issue, <archived notes>, 6/10 - increasing trend stopped by outage, direct signal has fewer peaks below warning setpoint, likely roller damage to S2 PC BRG, 6/28 - suspicious impact pattern in the timebase, Stage 1 envelope indicates damage to S1 PC BRG GS rollers, 7/19 - limited progression, reduce to cat 2, 9/2 - Direct signal reduced after March increase, 2/2 - controller issue apparently resolved, vibration remains below warning setpoint, FFT indicates damage to stage 1 carrier RS, 2/23 - spike on 2/11, 3/18 - No sidebands to indicate gearing issue, peak at stage 1 mesh ring fault frequency, monitor, 4/5 - stage 1 direct shows progression through March, high res FFT shows dense peaks at low frequencies, no peaks in enveloping spectrum, timebase suggests potential sensor mounting issue, | False Positive - Sensor Issue | -44423
Deuel Harvest | Resolved | 26 |  | EOW | Main Bearing | 2022-08-17 |  | 1 |  | EOW Claim | [7 empty] | False Negative | -44790
Santa Rita East | Resolved | 26 |  | Warning | 1st Planetary Stage | 2021-08-31 |  | 5 |  | Monitor | [6 empty] | SER Ring Fault GFED has been peaking above the alarm setpoint since 8/31, diverging from typical operation profile. Frequency spectrum does not show signs of damage and direct vibration profile is normal. Borescope when either becomes concerning. 12/28 - 5349g peak in timeseries 1/13 - 3X harmonics are present at low frequencies in the FFT, potential damage to stage 1 planet gear bearing inner race, monitor, | Case In Progress | -44439
Santa Rita East | Active | 26 | NTN Main Bearing Outer Race Issue | Sweep | Main Bearing | 2024-06-19 | 2024-11-22 | 2 | 8/29/24 - Sent out for re-borescope. 8/5/24 - June borescope did not find many damages, continue to monitor. 6/19/24 - Recommend borescoping this main bearing within 2 weeks from 6/19/24 with focus on outer race and rollers. | Repair Pending | 3411596 | Closed | Closed |  |  |  |  | Miss - Defect Not Caught | -45462
Sundance | Resolved | 26 | Main Bearing Accelerometer | Instrumentation | Main Bearing | 2023-03-14 |  | 5 | Sensor is reading an open circuit, please inspect wiring and connections. | CMSTRBLSHOOT | 3097551 | Closed | Closed |  | 2023-11-18 |  |  | Defect Confirmed - Repair Complete | 249
Maverick | Resolved | 26 |  | Warning | Generator Inboard | 2022-01-03 |  | 6 |  | Monitor |  |  |  |  | 2022-08-23 | 2/15 - standalone peak to alarm setpoint, monitor |  | False Positive - No Action | 232
Maverick | Active | 26 | Main Bearing Issue | GE Alert | Main Bearing | 2022-04-18 |  | 2 | 4/26 - GE Alert, minimal progression, 5/31 - slight indications of outer race damage, waiting on inspection images, 6/23 - high res spectrum shows clear bearing fault harmonics, likely damage to ORBP, 10/26 - temps are ok, fault harmonics remain prominent, 11/16 - elevated work order priority, 1/11 - damage confirmed by scope, recommending 50% derate 1/12/23 - GE Recommended shutdown of turbine | Final Report Needed | 2920947 | Closed | Closed |  |  | 4/26 - GE Alert, minimal progression, 5/31 - slight indications of outer race damage, waiting on inspection images, 6/23 - high res spectrum shows clear bearing fault harmonics, likely damage to ORBP, 10/26 - temps are ok, fault harmonics remain prominent, 11/16 - elevated work order priority, 1/11 - damage confirmed by scope, recommending 50% derate 1/12/23 - GE Recommended shutdown of turbine |  | Defect Confirmed - Awaiting Repair | -44669
Sundance | Resolved | 26 | 1st Planetary Stage Accelerometer | Instrumentation | 1st Planetary Stage | 2023-12-04 |  | 5 | 12/4/23 - 1st planetary stage sensor was swapped with bad main bearing sensor, recommend replacing 1st planetary stage accelerometer. | CMSTRBLSHOOT | 3233126 | Closed | Waiting on Parts |  | 2024-09-17 |  |  | Defect Confirmed - Repair Complete | 288
Deuel Harvest | Resolved | 26 | 1st Planetary Stage Sensor Issue | Instrumentation | 1st Planetary Stage | 2023-01-17 |  | 5 | 1/17/23 - Sensor giving erroneous readings, replace 1st planetary sensor | CMSTRBLSHOOT | 3069057 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Repair Complete | -44943
Thunderhead | Resolved | 26 | Main Bearing Sensor Issue | Instrumentation | Main Bearing | 2023-02-14 |  | 5 | Swap MB and S1 sensors and contact CMS Team for validation | CMSTRBLSHOOT | 3083963 | Closed | Closed |  |  | 2/14 - electrical noise? |  | Case In Progress | -44971
Bethel | Resolved | 27 | Gen Outboard Bearing Damage | Case Tracking | Generator Outboard | 2023-01-25 |  | 2 | 9/18/23 - Replace generator bearings 7/11/23 - Grease added to generator bearings | Longterm Watchlist | 3072186 | Closed | Closed |  | 2023-12-19 |  |  | Defect Confirmed - Repair Complete | 328
Bethel | Resolved | 27 |  | Alarm | Generator Outboard | 2022-01-31 |  | 3 |  | GENBCHECK | Create WO |  | #N/A |  | 2023-01-25 | 2/1 - NDE gen bearing signal has been above the alarm setpoint since late October. 20-30g impacts in the timebase, 3g peak at ORBP, 1 g peak at IRBP, inspect to determine RUL and plan for repair |  | Case In Progress | 359
Bethel | Resolved | 27 |  | Warning | Helical High Speed Stage | 2022-01-14 |  | 5 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - Stage 3 FFT shows 0.2g pinions fault sidebands with 1g peak at 2X GMF, timeseries shows Increases over the warning setpoint in late November and December, monitor for additional DEI events to indicate progressing damage |  | Case In Progress | 376
Deuel Harvest | Resolved | 27 |  | Warning | Helical High Speed Stage | 2022-09-16 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44820
Santa Rita East | Resolved | 27 |  | Alarm | 2nd Planetary Stage | 2022-06-12 |  | 5 | [9 empty] | Case In Progress | -44724
Santa Rita East | Resolved | 27 |  | Instrumentation | 2nd Planetary Stage | 2022-08-08 |  |  | Check sensor mounting | CMSTRBLSHOOT | 2984185 | Closed | Closed |  |  | 2022-08-11 |  |  | -44781
Deuel Harvest | Active | 27 | Potential MB inner race issue | Sweep | Main Bearing | 2024-03-21 |  | 2 | 4/01/24 - Borescope/inspection found bands of pitting on races and rollers, as well as some light spalling. 3/21/24 - CMS indicates MB issue, please perform full Main Bearing borescope | Repair Pending | 3320394 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45372
Maverick | Active | 27 | Main Bearing BS2X Issue | Sweep | Main Bearing | 2024-09-17 |  | 2 | 9/19/24 - AEP Requested 50% derate. 9/17/24 - Recommend borescoping this main bearing within 2 weeks from 9/17/24 with focus on outer race and rollers. | Repair Pending | 3428153 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45552
Upstream | Active | 27 | 1st Stage Planetary Bearing Issue | Sweep | 1st Planetary Stage | 2023-07-17 |  | 3 | Currently derated. 5/21/24 - sent out for re-borescope due to particle accumulation and spectrum increase since last borescope. 9/5/23 - Borescope found early stage planetary bearing spalling, continuing to monitor via CMS. | Longterm Watchlist | 3353466 |  | Ready to Schedule | Q1 2025 |  |  |  | Defect Confirmed - Awaiting Repair | -45124
Sundance | Resolved | 27 | Generator Inboard ORBP | Warning | Generator Inboard | 2022-07-31 |  | 2 | Please inspect generator grease and noise quality, upload results to HUVR. | Repair Pending | 3085673 | Closed | Closed |  |  | 8/1 - Direct signal trending slowly up since Feb 2022, inspect/add grease when signal exceeds alarm, 8/2 - additional ORBP alarm and Direct signal warning, highest amplitudes in mode 2, adding CMSGENB to add grease to both bearings, next climb, 8/26 - bearings noisy while running, Dark or split grease in both grease traps - added 1/2 tube kluberplex to each bearing, vibration has reduced on both bearings, DE has most damage. Monitor for replacement, 10/26 - DE bearing is trending up, replace when alarm is exceeded, 11/15 - spike to alarm and return to below warning vibration |  | True Positive | -44773
Upstream | Resolved | 28 |  | Warning | 1st Planetary Stage | 2021-12-14 |  | 4 |  | CMSGBXBORE | 2717470 | Closed | Closed |  |  | 2022-06-03 |  | False Positive - Sensor Issue | -44544
Upstream | Resolved | 28 |  | Warning | Main Bearing | 2021-10-18 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 |  | 11/3 - pulses in timebase indicate damage to outer race of the main bearing, step change in vibration amplitude after august 21, 11/30 - Impacts in timebase are concerning, 0.004g peak at cage fault frequency, monitor, 3/4 - monitor for main bearing direct to hit warning setpoint, 9/6 - frequent impacts in the timebase, 12/19 - DNR for failed yaw drive, | Case In Progress | 463
Upstream | Resolved | 28 |  | Instrumentation | 1st Planetary Stage | 2022-08-18 |  |  | Check sensor mounting | CMSTRBLSHOOT | 2992339 | Closed | Closed |  | 2022-08-25 |  | 8/18 - stage 1 alarms persist |  | 7
Bethel | Resolved | 28 | Generator Outboard ORBP | Warning | Generator Outboard | 2024-04-29 |  | 3 | 9/16/24 - Replace generator bearing. 4/29/24 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact CMSEngineers_OSW@invenergyllc.com for support | Repair Pending | 3343172 | Closed | Closed |  | 2024-11-07 |  |  | Defect Confirmed - Repair Complete | 192
Maverick | Active | 28 | Timken Main Bearing BS2X | Sweep | Main Bearing | 2023-05-15 |  | 1 | 10/27/23 - Turbine was repaired, repair report needed. 8/1/23 - Turbine DNR and waiting replacement | Final Report Needed | 3126189 | Closed | Closed |  | 2023-10-27 |  |  | Defect Confirmed - Awaiting Repair | 165
Sundance | Resolved | 28 |  | Warning | Helical High Speed Stage | 2022-01-20 |  | 3 |  | Monitor | 2736741 | Closed | Closed |  | 2022-03-08 | 1/25 - GE Alert requested HSS Check, vibration has remained at warning setpoint for full operating life, 2/16 - GE inspection didn't find any damage, 3/8 - resolving |  |  | 47
Deuel Harvest | Resolved | 28 | Main Bearing Accelerometer | Instrumentation | Main Bearing | 2023-03-15 |  | 5 | ​Main Bearing accelerometer is currently giving erroneous readings, please replace sensor. | CMSTRBLSHOOT | 3099322 | Closed | Ready To Schedule |  |  |  |  | Case In Progress | -45000
Santa Rita East | Active | 28 | SKF Main Bearing Issue | Alarm | Main Bearing | 2022-12-22 |  | 1 | Turbine currently down and awaiting main bearing replacement. | Final Report Needed | 3059666 | Closed | Closed |  |  |  |  | Case In Progress | -44917
Bethel | Resolved | 29 | Elevated NDE gen bearing vibration | Alarm | Generator Outboard | 2023-05-16 | 2024-01-01 | 2 | 11/2/23 - Recommend purging bearing grease to extend life, bearing replacement likely needed in 1-3 months. 6/30/23 - Burnt grease found, grease added | CMSGENB | 3218485 | Closed | Closed |  | 2024-01-05 |  |  | Defect Confirmed - Repair Complete | 234
Upstream | Resolved | 29 |  | Warning | Helical High Speed Stage | 2022-01-18 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 |  | 2/8 - peaks to warning setpoint, monitor, 4/15 - stage 3 direct signal has remained near 10g for full operating life, slight increasing trend, not rapid, 6/17 - HSS bearing fault harmonics at higher frequencies, 11/10 - recent decrease in S3 direct signal, likely mislaignment in S3 | Case In Progress | 371
Bethel | Resolved | 29 |  | Warning | 1st Planetary Stage | 2021-09-30 |  | 6 |  | Monitor |  |  |  |  | 2023-01-25 |  |  | Case In Progress | 482
Bethel | Resolved | 29 |  | Warning | Generator Outboard | 2021-10-04 |  | 5 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - NDE gen bearing signal has remained above the warning setpoint since July. Timebase hitting 10g's, 1g peak at ORBP, 0.5g peak at IRBP |  | Case In Progress | 478
Upstream | Resolved | 29 |  | Warning | Main Bearing | 2021-09-01 |  | 5 |  | Monitor | [6 empty] | 10/1 - ~2.5g pulses in timebase, 11/30 -peak to alarm on 10/26-28. Main Bearing ORBP indicates potential damage, along with frequency spectrum peak at ball spin fault frequency, 2/8 - continue to monitor, | Case In Progress | -44440
Santa Rita East | Resolved | 29 |  | Instrumentation | Main Bearing | 2023-01-18 |  |  | Main bearing sensor is currently reading an open circuit, please inspect wiring and connections. Replace sensor if needed. Please reach out to Andrew Barndt if you have any questions. | CMSTRBLSHOOT | 3069367 | Closed | Closed |  | 2023-01-21 |  |  | Defect Confirmed - Repair Complete | 3
Santa Rita East | Resolved | 29 |  | Particle Counter | Particle Counter | 2022-12-13 |  | 5 |  | Monitor | [8 empty] | -44908
Maverick | Active | 29 | Timken Main Bearing BS2X Signature | Sweep | Main Bearing | 2024-08-26 |  | 2 | 8/26/24 - Recommend borescoping this main bearing within 2 weeks from 8/26/24 with focus on outer race and rollers. | Repair Pending | 3409524 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45530
Santa Rita East | Active | 29 | Main Bearing BS2X | Sweep | Main Bearing | 2023-03-29 |  | 1 | 7/24/23 - CMS signatures have increased in amplitude, turbine to be DNR'd until replacement can be made. | Final Report Needed | 3104829 | Closed | Closed |  | 2023-08-28 |  |  | Defect Confirmed - Repair Complete | 152
Santa Rita East | Active | 29 | ZF S1 Planet Bearing Issue | Alarm | 1st Planetary Stage | 2023-01-25 |  | 2 | Moderate S1 planetary bearing and early HSS DnWind bearing damage shown in the borescope. Main bearing is also failing and GBX should be bundled with the MB repair. GBX likely has ~1 year left of runtime, added to the MCFL. | Final Report Needed | 3072023 | Closed | Closed |  | 2023-08-28 |  |  | Defect Confirmed - Repair Complete | 215
Bethel | Resolved | 30 | High Speed Stage Accelerometer | Instrumentation | Helical Intermediate Stage | 2023-09-25 |  | 4 | 9/25/23 - High speed stage accelerometer's bias voltage is unsteady. Please investigate sensor and harness for looseness. | CMSTRBLSHOOT | 3196479 | Closed | Closed |  | 2023-11-01 |  |  | Defect Confirmed - Repair Complete | 37
Upstream | Resolved | 30 |  | Warning | Main Bearing | 2022-12-22 |  | 6 | [6 empty] | 2022-01-09 |  |  |  | -347
Santa Rita East | Resolved | 30 | ZF S1 Planet Bearing/S2 Carrier Bearing Issue | Warning | 2nd Planetary Stage | 2021-11-23 |  | 1 | Damage found in the 1st and 2nd stage planets. Chipping found on 1 Ring | Final Report Needed |  |  |  |  | 2023-06-20 |  |  | Defect Confirmed - Repair Complete | 574
Upstream | Active | 30 | Main Bearing ORBP Damage | Sweep | Main Bearing | 2023-05-24 |  | 2 | ORBP fault harmonics, continuing to monitor. | Monitor | [7 empty] | Case In Progress | -45070
Upstream | Resolved | 31 | Elevated NDE Gen Bearing Vibration | Warning | Generator Outboard | 2023-03-03 |  | 2 | Planning to replace both bearing, team is worried about failing tach, shutdown if vibrations increase | Repair Pending | 3095072 | Closed | Closed |  | 2023-06-19 | 5/15 - Ryan Kudera sent videos of NDE noise, some abnormal rumbling. Grease added to both bearings, immediate reduction in vibration, 6/1 - reopening |  | Defect Confirmed - Repair Complete | 108
Upstream | Resolved | 31 |  | Warning | Generator Outboard | 2022-08-07 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 |  | 8/18 - 10g impacts, 1g ORBP and IRBP peak in mode 2, inspect, add grease when alarm is hit, 11/10 - reduce to cat 1, | Case In Progress | 170
Deuel Harvest | Resolved | 31 |  | Alarm | 1st Planetary Stage | 2022-06-27 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44739
Bethel | Resolved | 31 | Generator Inboard ORBP | Warning | Generator Inboard | 2024-02-22 | 2024-09-05 | 3 | 8/7/24 - Grease purge appears to be working, continue to monitor. 2/22/24 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | Monitor | 3303834 | Closed | Closed |  | 2024-07-08 |  |  | Defect Confirmed - Repair Complete | 137
Plymouth | Resolved | 31 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-11 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988833 | Cancelled | Cancelled | [5 empty] | -44784
Bethel | Active | 31 | Potential 1st Planetary Stage Bearing Issue | Warning | 1st Planetary Stage | 2024-03-04 | 2024-11-05 | 3 | 4/1/24 - Borescope found minor to moderate spalling on RS planetary bearings, recommend replace in Q3 2025. 3/4/24 - Recommend full gearbox borescope with focus on the 1st planetary stage within 1 month from 3/4/24. | Longterm Watchlist | 3312706 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45355
Thunderhead | Active | 31 | Potential Generator Inboard Issue | Alarm | Generator Inboard | 2024-11-13 | 2025-03-12 | 5 | 11/13/24 - CMS indicates potential generator inboard issue,continue to monitor for progression | CMSGENB | 3465561 |  | Ready to Schedule |  |  |  |  | Case In Progress | -45609
Thunderhead | Active | 31 | Generator Inboard ORBP | Alarm | Generator Inboard | 2024-11-15 |  | 3 | 11/15/24 - CMS indicates Generator Inboard ORBP Issue sent out for inspection/grease | CMSGENB | 3465561 |  | Ready to Schedule |  |  |  |  | Case In Progress | -45611
Upstream | Active | 31 | Stage 2 Planertary OBRP/IRBP | Sweep | 2nd Planetary Stage | 2024-05-08 |  | 3 | 11/7/24 - Potential re-scope request. 5/8/24 - CMS indicates Stage 2 ORBP/IRBP issue, work order made for inspection/borescope. | CMSGBXBORE | 3348540 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45420
Upstream | Active | 31 | Possible Generator DE sensor issue | Instrumentation | Generator Inboard | 2024-01-29 |  | 5 | 1/29/24 - CMS is showing a bias volatge of -22 in the generator IDE, work order sent out to troubleshoot issue | CMSTRBLSHOOT | 3261992 | Closed | Closed |  |  |  |  | Case In Progress | -45320
Upstream | Active | 31 | Particle Counts Rising | Particle Counter | Particle Counter | 2024-03-04 |  | 6 | 3/4/24 - Particle counts rising, possible planetary bearing issue. Check in on this when followup date is hit. | Monitor | [7 empty] | Case In Progress | -45355
Upstream | Active | 31 | CMS troubleshoot | Instrumentation | CMS Monitor | 2024-05-14 |  | 5 | 5/14/24 - CMS shows bias voltage for generator inboard sensor at -22 V. | Monitor | 3261992 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45426
Santa Rita East | Active | 31 | Potential Planet Gear Issue | Alarm | 1st Planetary Stage | 2023-08-22 |  | 1 | 9/7/23 - Gearbox split and oil leakage found, likely planetary gearing liberation. Turbine to remain down until gearbox replacement can be made. 8/28/23 - Borescope showed possible debris run over and S1 planetary bearing spalling, continue to monitor CMS and particle counters. 8/22/23 - Recommend full gearbox borescope with focus on 1st planetary stage within 24 hours. | Final Report Needed | 3177168 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45160
Bethel | Resolved | 32 | DE Gen Bearing Sensor Issue | Instrumentation | Generator Inboard | 2023-02-03 |  | 5 | Check DE bearing sensor harness for opens | CMSTRBLSHOOT | 3078019 | Closed | Closed |  | 2023-03-16 |  |  | Defect Confirmed - Repair Complete | 41
Bethel | Resolved | 32 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-01-25 |  | 5 | Troubleshoot Keyphasor | CMSTRBLSHOOT | 3132274 | Closed | Closed |  | 2023-06-06 |  |  | Defect Confirmed - Repair Complete | 132
Upstream | Resolved | 32 |  | Change 1 | 2nd Planetary Stage | 2022-08-04 |  | 1 |  | Monitor |  |  |  |  | 2022-11-29 | 8/18 - Envelope shows elevated input and IMS shaft harmonics, potential S2 PC BRG RS damage, 11/10 - limited progression |  | False Positive - No Inspection | 117
Bethel | Resolved | 32 | Generator Inboard IRBP issue | Alarm | Generator Inboard | 2023-12-28 | 2024-03-20 | 3 | 12/28 - Generator inboard is showing signs of IRBP issue, but direct hasn't progressed far enough to send out yet. Continue to monitor for direct increase or specturm changes. | Monitor | [7 empty] | Case In Progress | -45288
Plymouth | Resolved | 32 | Generator Inboard ORBP | Warning | Generator Inboard | 2023-11-10 |  | 2 | 12/18/23 - Warranty Claim submitted: 6608694 .11/10/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection | Monitor | 3224601 | Closed | Closed |  |  |  |  | Case In Progress | -45240
Thunderhead | Active | 32 | Elevated DE Gen Bearing Vibration | Warning | Generator Inboard | 2023-04-11 |  | 5 | 3/14/24 - Awaiting direct increase, continuing to monitor. 4/11/23 - Add grease to both bearings | Monitor | 3111897 | Closed | Closed |  |  |  |  | Case In Progress | -45027
Upstream | Resolved | 32 | S1 Planetary stage bearing | Change 1 | 1st Planetary Stage | 2022-12-17 | 2024-06-07 | 3 | 2/1/24 - Estimated repair date Q2 '24. 4/11/23 - Borescope confirmed damage to S1 PS BRGs, S2 PC BRG ORBP, expecting 6-8 months RUL with 50% derate | Final Report Needed | 3070740 | Closed | Closed |  |  | 3/24 - added to MCFL longterm watchlist |  | Defect Confirmed - Repair Complete | -44912
Bethel | Resolved | 33 |  | Alarm | 1st Planetary Stage | 2022-01-31 |  | 3 | [6 empty] | 2023-01-25 | 2/1 - Frequent peaks above the alarm setpoint for stage 1 direct. 1X GMF has low amplitude Planet fault sidebands. Borescope over the summer found damage to LSIS shaft gear, repair pending. Additional damage has likely been sustained since the borescope inspection, may want to nudge GE |  | Case In Progress | 359
Deuel Harvest | Resolved | 33 |  | Instrumentation | CMS Monitor | 2022-04-05 |  |  | wait | [5 empty] | 2022-06-08 |  |  |  | 64
Plymouth | Resolved | 33 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-04-10 |  | 3 | Please inspect keyphasor system using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3110514 | Closed | Closed |  | 2023-04-20 |  |  | Defect Confirmed - Repair Complete | 10
Plymouth | Resolved | 33 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-11 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988834 | Cancelled | Cancelled | [5 empty] | -44784
Plymouth | Resolved | 33 | CMS Monitor/Keyphasor Issue | Instrumentation | Keyphasor | 2024-01-22 |  | 3 | 1/22/24 - ​Not receiving any data/bad data from CMS monitor. Possible keyphasor issue or netcom monitor. Reach out to abarndt@invenergy.com for troubleshooting support. | CMSTRBLSHOOT | 3257217 | Closed | Ready to Schedule |  | 2024-02-07 |  |  | Defect Confirmed - Repair Complete | 16
Deuel Harvest | Resolved | 34 |  | Warning | Main Bearing | 2021-08-22 |  | 3 | [7 empty] | 2022-02-02 |  | False Positive - Sensor Issue | -44430
Santa Rita East | Resolved | 34 |  | Alarm | Helical High Speed Stage | 2021-03-04 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44259
Maverick | Active | 34 | Generator Inboard ORBP | Warning | Generator Inboard | 2024-04-15 | 2024-10-15 | 3 | 4/25/24 - Audible inspection did not find anything, recommend adding grease. 4/15/24 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact CMSEngineers_OSW@invenergyllc.com for support | Monitor | 3333801 | Closed | Closed |  |  |  |  | Case In Progress | -45397
Santa Rita East | Active | 34 | SKF Main Bearing Issue | Case Tracking | Main Bearing | 2022-04-29 |  | 1 |  | Final Report Needed | [5 empty] | 2022-10-09 |  | Defect Confirmed - Repair Complete | -44680
Bethel | Resolved | 35 | Generator Outboard ORBP | Warning | Generator Outboard | 2023-11-20 | 2024-01-20 | 3 | 11/20/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | CMSGENB | 3227552 | Closed | Ready to Schedule |  | 2023-12-20 |  |  | Defect Confirmed - Repair Complete | 30
Upstream | Resolved | 35 |  | Warning | Helical High Speed Stage | 2021-10-13 |  | 1 |  | Monitor |  |  |  |  | 2022-11-29 | 6/17 - likely misalignment and HSS bearing issue, 9/6 - recent vibration drop, | New warning 10/13, low concern, 5/5 - new warning 4/12, harmonics between 2X and 3X GMF in stage 3, indicating bearing damage, limited progression in the past 6 months, | False Positive - No Inspection | 412
Santa Rita East | Resolved | 35 |  | Warning | 1st Planetary Stage | 2022-03-08 |  | 6 |  | Monitor | [7 empty] | Case In Progress | -44628
Maverick | Active | 35 | NTN Main Bearing BS2X Signature | Sweep | Main Bearing | 2024-05-16 |  | 2 | 7/31/24 - Derated to 50% .7/3/24 - Recommend borescoping this main bearing within 2 weeks from 7/3/24 with focus on outer race and rollers. 5/16/24 - CMS indicates potential Main bearing bs2x rolling elements issue, however signature can be seen in the spectrum through a couple of slides and might be an intermittent signature. Continue to monitor for progression. | Repair Pending | 3379442 | Closed | Closed |  |  |  |  | Case In Progress | -45428
Plymouth | Resolved | 35 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-11 |  | 5 | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988835 | Cancelled | Cancelled | [5 empty] | -44784
Sundance | Active | 35 | Oil Particle Communication Issue | Particle Counter | Particle Counter | 2023-10-04 |  | 4 | 10/4/23 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3201743 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45203
Bethel | Active | 36 | Main Bearing Failure | Case Tracking | Main Bearing | 2023-02-03 |  | 1 | (DNR) Main Bearing failure, take turbine offline until inspection is completed | Final Report Needed | 3096733 | Closed | Closed |  |  | CMSMB |  | Defect Confirmed - Turbine Failed | -44960
Bethel | Resolved | 36 |  | Warning | Helical High Speed Stage | 2021-07-14 |  | 6 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - Stage 3 direct has been just above the warning setpoint for a year. FFT shows a 0.231g peak at 17.078X stage 3 shaft speed. Unclear what is causing it. |  | Case In Progress | 560
Sundance | Active | 36 | NTN Main Bearing Rolling Element Issue | GE Alert | Main Bearing | 2023-04-07 | 2024-08-05 | 1 | 2/15/24 - Turbine derated to 50%. 7/12/23 - Borescope found roller indents, cage degradation, and outer race clouding with spalls. Continue to monitor. | Final Report Needed | [7 empty] | Case In Progress | -45023
Bethel | Resolved | 37 |  | Alarm | 1st Planetary Stage | 2021-10-11 |  | 3 |  | Borescope | Create WO |  | #N/A |  | 2023-01-25 | 2/1 - Sudden increase in timeseries starting in July 2021, 0.015g ring fault sidebands in stage 2 FFT, recommending borescope inspection |  | Case In Progress | 471
Santa Rita East | Resolved | 37 |  | Warning | 2nd Planetary Stage | 2022-07-21 |  | 6 |  | Monitor | [8 empty] | -44763
Santa Rita East | Resolved | 37 |  | Warning | Main Bearing | 2022-12-13 |  | 5 |  | Monitor | [8 empty] | -44908
Santa Rita East | Resolved | 37 |  | Alarm | Main Bearing | 2021-12-21 |  | 4 |  | Replacement | [5 empty] | 2022-01-31 |  | True Positive | -44551
Thunderhead | Active | 37 | Instrumentation issue gearbox sensor 1 | Instrumentation | CMS Monitor | 2024-05-28 |  | 5 | 5/28/24 - Gearbox sensor 1 is at -22V. | CMSTRBLSHOOT | 3356852 | Closed | Closed |  |  |  |  | Case In Progress
Upstream | Resolved | 38 |  | Warning | Helical High Speed Stage | 2021-06-13 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 |  | 4/15 - high res FFT shows bearing fault harmonics between 2X and 3X GMF, 6/17 - potential misalignment, 8/18 - reduce to cat 1, 9/29 - potential HSS bearing damage | Case In Progress | 590
Bethel | Resolved | 38 |  | Alarm | 1st Planetary Stage | 2022-01-27 |  | 3 |  | Borescope | Create WO |  | #N/A |  | 2023-01-25 | 2/1 - Stage 1 direct increased to the alarm setpoint in October 2021, low amplitude harmonics are present, indicating damage to stage 1 carrier. Stage 2 Planet faults are present in both the stage 1 & 2 FFT's. Borescope |  | Case In Progress | 363
Bethel | Resolved | 38 |  | Alarm | Generator Outboard | 2022-01-31 |  | 5 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - NDE gen bearing signal has increased to the alarm setpoint over the past year. Timebase had 10g impacts and a 1g peak at IRBP, monitor for failure |  | Case In Progress | 359
Bethel | Resolved | 38 | Gen Bearing Damage | Case Tracking | Generator Outboard | 2023-01-25 |  | 2 | Replace gen bearings | Repair Pending | 3072187 | Closed | Closed |  | 2023-08-24 |  |  | Defect Confirmed - Repair Complete | 211
Sundance | Active | 38 | NTN Main Bearing Rolling Element Issue | Sweep | Main Bearing | 2024-02-06 |  | 2 | 4/25/24 - Turbine DNR'd. 2/14/24 - Customer requested turbine be power derated to 50%. 2/6/24 - Recommend main bearing borescope and thrust derate at next possible opportunity. | Final Report Needed | 3268260 | Closed | Closed |  | 2024-04-25 |  |  | Defect Confirmed - Repair Complete | 79
Upstream | Active | 38 | Generator Inboard ORBP | Alarm | Generator Inboard | 2021-12-30 |  | 6 |  | Monitor | 2992349 | Closed | Closed |  |  |  | Inspection found dark metallic grease, recommended grease flush. 1/11 - DE Gen Bearing is approaching failure. 3.6g peak at ORBP fault frequency, 10-20g impacts in timebase. WO 2575705, WO 2717453, 3/25 - frequent peaks to alarm setpoint, 4g peak at ORBP, 4/15 - damage has been sustained by the DE gen bearing, trend has reduced to normal levels, continue to run. Hold off on inspection until trend increases to alarm setpoint, 8/18 - 10g impacts, alarm level peaks, | Defect Confirmed - Awaiting Repair | -44560
Sundance | Resolved | 38 |  | Alarm | 1st Planetary Stage | 2021-07-31 |  | 2 |  | Monitor | 2614348 | Closed | Closed |  | 2022-06-24 | significant modulation, guessing damage to ring gear, 3/8 - no major findings from GE Requested borescope. CMS Shows direct vibrations reduce to normal operation in December 2021. FFT shows low amplitude shaft harmonics, 6/1 - limited progression |  | False Postive - Sensor Issue | 328
Sundance | Resolved | 38 |  | Instrumentation | 1st Planetary Stage | 2022-03-08 |  |  | Check all Gearbox CMS sensors | CMSTRBLSHOOT | 2813529 | Closed | Closed |  | 2022-05-03 | 5/17 - Cody replaced gearbox sensor 1 per GE's request |  |  | 56
Santa Rita East | Active | 38 | Main Bearing Parking Marks | Sweep | Main Bearing | 2023-12-04 |  | 6 | 12/4/23 - April 2023 borescope found parking marks, continue to monitor for signature progressions | Monitor | [7 empty] | Case In Progress | -45264
Upstream | Resolved | 38 | Generator Ouboard OBRP | Warning | Generator Outboard | 2023-09-14 | 2024-05-02 | 3 | 9/14/2023 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings | Final Report Needed | 3191426 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -45183
Bethel | Active | 39 | Main Bearing Inner Raceway Damage | Sweep | Main Bearing | 2023-04-04 | 2024-06-20 | 6 |  | Monitor | [7 empty] | Case In Progress | -45020
Bethel | Active | 39 | HSS Bearing Damage | Case Tracking | Helical High Speed Stage | 2023-01-25 |  | 3 | 6/4/24 - Minor damages found on HSS DnWind Rear bearing.5/7/24 - Please perform a complete gearbox borescope with focus on the high speed stage at next tower climb. 1/25/23 - Monitor bearings for progression | CMSGBXBORE | 3347661 | Closed | Closed |  |  |  |  | Case In Progress | -44951
Bethel | Resolved | 39 |  | Alarm | Helical High Speed Stage | 2022-01-05 | [8 empty] | 2023-01-25 | 2/1 - MCFL entry created in 2020, unclear whether repair will proceed. CMS event indicate damage to stage 3 in addition to stage 1 carrier. |  | Case In Progress | 385
Bethel | Active | 39 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-09-16 |  | 3 | 9/16/24 - Generator speed signal (Keyphasor) is not communicating with CMS monitor. Check gen encoder wiring and orientation, check PEM and connection to KPH. | CMSTRBLSHOOT | 3427539 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45551
Deuel Harvest | Active | 39 | S2 SER Planet alarm | Alarm | 2nd Planetary Stage | 2024-02-20 | 2025-04-02 | 5 | 2/20/2024 - CMS alarm went off in the s2 set planet fault group. Continue to monitor | Monitor | [7 empty] | Case In Progress | -45342
Sundance | Active | 39 | 1st Planetary Stage Accelerometer | Instrumentation | 1st Planetary Stage | 2024-09-12 |  | 5 | 9/12/24 -1st planetary stage sensor reading an open circuit, please investigate wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3426667 | Completed Awaiting Review | Ready to Schedule |  |  |  |  | Case In Progress
Sundance | Active | 39 | Potential NTN Main Bearing Outer Race Issue | Sweep | Main Bearing | 2024-03-05 |  | 2 | 3/28/24 - Turbine placed on DNR list. 3/12/24 - Customer requested derate to 35%. 3/7/24 - Customer requested derate to 80%. 3/5/24 - Recommend main bearing borescope within 2 weeks from 3/5/24. Recommend 50% derate as well. | Final Report Needed | 3313203 | Closed | Closed |  | 2024-04-28 |  |  | Defect Confirmed - Repair Complete | 54
Thunderhead | Resolved | 39 | Main Bearing Sensor Issue | Instrumentation | Main Bearing | 2023-01-24 |  | 5 | Check harness for open wiring | CMSTRBLSHOOT | 3071331 | Closed | Closed |  | 2023-07-10 |  |  | Defect Confirmed - Repair Complete | 167
Bethel | Resolved | 40 | Generator Outboard Bearing Issue | Alarm | Generator Outboard | 2023-02-23 |  | 3 | Monitor bearings for replacement | Longterm Watchlist | 3086600 | Closed | Closed |  | 2024-01-08 |  |  | Defect Confirmed - Repair Complete | 319
Upstream | Resolved | 40 |  | Warning | Helical High Speed Stage | 2022-05-29 |  | 3 |  | Monitor | [7 empty] | Case In Progress | -44710
Bethel | Resolved | 40 |  | Alarm | Generator Outboard | 2022-01-31 |  | 5 |  | GENBCHECK | Create WO |  | #N/A |  | 2023-01-25 | 2/1 - NDE gen bearing shows signal if hitting the alarm setpoint. Timebase shows 15g impacts, FFT shows 1.1g peak at IRBP, inspect to determine RUL |  | Case In Progress | 359
Bethel | Resolved | 40 |  | Warning | Helical High Speed Stage | 2022-01-31 |  | 6 |  | Check Gearbox CMS Sensors | Create WO |  | #N/A |  | 2023-01-25 | 2/1 - direct signal has remained between warning and alarm setpoint since June, FFT shows 0.3g peak at ORBP for the HSIS UpWind bearing. Signal jumped to the alarm setpoint immediately following return to service after gearbox replacement, suspecting loose sensor mounting. |  | Case In Progress | 359
Deuel Harvest | Resolved | 40 |  | EOW | Main Bearing | 2022-09-06 |  | 1 |  | EOW Claim | [7 empty] | False Negative | -44810
Thunderhead | Active | 40 | Potential 2nd Stage Carrier Bearing Issue | Particle Counter | Particle Counter | 2024-04-11 | 2025-03-06 | 6 | 5/7/24 - Please perform a full gearbox borescope with focus on the 2nd planetary stage at next tower climb. 4/11/24 - Oil particles are rising,check back up in a few weeks. | CMSGBXBORE | 3347446 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45393
Plymouth | Resolved | 40 | CMS Monitor/Keyphasor Issue | Instrumentation | Keyphasor | 2024-01-22 |  | 3 | 2/6/24 - Turbine has been down, keeping case open for tracking purposes. 1/22/24 - ​Not receiving any data/bad data from CMS monitor. Possible keyphasor issue or netcom monitor. Reach out to abarndt@invenergy.com for troubleshooting support. | CMSTRBLSHOOT | 3257218 | Closed | Closed |  |  |  |  | Case In Progress | -45313
Plymouth | Resolved | 40 | NTN Main Bearing Outer Race Damage | Warning | Main Bearing | 2023-08-03 |  | 2 | 8/21/23 - Borescope showed some early surface damage to inner and outer races, continue to monitor CMS data and temps. 8/3/23 - Recommend main bearing borescope at next opportunity. | Monitor | 3169016 | Closed | Closed |  | 2024-05-08 |  |  | Defect Confirmed - Repair Complete | 279
Deuel Harvest | Resolved | 40 | Generator Inboard Accelerometer Issue | Instrumentation | Generator Inboard | 2023-01-30 |  | 5 | ​Generator inboard sensor is reading an open circuit bias voltage. Please inspect sensor harness, replace sensor if needed. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3073743 | Closed | Closed |  |  |  |  | Case In Progress | -44956
Bethel | Resolved | 41 |  | Warning | 1st Planetary Stage | 2022-01-29 |  | 6 | [6 empty] | 2023-01-25 |  |  | Case In Progress | 361
Bethel | Resolved | 41 |  | Warning | Generator Outboard | 2022-02-01 |  | 5 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - NDE gen bearing signal stays at the warning setpoint, 10g impacts in the timebase, FFT peaks at several fault frequencies (1g max) |  | Case In Progress | 358
Santa Rita East | Resolved | 41 |  | Change 1 | 1st Planetary Stage | 2022-06-01 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44713
Santa Rita East | Resolved | 41 |  | Warning | Generator Outboard | 2022-09-15 |  | 6 |  | Monitor | [8 empty] | -44819
Santa Rita East | Resolved | 41 | High Speed Stage Accelerometer | Instrumentation | Helical High Speed Stage | 2024-01-16 |  | 5 | 1/16/23 - High speed stage accelerometer is currently reading an open circuit. Please investigate sensors and wiring, replace sensor if needed. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3254943 | Closed | Ready to Schedule |  | 2024-01-22 |  |  | Defect Confirmed - Repair Complete | 6
Santa Rita East | Active | 41 | 1st Planetary Stage Gearing Issue | Warning | 1st Planetary Stage | 2023-04-04 |  | 1 | Borescope found planetary gearing damage, turbine to remain down until replacement is made | Final Report Needed | 3108178 | Closed | Closed |  |  |  |  | Defect Confirmed - Turbine Failed | -45020
Upstream | Resolved | 42 |  | Warning | Generator Outboard | 2021-08-16 |  | 1 |  | Monitor | 2575726 | Closed | Closed |  | 2022-08-18 |  |  | True Positive | 367
Deuel Harvest | Resolved | 42 |  | Instrumentation | CMS Monitor | 2022-04-05 |  |  | check monitor power and wiring, reboot | CMSTRBLSHOOT | 2943206 | Cancelled | Cancelled |  | 2022-07-25 |  | Self resolved? |  | 111
Santa Rita East | Resolved | 42 |  | Warning | Generator Outboard | 2022-09-19 |  | 6 |  | Monitor | [8 empty] | -44823
Maverick | Resolved | 42 |  | Warning | Main Bearing | 2021-07-28 |  | 6 |  | Monitor |  |  |  |  | 2022-12-06 | 3/10 - recent peaks to warning setpoint, no indicators in the FFT, 5/9 - timeseries trend is going down, 5/31 - monitor for peaks to warning setpoint, 6/23 - signal has reduced over the past months, 8/23 - low concern, 12/6 - temps are ok, resolving |  | False Positive - No Action | 496
Santa Rita East | Active | 42 | Main Bearing BS2X | GE Alert | Main Bearing | 2022-07-05 |  | 1 | thrust derate | Final Report Needed | [7 empty] | Case In Progress | -44747
Upstream | Active | 42 | Main Bearing Inner race issue | Sweep | Main Bearing | 2024-05-02 |  | 2 | Currently derated. 4/18/24 - Turbine may continue to operate as normal, brescope found inner/outer race damage, and roller damage. However, this turbine's expected to last roughly a year until replacement is needed. 3/21/24 - CMS indicates potential main bearing inner race issue. Please perform full main bearing borescope. | Longterm Watchlist | 3320349 | Closed | Closed | Q1 2025 |  |  |  | Defect Confirmed - Awaiting Repair | -45414
Upstream | Active | 42 | Main Bearing OR and Roller damage | Warning | Main Bearing | 2023-05-08 |  | 2 | Borescope found IR indents and gold grease, estimated replacement Q2 2024 | Monitor |  |  | Closed | Q3 2024 |  |  |  | Defect Confirmed - Awaiting Repair | -45054
Sundance | Resolved | 42 |  | GE Alert | 1st Planetary Stage | 2022-05-19 |  | 1 |  | Pending Replacement |  |  |  |  | 2022-10-20 | 5/19 - GE requests turbine is shutdown until it can be inspected. Spike is only in Stage 1 SER Planet Fault GFR SR3 - no increase in direct signal. Note whether any actual damage is found considering lack on evidence in the raw data, 6/1 - potential damage to S1 PC BRG GS raceway, waiting on borescope findings, 6/13 - Planet tooth crack found in borescope, 10/26 - resolving, RTS - keeping active until I can update the config, 11/15 - still waiting on replacement config, 12/7 - FDM2F, resolving |  | True Positive - GE Alert | 154
Upstream | Resolved | 42 | Generator Ouboard OBRP | Alarm | Generator Outboard | 2023-09-08 |  | 3 | 9/8/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | CMSGENB | 3187713 | Closed | Closed |  | 2024-02-25 |  |  | Defect Confirmed - Repair Complete | 170
Thunderhead | Resolved | 42 | Main Bearing Sensor Issue | Instrumentation | Main Bearing | 2023-01-24 |  | 5 | Check harness for open wiring | CMSTRBLSHOOT | 3071332 | Closed | Closed |  | 2023-07-10 |  |  | Defect Confirmed - Repair Complete | 167
Upstream | Resolved | 43 |  | Alarm | 1st Planetary Stage | 2022-05-29 |  | 3 |  | Monitor | [7 empty] | Case In Progress | -44710
Thunderhead | Resolved | 43 | 1st Stage Planetary Gearing Issue | Alarm | 1st Planetary Stage | 2024-04-16 |  | 1 | 4/26/24 - Repair pending 4/24/24 - Tower remaining down until pending replacement. 4/24/24 -Initial borescope seemed to miss major damages, secondary inspection revealed a massive crack/liberation on one tooth in the 1st stage planet gears, warranty claim updated. 4/16/24 - Recommend full gearbox borescope with focus on the 1st planetary stage at next possible opportunity. Turbine also to be derated to 50%. | Repair Pending | 3334166 | Closed | Closed | Q3 2024 |  |  |  | Defect Confirmed - Repair Complete | -45398
Plymouth | Resolved | 43 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-03-18 |  | 3 | 3/18/24 - CMS monitor is not receiving a speed signal from the generator encoder. Please inspect PEM and encoder using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3318155 | Closed | Closed |  | 2024-06-19 |  |  | Defect Confirmed - Repair Complete | 93
Bethel | Resolved | 44 |  | Alarm | Helical High Speed Stage | 2022-01-31 |  | 3 |  | Borescope HSS bearing | Create WO |  | #N/A |  | 2023-01-25 | 2/1 - FFT indicates damage to the outer race of the HSS DnWind Rear Bearing, Timeseries shows progressive increase in signal, borescope HSS bearings |  | Case In Progress | 359
Santa Rita East | Resolved | 44 |  | Warning | Generator Outboard | 2021-11-07 |  | 6 |  | Monitor | [7 empty] | Case In Progress | -44507
Santa Rita East | Active | 44 | ZF S2 Carrier Bearing Issue | Case Tracking | 2nd Planetary Stage | 2022-08-03 |  | 1 | Found damage in 1P1 and 1P3 BRG RS spalling. Gearbox needs replacement. Claim submitted. | Final Report Needed | 2971669 |  | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -44776
Sundance | Resolved | 44 | S1 Planetary Sensor Issue | Instrumentation | 1st Planetary Stage | 2023-02-06 |  | 5 | CMS sensor giving erratic readings directly after the yaw system was worked on. Please inspect the S1 Planetary sensor for proper torqueing. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3078542 | Closed | Closed |  | 2023-02-06 |  |  | Defect Confirmed - Repair Complete | 0
Upstream | Resolved | 44 | Generator Outboard IRBP | Warning | Generator Outboard | 2023-09-08 | 2024-04-25 | 3 | 3/11/24 - Component replaced, CMS data is updated. 9/8/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | Final Report Needed | 3187717 | Closed | Closed |  | 2024-03-11 |  |  | Defect Confirmed - Repair Complete | 185
Upstream | Resolved | 45 |  | Warning | Helical High Speed Stage | 2022-04-12 |  | 3 |  | Monitor | [7 empty] | Case In Progress | -44663
Santa Rita East | Resolved | 45 | IONet Issue | Instrumentation | CMS Monitor | 2023-04-07 |  | 5 | CMS monitor is missing it's power signal, please perform toolbox CBM download. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3116888 | Closed | Closed |  | 2023-04-18 |  |  | Defect Confirmed - Repair Complete | 11
Maverick | Active | 45 | Potential Main Bearing Issue | Warning | Main Bearing | 2023-10-19 | 2024-10-19 | 6 | 10/19/23 - Possible signature coming out of a long term outage, continue to monitor. | Monitor | [7 empty] | Case In Progress | -45218
Sundance | Active | 45 | Potential NTN Main Bearing Outer Race Issue | Sweep | Main Bearing | 2024-03-05 |  | 2 | 3/25/24 - Turbine DNR'd 3/12/24 - Customer requested derate to 35%. 3/7/24 - Customer requested derate to 80%. 3/5/24 - Recommend main bearing borescope within 2 weeks from 3/5/24. Recommend 50% derate as well. | Final Report Needed | 3313195 | Closed | Closed |  | 2024-03-24 |  |  | Defect Confirmed - Repair Complete | 19
Sundance | Active | 45 | Oil Particle Communication Issue | Particle Counter | Particle Counter | 2023-10-04 |  | 4 | 10/4/23 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3201756 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45203
Thunderhead | Active | 45 | Outer Race Banding | Sweep | Main Bearing | 2023-02-14 |  | 2 |  | Monitor | [5 empty] | 2/14 - 14.5x harmonics since COD, standstills? |  | Case In Progress | -44971
Bethel | Resolved | 46 | NDE gen bearing sensor issue | Instrumentation | Generator Outboard | 2023-01-25 |  | 2 | Replace sensor on NDE gen bearing | CMSTRBLSHOOT | 3072191 | Closed | Ready to Schedule |  | 2023-11-14 | 2/6 - increase priority in case vibration is real |  | Defect Confirmed - Repair Complete | 293
Upstream | Resolved | 46 |  | Warning | Helical High Speed Stage | 2021-08-28 |  | 3 |  | Monitor | [6 empty] | 11/3 - Peaks to warning setpoint, monitor, 11/30 - 0.56g peak at 2x GMF, minor sidebands, 1/11 - 2X peak = 0.86g, elevating to cat 2, 2/8 - 2X peak = 1.956, sidebands between 2X and 3X GMF, 4/15 - operation just below warning setpoint, 10g vibration floor in timebase, bearing fault harmonics between 2X and 3X GMF, 2X peak indicates misalignment, 8/19 - no progression, misalignment in S3 mesh, | Case In Progress | -44436
Upstream | Resolved | 46 |  | Warning | Generator Outboard | 2022-01-30 |  | 3 |  | Monitor | [7 empty] | Case In Progress | -44591
Upstream | Resolved | 46 |  | Alarm | Main Bearing | 2022-11-25 |  | 3 |  | Monitor | [8 empty] | -44890
Bethel | Resolved | 46 | DE Gen bearing elevated vibration | Alarm | Generator Inboard | 2023-04-07 |  | 2 | Add grease to both gen bearings | CMSGENB | 3110038 | Closed | Closed |  | 2023-10-04 |  |  | Defect Confirmed - Repair Complete | 180
Maverick | Active | 46 | Potential Timken Main Bearing Rolling Element Issue | Sweep | Main Bearing | 2024-04-05 |  | 2 | 6/25/24 - Turbine DNR'd. 5/28/24 - Borescope found initial roller cracking. 4/30/24 - Turbine derated to 50%. 4/5/24 - Recommend main bearing borescope + grease purge within 2 weeks from 4/5/24. | Final Report Needed | 3329426 | Closed | Closed |  | 2024-06-25 |  |  | Defect Confirmed - Repair Complete | 81
Deuel Harvest | Active | 46 | S3 Possible Pinion Tooth damage | Alarm | Helical High Speed Stage | 2024-01-16 |  | 2 | 1/16/2024 - CMS indicates possible damage to the Pinion tooth, inspection and derate reccommened. 2/29 - no shavings found, or damage on brearings or teeth and sensor tested fine. Likely was hydraulic brake issue, as signature is no longer there | CMSHSS | 3254962 | Closed | Closed |  |  |  |  | Case In Progress | -45307
Plymouth | Resolved | 46 | High Speed Stage Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2024-07-08 |  | 4 | 7/8/24 - Please investigate HSS sensor wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | 3380405 | Closed | Ready to Schedule |  | 2024-07-16 |  |  | Defect Confirmed - Repair Complete | 8
Plymouth | Active | 46 | 1st Planetary Stage Bearing/2nd Stage Planetary Gearing Failure | Alarm | 1st Planetary Stage | 2023-04-05 |  | 2 | Planetary Gearing failure, turbine is DNR'd until gearbox replacement. | Final Report Needed | 3109156 | Closed | Closed |  | 2023-07-26 |  |  | Defect Confirmed - Repair Complete | 112
Santa Rita East | Active | 46 | Main Bearing BS2X | Sweep | Main Bearing | 2023-09-07 |  | 1 | 1/3/24 - Denting and roller damage seen, asymmetrical cage wear seen, and outer race edge chipping. Est repair Q1 2024. 9/7/23 - CMS indicates damage of the main bearing roller bearings, recommend thrust derating and performing a borescope of the main bearing at the next possible opportunity. | Final Report Needed | 3187380 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45176
Bethel | Resolved | 47 | Lost Comms | Instrumentation | CMS Monitor | 2023-03-17 |  | 5 | Check 60M100 monitor power supply and reboot | CMSTRBLSHOOT | 3100208 | Closed | Closed |  | 2023-10-25 |  |  | Defect Confirmed - Repair Complete | 222
Upstream | Resolved | 47 |  | Warning | 1st Planetary Stage | 2021-12-29 |  | 2 |  | Monitor |  |  |  |  | 2022-02-08 | 1/11 - varied events for all three stages, 2/8 -large spike on 10/23-26 from failing gearbox, gearbox replaced, resolving and updating monitor configuration |  | True Positive | 41
Upstream | Resolved | 47 |  | Alarm | 2nd Planetary Stage | 2021-10-26 |  | 5 |  | Replace Gearbox | [5 empty] | Failed gearbox discovered due to a fault, CMS missed due to unplanned time off |  | False Negative | -44495
Upstream | Resolved | 47 |  | Warning | 1st Planetary Stage | 2022-02-24 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 |  | 5/25 - peak at 35.156X, otherwise low concern, 8/19 - increasing signal peak amplitude, S1 PC BRG GS rollers, 10/19 - minor progression in stage 1, | Case In Progress | 334
Santa Rita East | Resolved | 47 |  | Instrumentation | CMS Monitor | 2021-11-02 |  |  | Controller Issue |  | 2631667 |  | Closed |  |  | 2021-12-15 |  |  | -44502
Maverick | Resolved | 47 |  | Warning | 2nd Planetary Stage | 2021-11-28 |  | 5 |  | Monitor |  |  |  |  | 2022-11-16 | 1/11 - sidebands under 0.01g, 2/15 - GMF peaks at 4x, 5x, FFT shows some stage 2 planet fault sidebands and/or stage 3 pinion fault sidebands, monitor, 4/18 - likely stage 2 bearing damage, 6/23 - limited progression, 11/16 - no progression, resolving |  | False Positive - No Action | 353
Maverick | Active | 47 | NTN Main Bearing BS2X Signature | Sweep | Main Bearing | 2024-07-03 |  | 2 | 8/20/24 - DNR'd 7/3/24 - Recommend borescoping this main bearing within 2 weeks from 7/3/24 with focus on outer race and rollers. | Final Report Needed | 3379473 | Closed | Closed |  | 2024-08-20 |  |  | Defect Confirmed - Repair Complete | 48
Thunderhead | Resolved | 47 | IONet issue | Instrumentation | CMS Monitor | 2024-02-21 |  |  | 2/21/24 - Please perform toolbox download to CBM card. | CMSTRBLSHOOT | 3303650 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -45343
Sundance | Active | 47 | NTN Main Bearing Outer Race Signature | Sweep | Main Bearing | 2024-02-06 | 2024-07-03 | 6 | 4/22/24 - Minor damage progression, continue to monitor via CMS. 4/9/24 - Outer race progression. Recommend main bearing borescope + grease purge within 2 weeks from 4/9/24. 2/6/24 - ORBP signature, continue to monitor | Monitor | 3331468 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45328
Upstream | Resolved | 47 | Generator Outboard ORBP | Alarm | Generator Outboard | 2023-10-16 | 2024-04-15 | 4 | 2/10/24 - Component replaced, CMS data is updated. 10/16/23 - CMS shows increase in direct (7 g pk) and harmonics for generator outboard ORBP. 12/27/23 - direct peaked at 50. 12/29 - direct peaked at 53. | Final Report Needed | 3213200 | Closed | Closed |  | 2024-02-10 |  |  | Defect Confirmed - Repair Complete | 117
Deuel Harvest | Resolved | 48 |  | Instrumentation | Generator Inboard | 2022-06-08 |  |  | check for shorted sensor wiring | CMSTRBLSHOOT | 2943207 | Cancelled | Cancelled |  | 2022-08-26 |  |  |  | 79
Bethel | Resolved | 48 |  | Warning | 1st Planetary Stage | 2022-01-29 |  | 6 | [6 empty] | 2023-01-25 |  |  | Case In Progress | 361
Bethel | Resolved | 48 |  | Warning | Generator Outboard | 2022-01-31 |  | 5 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - NDE bearing signal has increased throughout the second half of 2021, 10g impacts in the timebase, 1g peaks throughout FFT fault frequencies |  | Case In Progress | 359
Bethel | Resolved | 48 | Gen Bearing Failure | Alarm | Generator Outboard | 2023-01-25 |  | 1 | Replace gen bearings | CMSGENB | 3072190 | Closed | Closed |  | 2023-02-25 | 2/16 - replacement underway |  | Defect Confirmed - Repair Complete | 31
Santa Rita East | Resolved | 48 |  | Case Tracking | Main Bearing | 2022-04-29 |  | 1 |  | DNR | 2965426 | Closed | Closed |  |  |  |  | True Positive | -44680
Santa Rita East | Resolved | 48 |  | Instrumentation | Main Bearing | 2022-08-09 |  |  | Open sensor wiring | CMTRBLSHOOT | 2987883 | Closed | Closed |  |  | 2022-08-10 |  |  | -44782
Santa Rita East | Resolved | 48 | 1st Planetary Stage Accelerometer Open Circuit | Instrumentation | 1st Planetary Stage | 2022-08-30 |  | 5 | 1st Planetary Stage sensor is currently reading an open circuit, please inspect wiring harness. | CMSTRBLSHOOT | 3073702 | Closed | Closed | [5 empty] | -44803
Maverick | Active | 48 | Main Bearing BS2X Issue | Sweep | Main Bearing | 2024-09-17 |  | 2 | 10/4/24 - Customer requested turbine be derated to 75%. 9/17/24 - Recommend borescoping this main bearing within 2 weeks from 9/17/24 with focus on outer race and rollers. | Repair Pending | 3428148 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45552
Plymouth | Resolved | 48 | CMS Monitor Netcom/Keyphasor Issue | Instrumentation | Other | 2024-08-05 |  | 3 | 8/5/24 - Not receiving data via Onyx Insight, please investigate if monitor is netcom or not receiving a speed signal. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3397303 | Closed | Closed |  | 2024-09-05 |  |  | Defect Confirmed - Repair Complete | 31
Santa Rita East | Resolved | 48 | 1st Planetary Stage Accelerometer | Instrumentation | 1st Planetary Stage | 2023-06-27 |  | 5 | 1st planetary stage sensor reading uneven bias voltage, recommend inspecting wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | 3148533 |  | Ready to Schedule |  |  |  |  | Case In Progress | -45104
Upstream | Resolved | 48 | ZF Flash S1 Planet Bearing Issue | Sweep | 1st Planetary Stage | 2023-06-22 | 2025-03-01 | 2 | Currently shutdown and DNR'd 11/13/24 - CMS shows defect progression, shutdown requested and completed. 7/29/24 - request re-borescope due to S2 defect signature progression. 6/27 - Borescope found minor damages on S1 planetary bearings continue to monitor via CMS. 6/22/23 - Work order created for S1 PSBG issue. | Longterm Watchlist | 3393106 | Closed | Closed | Q4 2024 |  |  |  | Defect Confirmed - Awaiting Repair | -45099
Deuel Harvest | Resolved | 49 | Gearbox 1 Sensor Issue | Instrumentation | 1st Planetary Stage | 2022-03-23 |  |  | check for open sensor wiring on gearbox 1 sensor | CMSTRBLSHOOT | 2889954 |  | Closed | [5 empty] | -44643
Deuel Harvest | Resolved | 49 |  | GE Alert | 1st Planetary Stage | 2021-12-20 |  | 3 |  | Inspect per GE Request | [5 empty] | 2022-03-18 |  | True Positive | -44550
Upstream | Resolved | 49 |  | Alarm | Helical High Speed Stage | 2022-08-26 |  | 1 |  | Monitor | 3012690 | Closed | Closed |  | 2022-09-29 | 9/7 - Peaks in the S3 pinion fault signal, modulation in the timebase, and pinion fault sidebands indicate recently progressed damage to the HSS pinion. The envelope spectrum also indicates roller and raceway damage to HSS GS bearing, recommending HSS check, 9/29 - no damage in borescope, 1 brake pad was installed upside down, likely cause of vibration, resolve |  | True Positive | 34
Upstream | Resolved | 49 |  | Warning | Generator Outboard | 2022-07-26 |  | 3 |  | Monitor | [7 empty] | Case In Progress | -44768
Santa Rita East | Resolved | 49 |  | Change 1 | Helical High Speed Stage | 2022-04-11 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44662
Sundance | Active | 49 | 1st Stage Planetary Bearing Issue | Sweep | 1st Planetary Stage | 2024-10-02 |  | 3 | 10/2/24 - Recommend full gearbox borescope with focus on the 1st planetary stage within 3 months from 10/2/24. | CMSGBXBORE | 3440869 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45567
Sundance | Active | 49 | Main Bearing Issue | Case Tracking | Main Bearing | 2023-09-21 |  | 1 | 9/29/23 - Severe Outer Race edge chipping at 6 o'clock position, Cat 3 OR spalling, Roller DLC delamination. Turbine DNR'd until repair. | Final Report Needed | [7 empty] | Miss - Defect Not Caught | -45190
Upstream | Active | 49 | Generator Outboard OBRP issue | Alarm | Generator Outboard | 2024-07-18 |  | 3 | 7/18/24 - CMS indicates generator outboard ORBP issue. Request for inspection. | CMSGENB | 3388801 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45491
Upstream | Active | 49 | Instrumentation Issue Generator Inboard sensor | Alarm | CMS Monitor | 2024-11-13 |  | 5 | CMS indicates sensor issue in gearbox sensor 1 | Monitor |  |  | Ready to Schedule |  |  |  |  | Case In Progress
Upstream | Active | 49 | HSS Rotational | Warning | Helical High Speed Stage | 2023-07-11 |  | 4 | Please perform generator alignment and check HSS coupler for any signs of damage. Also check high speed stage vibration sensor mounting and circuit for looseness and open/shorted wiring. Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | CMSHSS | 3155269 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45118
Bethel | Resolved | 50 |  | Warning | Helical High Speed Stage | 2022-01-31 | [8 empty] | 2023-01-25 | 2/1 - repair pending |  | Case In Progress | 359
Deuel Harvest | Resolved | 50 |  | Alarm | Generator Inboard | 2021-08-18 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44426
Upstream | Resolved | 50 |  | Warning | Helical High Speed Stage | 2022-01-18 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 |  | 5/5 - no progression, 2X/3X harmonics indicate damage to HSS bearings, 9/7 - misalignment, | Case In Progress | 371
Santa Rita East | Resolved | 50 | Intemediate Stage Accelerometer | Instrumentation | 2nd Planetary Stage | 2023-05-22 |  | 5 | Intermediate stage sensor is reading a short circuit, please inspect sensor wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | 3130586 | Closed | Closed |  | 2023-06-09 |  |  | Defect Confirmed - Repair Complete | 18
Santa Rita East | Resolved | 50 | 1st Planetary Stage Accelerometer | Instrumentation | 1st Planetary Stage | 2023-09-29 |  | 5 | 9/29/23 - 1st Stage Accelerometer is currently reading a short circuit. Please inspect wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | 3198514 | Closed | Ready to Schedule |  | 2023-12-09 |  |  | Defect Confirmed - Repair Complete | 71
Maverick | Active | 50 | 1st Planetary Stage Planet Bearing/gearing Issue | Particle Counter | 1st Planetary Stage | 2024-07-31 |  | 3 | 8/29/24 - Turbine experienced gearing failure, turbine idling. 7/31/24 - Recommend full gearbox borescope with focus on the 1st planetary stage within 3 months from 7/31/24. | Final Report Needed | 3395484 | Closed | Closed |  | 2024-08-29 |  |  | Defect Confirmed - Repair Complete | 29
Bethel | Active | 51 | Gen Outboard Bearing Damage | Warning | Generator Outboard | 2023-01-26 |  | 3 | Add grease to both gen bearings | Monitor | 3072469 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -44952
Bethel | Resolved | 51 |  | Warning | Generator Outboard | 2021-04-05 |  | 5 | [6 empty] | 2023-01-25 | 2/1 - 10g impacts in timebase, 1g peak at ORBP 0.75g peak at IRBP, signal appears to be trending up, monitor closely for failure |  | Case In Progress | 660
Deuel Harvest | Resolved | 51 |  | Instrumentation | CMS Monitor | 2022-02-02 |  |  | Wait | [5 empty] | 2022-04-05 |  | Failed Generator, 2/23 - not running |  | 62
Upstream | Resolved | 51 |  | Change 1 | 1st Planetary Stage | 2022-04-25 |  | 3 |  | Monitor | [7 empty] | Case In Progress | -44676
Upstream | Resolved | 51 |  | Warning | Generator Outboard | 2021-12-31 |  | 3 |  | Monitor | [7 empty] | Case In Progress | -44561
Maverick | Resolved | 51 | Main Bearing IRBP | Sweep | Main Bearing | 2023-09-25 | 2023-12-10 | 6 | 9/25/23 - Intermittent IRBP signature, continuing to monitor. | Monitor | [7 empty] | Case In Progress | -45194
Upstream | Active | 51 | Generator outboard | Alarm | Generator Outboard | 2024-07-25 |  | 3 | 7/25/24 - CMS shows potential generator outboard obrp/irbp issue. Continue to monitor via CMS | Monitor |  |  | Ready to Schedule |  |  |  |  | Case In Progress | -45498
Upstream | Active | 51 | Monitor Main Bearing Parking Marks | Sweep | Main Bearing | 2024-03-26 | 2025-03-07 | 5 | 3/26/24 - CMS shows parking marks, continue to monitor via CMS for progression | Monitor | [7 empty] | Case In Progress | -45377
Bethel | Resolved | 52 | Keyphasor Sensor Issue | Instrumentation | Keyphasor | 2023-04-07 |  | 5 | Check both NDE gen bearing sensor and keyphasor loops for open | CMSTRBLSHOOT | 3110040 | Closed | Closed |  | 2023-10-06 |  |  | Defect Confirmed - Repair Complete | 182
Bethel | Resolved | 52 |  | Alarm | Helical High Speed Stage | 2022-01-29 |  |  |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - stage 3 shows signs of damage to the pinion, FFT shows pinion fault sidebands at 2X GMF, direct signal is trending towards alarm setpoint, monitor |  | Case In Progress | 361
Deuel Harvest | Resolved | 52 |  | Warning | 2nd Planetary Stage | 2021-11-10 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44510
Bethel | Active | 52 | Generator Inboard ORBP/IRBP | Alarm | Generator Inboard | 2024-05-14 | 2024-07-02 | 5 | 5/14/24 - CMS indicates potential GENB IRBP/ORBP issue. However signature shows up 6 months ago so may be a false positive. Continue to monitor for progression. Possibly recommend for grease change | Monitor | [7 empty] | Case In Progress | -45426
Thunderhead | Active | 52 | S1 Planetary IRBP Issue | Sweep | 1st Planetary Stage | 2024-05-28 |  | 4 | 5/28/24 - CMS shows early S1 bearing signature, continue to monitor for changes. | Monitor | [7 empty] | Case In Progress | -45440
Sundance | Resolved | 52 |  | Instrumentation | 1st Planetary Stage | 2022-06-01 |  |  | Check Gearbox 1 sensor mounting and wiring, next climb | CMSTRBLSHOOT | 2940497 | Closed | Closed |  | 2022-08-26 |  |  |  | 86
Sundance | Active | 52 | Oil Particle Communication Issue | Particle Counter | Particle Counter | 2023-10-04 |  | 4 | 10/4/23 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3201728 | Ready to Schedule | Ready to Schedule | [5 empty] | -45203
Sundance | Resolved | 52 | Main Bearing Accelerometer Open Circuit | Instrumentation | Main Bearing | 2023-11-20 |  | 4 | 11/20/23 - Main bearing accelerometer is currently reading an open circuit since main bearing replacement. Please inspect wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | 3227474 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -45250
Sundance | Active | 52 | Main Bearing Vibration | GE Alert | Main Bearing | 2023-04-07 |  | 1 | CMS is indicating progressing MB damage, recommend shutting turbine down until inspection can be made. DNR | Final Report Needed | 3116897 | Closed | Closed |  | 2024-08-07 |  |  | Defect Confirmed - Awaiting Repair | 488
Bethel | Active | 53 | Generator Outboard Bearing Issue | Alarm | Generator Outboard | 2023-02-23 | 2024-08-22 | 3 | Add grease to both gen bearings | Monitor | 3086601 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -44980
Bethel | Resolved | 53 |  | Warning | Helical High Speed Stage | 2022-01-31 |  | 6 | [7 empty] | 2023-01-25 |  | Case In Progress | -44592
Bethel | Resolved | 53 |  | Warning | Generator Outboard | 2022-01-31 |  | 5 |  | Monitor | [5 empty] | 2023-01-25 |  | Case In Progress | -44592
Deuel Harvest | Resolved | 53 |  | Warning | 2nd Planetary Stage | 2021-12-22 |  | 5 |  | Monitor | [6 empty] | 12/27 - Ring fault sidebands are present at 3X GMF, 0.02g, 2/2 - ring fault sidebands persist, continue to monitor, 6/10 - no progression, 6/28 - potential S2 bearing damage, carrier and planets, 9/2 - elevated IMS harmonics, potential HSS bearing fault, 11/23 - | Case In Progress | -44552
Upstream | Resolved | 53 |  | Warning | Helical High Speed Stage | 2021-10-13 |  | 1 |  | Monitor |  |  |  |  | 2022-11-29 | low concern, high wind 10/13, 3/4 - additional alarm on 2/16, 9/7 - S3 mesh misalignment, potential HSS bearing damage |  | False Positive - No Inspection | 412
Bethel | Active | 53 | Potential HSS DnWind Bearing IRBP | Warning | Helical High Speed Stage | 2024-04-01 | 2024-07-14 | 2 | 4/24/24 - HSS Upwind bearings found spalled, recommend HSS replacement. 4/1/24 - Recommend full gearbox borescope with focus on HSS bearings within 1 month from 4/1/24. | Longterm Watchlist | 3326983 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45383
Thunderhead | Active | 53 | Potential Generator Inboard ORBP/IRBP | Alarm | Generator Inboard | 2025-01-22 |  | 3 | 1/22/24 - CMS indicates potential damage to the DE generator inboard bearing's outer race. | CMSGENB | 3498331 |  | Ready to Schedule |  |  |  |  | Case In Progress
Bethel | Resolved | 54 |  | Instrumentation | CMS Monitor | 2022-01-31 |  |  | Replace Monitor |  | 2740307 |  | Cancelled |  |  | 2023-01-25 |  |  | -44592
Bethel | Resolved | 54 | Gen Bearing Failure | Case Tracking | Generator Outboard | 2023-01-25 |  | 1 | Replace gen bearings | CMSGENB | 3072192 | Closed | Closed |  | 2023-02-25 |  |  | Defect Confirmed - Repair Complete | 31
Santa Rita East | Resolved | 54 |  | Warning | 2nd Planetary Stage | 2022-03-07 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44627
Deuel Harvest | Active | 54 | S1 Planetary IRBP Issue | Sweep | 1st Planetary Stage | 2024-04-24 |  | 2 | 4/24/24 - CMS indicates stage 1 Planetary IRBP issue. Please perform full gearbox borescope inspection and upload the report to HUVR. | Longterm Watchlist | 3337076 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45406
Bethel | Resolved | 55 | Generator Outboard ORBP | Warning | Generator Outboard | 2023-09-25 |  | 3 | 2/28/24 - Replace generator outboard bearing. 9/25/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings | Repair Pending | 3196484 | Closed | Closed |  | 2024-09-23 |  |  | Defect Confirmed - Repair Complete | 364
Upstream | Resolved | 55 | HSS Pinion Tooth Damage | Warning | Helical High Speed Stage | 2021-11-17 |  | 1 | Fractured Pinion Tooth, HSS replacement pending | Monitor for Failure | 2938151 | Closed | Closed |  | 2023-02-20 | 3/13 - HSS replacement complete, latch reset, resolved |  | True Positive | 460
Maverick | Resolved | 55 | Generator Inboard Sensor Issue | Instrumentation | Generator Inboard | 2022-05-09 |  | 4 | DE Generator sensor is reading an open circuit. Please inspect wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | 2929289 | Closed | Closed |  | 2024-05-09 |  |  | Defect Confirmed - Repair Complete | 731
Maverick | Active | 56 | NTN Main Bearing BS2X Signature | Sweep | Main Bearing | 2024-09-30 |  | 2 | 10/8/24 - Turbine derated to 50%. 9/30/24 - Please borescope with focus on MB roller elements within 2 weeks from 9/30/24. | Repair Pending | 3439218 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45565
Santa Rita East | Active | 56 | Main Bearing BS2X | Sweep | Main Bearing | 2023-06-07 |  | 1 | 7/31/23 - CMS signatures have increased in amplitude, turbine to be DNR'd until replacement can be made. | Final Report Needed | 3139730 | Closed | Closed |  | 2023-10-21 |  |  | Defect Confirmed - Repair Complete | 136
Bethel | Resolved | 57 | Gen Outboard Bearing Damage | Warning | Generator Outboard | 2023-01-26 | 2024-05-21 | 2 | 2/22/24 - Replace generator outboard bearing | Repair Pending | 3072470 | Closed | Closed |  | 2024-06-03 |  |  | Defect Confirmed - Repair Complete | 494
Santa Rita East | Resolved | 57 |  | Change 1 | 2nd Planetary Stage | 2022-05-09 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44690
Maverick | Resolved | 57 |  | Instrumentation | Helical High Speed Stage | 2022-05-09 |  |  | CMS Gearbox 1 and Gearbox 3 channel not ok, likely shorted wiring | CMSTRBLSHOOT | 2929290 | Closed | Closed |  |  | 2022-12-16 |  |  | -44690
Maverick | Resolved | 57 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-11-21 |  | 3 | 11/21/2023 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3227909 | Closed | Ready to Schedule |  | 2024-10-18 |  |  | Defect Confirmed - Repair Complete | 332
Thunderhead | Resolved | 57 | Pinion Tooth Damage | Warning | Helical High Speed Stage | 2023-01-20 |  | 4 | Check pinion for mesh damage | Monitor | 3084526 | Closed | Closed |  |  | 1/24 - pinion sidebands |  | False Positive | -44946
Bethel | Active | 58 | HSS Bearing Damage | Case Tracking | Helical High Speed Stage | 2023-02-06 |  | 4 | Check HSS bearing for damage | Monitor | 3080388 | Closed | Closed |  |  |  |  | Case In Progress | -44963
Bethel | Active | 58 | 1st Planetary Stage gearing Issue | Warning | 1st Planetary Stage | 2024-10-14 |  | 1 | 10/14/24 - Recommend full gearbox borescope within 24-72 hours from 10/14/24 with focus on the 1st planetary stage. Also recommend derating turbine to 50% until inspection can be performed. | Final Report Needed | 3445942 | Closed | Ready to Schedule |  | 2024-11-28 |  |  | Defect Confirmed - Repair Complete | 45
Bethel | Active | 58 | Generator Outboard IRBP | Alarm | Generator Outboard | 2024-04-25 |  | 6 | 4/25/24 - Awaiting direct increase. | Monitor |  |  |  |  | 2024-08-10 |  |  | Case In Progress | 107
Bethel | Resolved | 59 |  | Instrumentation | CMS Monitor | 2022-01-31 |  |  |  |  | 2740315 |  | Cancelled |  |  | 2023-01-25 |  |  | -44592
Deuel Harvest | Resolved | 59 |  | EOW | 1st Planetary Stage | 2022-08-23 |  | 1 |  | EOW Claim | [5 empty] | 9/21 - S1 PS BRG indent and end scoring |  | False Negative | -44796
Santa Rita East | Resolved | 59 |  | Change 1 | 2nd Planetary Stage | 2022-04-23 |  | 1 |  | Monitor | [7 empty] | Case In Progress | -44674
Deuel Harvest | Active | 59 | Potential S1 Planetary IRBP Issue | Sweep | 1st Planetary Stage | 2024-03-21 | 2025-04-03 | 2 | 8/06/24 - defect signature is showing slight progression continue to monitor. 4/04/24 - borescope found no notable defects, continue to monitor via CMS. 3/21/24 - CMS indicates damage to S1 IRBP, please perform full gearbox borescope | Longterm Watchlist | 3320356 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45372
Upstream | Resolved | 59 | HSS Pinion Issue | Alarm | Helical High Speed Stage | 2024-01-02 | 2024-08-03 | 1 | 3/6/24 - Borescope found chipped tooth, turbine currently under a 50% derate. 3/6/24 - CMS is showing a progression in the pinion signature post 50 range. CMS indicates that this is a HSS pinion issue, sent out for borescope and inspection. 2/14 - Turbine pinion signature is now showing after 1st fault peak | Final Report Needed | 3248543 | Closed | Closed | Q2-3 2024 |  |  |  | Defect Confirmed - Repair Complete | -45293
Thunderhead | Active | 59 | Potential Early stage S1 IRBP | Sweep | 1st Planetary Stage | 2024-01-02 | 2025-03-07 | 5 | 1/3/24 - Noise floor is exhibiting harmonics for early stage IRBP issue, but signature hasn't been there long can also be a flase positive | Monitor | [7 empty] | Case In Progress | -45293
Plymouth | Resolved | 59 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-11 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988837 | Cancelled | Cancelled | [5 empty] | -44784
Plymouth | Resolved | 59 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-12-11 |  | 3 | 12/11/23 - CMS monitor is not receiving a speed signal from the generator encoder. Please inspect PEM and encoder using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3240301 | Closed | Closed |  | 2023-12-22 |  |  | Defect Confirmed - Repair Complete | 11
Plymouth | Resolved | 59 | CMS Monitor Netcom/Keyphasor Issue | Instrumentation | Other | 2024-08-05 |  | 3 | 8/5/24 - Not receiving data via Onyx Insight, please investigate if monitor is netcom or not receiving a speed signal. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3397304 | Closed | Ready to Schedule |  | 2024-08-11 |  |  | Defect Confirmed - Repair Complete | 6
Santa Rita East | Active | 59 | Main Bearing Issue | Case Tracking | Main Bearing | 2023-05-09 | 2024-12-05 |  |  | Monitor | [5 empty] | Potential inner/outer race damage. Old 2021 borescope showed early spalling |  | Case In Progress | -45055
Sundance | Resolved | 59 | Main Bearing Accelerometer | Instrumentation | Main Bearing | 2023-08-15 |  | 5 | Main Bearing sensor is currently showing an open circuit. Please inspect wirings and connections, replace sensor if needed. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3174102 | Closed | Closed |  | 2024-08-07 |  |  | Defect Confirmed - Repair Complete | 358
Santa Rita East | Resolved | 60 |  | Warning | 1st Planetary Stage | 2021-09-22 |  | 6 |  | Monitor | 2931232 | Closed | Closed |  |  |  | Frequency peaks at Ring and Sun Fault Frequencies, 12/28 - vibrations have decreased from summer levels, watch for increase next summer, 1/13 - likely stage 1 bearing issue, 1/31 - continue to monitor, 4/25 - stage 1 direct shows rapid progression in April, likely damage to stage 1 carrier GS, elevating to cat 3, 5/13 - progression in the direct signal to the alarm setpoint, concerning increase, recommending derate and borescope, | False Positive - Sensor Issue | -44461
Bethel | Resolved | 60 | Gen Outboard Bearing Damage | Warning | Generator Outboard | 2024-01-26 |  | 3 | 5/6/24 - Created new WO to inspect bearing. 1/26/23 - NDE grease appeared burnt from the inspection pictures, placing on long term watchlist | Longterm Watchlist | 3346756 | Closed | Ready to Schedule |  | 2024-07-29 |  |  | Defect Confirmed - Repair Complete | 185
Plymouth | Active | 60 | HSS Pinion Issue | Warning | Helical High Speed Stage | 2023-08-21 |  | 2 | 10/3/23 - Inspections did not find anything, continuing to monitor for changes. 8/21/23 - Recommend full gearbox borescope with focus on 2nd planetary stage. | Monitor | 3176757 | Closed | Closed |  |  |  |  | False Positive | -45159
Bethel | Resolved | 61 |  | Instrumentation | Helical High Speed Stage | 2022-01-31 |  |  | Check sensor wiring and circuit |  | 2740319 |  | Closed |  |  | 2023-01-25 |  |  | -44592
Bethel | Resolved | 61 | Gearbox 3 sensor issue | Instrumentation | Helical High Speed Stage | 2023-01-25 |  | 5 | Check harness for opens | CMSTRBLSHOOT | 3072196 | Closed | Ready to Schedule |  | 2023-11-29 |  |  | Defect Confirmed - Repair Complete | 308
Bethel | Resolved | 61 | Gen Bearing Damage | Alarm | Generator Outboard | 2023-01-26 | 2023-04-25 | 2 | Add grease to both gen bearings | CMSGENB | 3072473 | Closed | Closed |  | 2023-04-17 |  |  | Defect Confirmed - Repair Complete | 81
Upstream | Resolved | 61 |  | Warning | Helical High Speed Stage | 2021-06-18 |  | 6 |  | Monitor | 2575728 | Cancelled | Cancelled |  | 2023-01-24 | 4/15 - stage 3 direct remains at warning setpoint, FFT shows bearing fault peaks, 5/25 - likely misalignment, HSS bearing fault harmonics, 8/19 - reduce to cat 1, |  | Case In Progress | 585
Santa Rita East | Resolved | 61 |  | Instrumentation | CMS Monitor | 2022-10-10 |  |  |  | CMSTRBLSHOOT | Wait |  |  |  |  | Wait for repair to be complete. |  |  | -44844
Santa Rita East | Resolved | 61 |  | Instrumentation | CMS Monitor | 2021-09-08 |  |  | Wait - turbine is offline for repair, replacement CMS montior needed | CMSTRBLSHOOT | 2919881 | Cancelled | Cancelled |  |  | 2022-09-26 |  |  | -44447
Santa Rita East | Resolved | 61 |  | Instrumentation | CMS Monitor | 2021-08-09 |  |  | Turbine offline for Main Bearing replacement | CMSTRBLESHOOT | 2476079 |  | Cancelled | [5 empty] | -44417
Santa Rita East | Resolved | 61 | CMS Sensor Issue | Instrumentation | Main Bearing | 2023-04-11 |  | 2 | All CMS sensors are currently reading open circuits after major component replacement. Please ensure CMS accelerometers are properly connected and installed on the gearbox.​ | CMSTRBLSHOOT | 3111643 | Closed | Closed |  | 2023-04-25 |  |  | Defect Confirmed - Repair Complete | 14
Sundance | Active | 61 | NTN Main Bearing Outer Race Signature | Sweep | Main Bearing | 2024-02-06 |  | 2 | 4/8/24 - Turbine placed on DNR list. 2/21/24 - Turbine has been derated to 40%. 2/20/24 - Recommend main bearing borescope at next opportunity, please upload results to HUVR. 2/6/24 - ORBP signature, continue to monitor | Final Report Needed | 3302721 | Closed | Closed |  | 2024-04-08 |  |  | Defect Confirmed - Repair Complete | 62
Sundance | Active | 61 | 1st Planetary Stage Accelerometer | Instrumentation | 1st Planetary Stage | 2024-09-12 |  | 5 | 9/12/24 -1st planetary stage sensor reading an open circuit, please investigate wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3426670 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress
Upstream | Resolved | 61 | Generator Outboard IRBP | Warning | Generator Outboard | 2022-01-01 | 2024-04-12 | 3 | 09/27/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | CMSGENB | 3197695 | Closed | Closed |  | 2024-03-19 | 10/1 - DE gen bearing shows some damage to ORBP, 2/8 - cancelling WO, not needed right now, 1/11 - NDE gen bearing vibrations are increasing, inconsistent impacts in timebase, ~ 10g max, peaks at ORBP in FFT, 6/17 - direct signal remains below warning setpoint, 8/19 - 5g impacts, 0.5g ORBP peak, 12/19 - IRBP warning, add grease | flagged again 10/17, direct is increasing | Defect Confirmed - Repair Complete | 808
Bethel | Active | 62 | Main Bearing sensor issue | Instrumentation | Main Bearing | 2023-01-25 |  | 5 | 1/16/24 - Sensor continues to show uneven bias voltage, ensure sensor is properly mounted and/or replace sensor. | CMSTRBLSHOOT | 3072464 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -44951
Maverick | Active | 62 | Potential Main Bearing Issue | Sweep | Main Bearing | 2024-04-05 |  | 2 | 5/28/24 - Borescope found DLC delamination, IR spalls, indents. Recommend 50% derate. 4/5/24 - Recommend main bearing borescope + grease purge within 2 weeks from 4/5/24. | Final Report Needed | 3329429 | Closed | Closed |  | 2024-08-05 |  |  | Defect Confirmed - Repair Complete | 122
Bethel | Resolved | 62 | Generator Outboard ORBP | Warning | Generator Outboard | 2024-09-16 |  | 3 | 9/16/24 - Replace generator bearing. | Final Report Needed | [7 empty] | Defect Confirmed - Repair Complete | -45551
Upstream | Resolved | 63 |  | Warning | Helical High Speed Stage | 2021-05-22 |  | 3 |  | Monitor | [6 empty] | 5/5 - Likely damage to HSS GS Rear bearing inner race, evidenced by clear harmonics and sidebands for inner race fault frequency. Monitor for progression, 5/25 - increase to above warning setpoint in May, continue to monitor, 6/17 - HSS bearing fault harmonics at high frequencies near elevated 2X GMF, indicates misalignment, | Case In Progress | -44338
Santa Rita East | Resolved | 63 |  | Warning | Helical High Speed Stage | 2022-12-07 |  | 6 |  | Monitor | [8 empty] | -44902
Santa Rita East | Resolved | 63 | Main Bearing BS2X | GE Alert | Main Bearing | 2022-12-05 |  | 1 |  | Final Report Needed | 3053733 | Closed | Closed |  | 2023-01-24 | 12/5 - GE alert for main bearing damage, recommending power derate and borescope |  | Defect Confirmed - Repair Complete | 50
Maverick | Active | 63 | NTN Main Bearing BS2X Signature | Sweep | Main Bearing | 2024-03-26 |  | 2 | 4/29/24 - Turbine derated to 40%. 3/26/24 - Recommend main bearing borescope and 50% power derate at next opportunity. | Final Report Needed | 3323495 | Closed | Closed |  | 2024-04-30 |  |  | Defect Confirmed - Repair Complete | 35
Bethel | Resolved | 63 | Generator NDE Bearing Issue | Warning | Generator Outboard | 2023-07-17 |  | 3 | Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. | Monitor | 3157123 | Closed | Closed |  | 2024-01-18 |  |  | Defect Confirmed - Repair Complete | 185
Plymouth | Resolved | 63 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2024-04-24 |  | 3 | 4/24/24 - CMS monitor is netcom, please ensure monitor is powered and network cable is plugged into Port A. Contact CMSEngineers_OSW@invenergyllc.com for support. | CMSTRBLSHOOT | 3337184 | Closed | Closed |  | 2024-05-10 |  |  | Defect Confirmed - Repair Complete | 16
Bethel | Resolved | 64 | Generator Outboard IRBP | Warning | Generator Outboard | 2023-10-05 |  | 2 | 4/24/24 - Monitor for progression. 1/16/24 - Continue to monitor for progression. 10/5/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings | Monitor | 3202381 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -45204
Bethel | Active | 64 | 1st Planetary Gearing Damage | Alarm | 1st Planetary Stage | 2023-12-05 |  | 1 | 12/11/23 - Borescope found planetary gearing fractures, continued operation is not recommended. Recommend turbine remain down until gearbox replacement has been completed. 12/5/23 - Recommend full gearbox borescope with focus on 1st planetary stage gearing, Please shut down this unit until inspection can be completed. | Final Report Needed | 3234984 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45265
Bethel | Resolved | 64 |  | Warning | Helical High Speed Stage | 2022-02-01 |  | 5 |  | Monitor | [5 empty] | 2023-01-25 |  | Case In Progress | -44593
Bethel | Resolved | 64 |  | Warning | Generator Outboard | 2022-01-31 |  | 5 |  | Monitor | [5 empty] | 2023-01-25 |  | Case In Progress | -44592
Upstream | Resolved | 64 |  | Change 1 | 1st Planetary Stage | 2022-05-24 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 | 5/25 - stage 1 FFT has a peak at 47.563 with harmonics, 6/17 - Change alert for stage 2, envelope indicates bearing damage, monitor for progression, 8/19 - 10g average timebase floor, S2 PC BRG GS roller faults present, 11/29 - limited progression, 12/20 - potential S2 PC BRG GS IRBP fault harmonics present |  | Case In Progress | 245
Upstream | Resolved | 64 |  | Warning | Main Bearing | 2022-10-03 |  | 3 |  | Monitor | [6 empty] | 10/19 - main bearing progression trending to alarm threshold, no claim at EOW, 11/29 - reduced signal, temps are ok |  | -44837
Santa Rita East | Resolved | 64 | 1st Planetary Stage Accelerometer Issue | Warning | 1st Planetary Stage | 2021-11-07 | 2023-02-23 | 5 | 1st Planetary Stage Accelerometer is giving erroneous readings​, please inspect wiring and ensure sensor is properly torques. Reach out to abarndt@invenergy.com if you have any questions. | GBXPARTTS | 3073720 | Closed | Closed |  |  | 11/15 - Direct vibrations have been increasing since September. Frequency spectrum shows mild peaks at shaft harmonics. Recommended Borescope inspection 12/14 - WO 2645291 didn't find any damage aside from mild banding , 9/19 - less than 1mg debris detected. Signal remains elevated, no damage indicators in envelope or high resolution, high amplitude vibration in both S1 and S2. Early pinion fault ins S3, 11/4 - increasing trends in S2 and S1 but no debris detected. Particle counter troubleshoot recommended, 12/14 - reduce to cat 1 | 12/28 - low concern, monitor, 1/31 - spikes above warning setpoint continue, 4/25 - monitor for additional peaks past alarm setpoint, 5/13 - increasing amplitude of peaks in the trend, 6/30 - alarm level vibration in stages 1 and 2, plan to borescope if progression continues, 7/22 - vibration reduced to just below alarm setpoint since June, continue to monitor for progression, particle counter doesn't show significant debris generation or high temps in tads, continue to monitor, 8/8 - still no debris generation, vibration is peaking above the alarm setpoint, plan to inspect if elevated vibration is sustained | Case In Progress | -44507
Santa Rita East | Resolved | 64 | S1 Planetary Accelerometer Issue | Instrumentation | 1st Planetary Stage | 2023-03-15 |  | 4 | S1 Planetary Accelerometer giving erroneous reading, please inspect sensor for loose connection. | CMSTRBLSHOOT | 3098846 | Closed | Closed |  | 2023-04-15 |  |  | Defect Confirmed - Repair Complete | 31
Santa Rita East | Resolved | 64 | ​1st + 2nd Planetary Stage Accelerometer | Instrumentation | 1st Planetary Stage | 2023-10-04 |  | 5 | 10/4/23 - ​1st + 2nd planetary stage sensors are giving erroneous readings, please ensure sensors are properly torqued down. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3201710 | Closed | Closed |  |  |  |  | Case In Progress | -45203
Maverick | Resolved | 64 |  | Instrumentation | CMS Monitor | 2022-02-15 |  |  | Software Download? | CMSTRBLSHOOT | 2802866 |  | Cancelled |  | 2022-02-24 | Controller Power and Speed are not valid, likely requires software download, Rowdy rebooted monitor 2/23, likely software issue, email Andrew Barndt if persists |  |  | 9
Maverick | Resolved | 64 |  | Keyphasor Issue | Keyphasor | 2022-03-28 |  |  | Use Keyphasor troubleshoot guide + Replace 60M100 CMS Monitor | CMSTRBLSHOOT | 2892347 |  | Cancelled |  | 2022-08-23 | 4/12 - incoming download from GE |  |  | 148
Deuel Harvest | Active | 64 | Main Bearing Inner Race and Rolling Elements | Sweep | Main Bearing | 2024-03-26 |  | 2 | 3/19/24 - T64 was inspected due to high temps in the MB. DLC delamination on rollers, indentations on the inner race, and metallic grease. Due to the roller spall turbine derated by 50% to slow damage progression. Estimated failure of Q3-Q4, '24. | Longterm Watchlist | [7 empty] | Defect Confirmed - Awaiting Repair | -45377
Santa Rita East | Resolved | 64 | 1st Planetary Stage Accelerometer | Instrumentation | 1st Planetary Stage | 2024-10-07 |  | 4 | 10/7/24 - Possible 1st planetary stage sensor issue, please investigate wiring and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3443194 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45572
Plymouth | Resolved | 64 | Netcom Monitor | Instrumentation | CMS Monitor | 2022-06-03 |  | 3 | Replace 60M100 monitor | CMSTRBLSHOOT | 2924753 | Closed | CLosed |  | 2023-08-31 |  |  | True Positive | 454
Bethel | Resolved | 65 |  | Alarm | Generator Outboard | 2022-01-31 |  | 3 |  | GENBCHECK | Create WO |  | #N/A |  |  | 2023-01-25 |  | Case In Progress | -44592
Bethel | Resolved | 65 | Gen Bearing Damage | Case Tracking | Generator Outboard | 2023-01-25 |  | 1 | Replace gen bearings | CMSGENB | 3072198 | Closed | Closed |  | 2023-02-28 |  |  | Defect Confirmed - Repair Complete | 34
Upstream | Resolved | 65 |  | Warning | Helical High Speed Stage | 2022-01-18 |  | 1 |  | Monitor |  |  |  |  | 2022-11-29 | 2/8 - consistent peaks to warning setpoint, 0.2g sidebands between 2X and 3X GMF in stage 3 signal, 5/25 - no progression, 10/19 - reduce to cat 1, 11/29 - resolving |  | False Positive - No Inspection | 315
Santa Rita East | Resolved | 65 |  | Change 1 | Helical High Speed Stage | 2022-04-20 |  | 6 |  | Monitor | [7 empty] | Case In Progress | -44671
Santa Rita East | Resolved | 65 |  | Instrumentation | 1st Planetary Stage | 2021-10-15 |  |  | Replace Sensor | CMSTRBLESHOOT | 2616796 |  | Closed |  |  | 2022-02-22 |  |  | -44484
Sundance | Active | 65 | NTN Main Bearing Roller Element Issue | Sweep | Main Bearing | 2024-10-02 |  | 2 | 10/2/2024 - Recommend borescoping this main bearing within 2 weeks from 10/2/24 with focus on outer race and rollers. | CMSMBBORE | 3440872 | In Progress | Ready to Schedule |  |  |  |  | Case In Progress | -45567
Santa Rita East | Active | 65 | Main Bearing BS2X | GE Alert | Main Bearing | 2022-07-22 |  | 1 | thrust derate | Final Report Needed | [5 empty] | 7/22 - GE Alert, BEER signal, inspect within 2 weeks, 10/11 - progression continues, 2g impacts in the timebase, temps are ok |  | Case In Progress | -44764
Thunderhead | Resolved | 65 | Generator Inboard Potential ORBP | Alarm | Generator Inboard | 2023-12-20 | 2024-05-08 | 4 | Found broken wire in profibus connection on the 175x1 terminal plug. Rotated 195x1 to 175 x1. Faults cleared tower is running. Greased Gen for work order. 1/3/24 - direct has gone up signaifcantly sending out for inspection . 12/20/23 - contine to monitor cms specturm and direct (direct seems to have been increasing over past 6mo) | CMSGENB | 3248904 | Closed | Closed |  |  |  |  | False Positive | -45280
Santa Rita East | Resolved | 66 |  | Change 1 | Helical High Speed Stage | 2022-11-25 |  | 5 |  | Monitor | [8 empty] | -44890
Maverick | Active | 66 | Potential Main Bearing Rolling Element Damage | Sweep | Main Bearing | 2023-12-13 |  | 2 | 6/6/24 - Turbine DNR'd due to over temp. 2/15/24 - Turbine derated to 50% 1/8/24 - Borescope found minimal damage, however experienced a temperature event. Sending out for reinspection. 12/13/23 - Recommend main bearing borescope within 2 weeks from 12/13/23. | Final Report Needed | 3251209 | Closed | Closed |  | 2024-06-04 |  |  | Defect Confirmed - Repair Complete | 174
Bethel | Active | 66 | Potential Main bearing IRBP issue | Sweep | Main Bearing | 2024-05-17 |  | 2 | 5/17/24 - CMS shows Main bearing IRBP signature. Recommend main bearing borescope. | Monitor | 3352230 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45429
Maverick | Resolved | 66 | Main Bearing Accelerometer Open Circuit | Instrumentation | Main Bearing | 2024-09-16 |  | 5 | 9/16/24 - Main Bearing open circuit, please inspect wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3427596 | Closed | Closed |  | 2024-10-23 |  |  | Defect Confirmed - Repair Complete | 37
Thunderhead | Active | 66 | CMS Monitor Missing | Sweep | CMS Monitor | 2024-11-20 |  | 5 | 11/20/24 - CMS monitor is missing please check if CMS monitor is receiving a power signal and if the ethernet is connected into Port A. Requires troubleshooting and potentially a CBM download. | CMSTRBLSHOOT | 3466607 |  | Ready to Schedule |  |  |  |  | Case In Progress
Bethel | Active | 67 | Gen Outboard Bearing Damage | Warning | Generator Outboard | 2023-01-25 | 2024-10-16 | 3 | Add grease to both gen bearings | Monitor | 3072474 | Closed | Closed |  |  |  |  | Case In Progress | -44951
Upstream | Resolved | 67 |  | Warning | Helical High Speed Stage | 2021-06-04 |  | 1 |  | Pending Replacement |  |  |  |  | 2022-05-25 |  | low concern, high wind 10/13, 4/1 - High speed stage issue, reopening case, check CMS when data flow is restored, 5/25 - HSIS bearing failure - gearbox locked up, replacement | False Negative | 355
Santa Rita East | Resolved | 67 |  | Warning | Main Bearing | 2022-03-09 |  | W |  | Replacement | [5 empty] | 2022-08-15 |  | True Positive | -44629
Plymouth | Resolved | 67 | High Speed Stage Acceletometer issue. | Instrumentation | Helical High Speed Stage | 2024-10-07 |  | 4 | 10/7/24 - ​Possible HSS sensor issue, please investigate wiring and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3443194 | Closed | Ready to Schedule |  | 2024-10-11 |  |  | Defect Confirmed - Repair Complete | 4
Santa Rita East | Active | 67 | ZF S2 Carrier Bearing Issue | Warning | 2nd Planetary Stage | 2021-11-09 |  | 1 | Estimated failure date: Late Q2 early Q3 2023 Excessive spalling, micropitting, and indentations to first and second stage planetary bearings Indentations and pitting to planet gears. Derated to 50% until replacement is made | Final Report Needed | 3033153 | Closed | Closed |  |  | 4/4 - likely damage to stage 2 carrier GS outer race, potential damage to stage 3 bearings, DNR for main bearing, 8/31 - additional S2 planet fault alarm and DEI Intermediate warnings, S2 PS BRG IRBP fault harmonics are very pronounced at higher frequencies, 9/19 - S2 damage appears to progress after outage, 10/11 - debris counts resumed after cycling gearbox, likely HSS bearing damage, 11/3 - Borescope found pitting in the S1 and S2 PS BRG | 11/15 - spikes in Planet Fault GFED only, monitor, 12/28 -DEI has increased to the alarm setpoint, FFT indicates damage to the outer race of the stage 2 carrier bearing. Monitor for an increase in ORBP peak amplitude, direct signal 1/13 - stage 2 planet (maybe sun shaft) fault sidebands hit 0.15g. ORBP peak for Stage 2 Carrier DnWind is still 0.1g, 2/21 - no change, | Case In Progress | -44509
Sundance | Active | 67 | Generator Outboard ORBP | Sweep | Generator Outboard | 2023-09-25 |  | 3 | 9/25/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | Monitor | 3196350 | Closed | Closed |  |  |  |  | Case In Progress | -45194
Bethel | Active | 68 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-05-10 |  | 5 | Follow keyphasor troubleshoot guide | CMSTRBLSHOOT | 3125135 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45056
Deuel Harvest | Active | 68 | S1 Planet Carrier ORBP | Warning | 1st Planetary Stage | 2021-11-26 |  | 2 |  | Repair Pending | [6 empty] | 12/27 - potential damage to the stage 1 planet gear bearings, FFT shows 0.015 bearing fault frequencies, 6/28 - S1 PC BRG GS roller damage, 7/19 - S1 PS BRG IRBP fault peak is present, direct signal is peaking towards warning setpoint, 11/28 - S1 direct has spiked to warning setpoint twice recently but there is no trend upwards | Case In Progress | -44526
Santa Rita East | Resolved | 68 |  | Change 1 | 2nd Planetary Stage | 2022-05-22 |  | 6 |  | Monitor | [7 empty] | Case In Progress | -44703
Upstream | Resolved | 69 |  | Warning | 2nd Planetary Stage | 2022-05-29 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 | 6/17 - (ZF 5/29 event) isolated peak to warning setpoint in stage 2 DEI, much higher amplitude events in lower power modes indicates early bearing damage, sidebands on GMFs indicate potential ring gear damage, 11/29 - S2 SER Ring Fault signal is elevated, potential S2 BRG damage |  | Case In Progress | 240
Upstream | Resolved | 69 |  | Warning | Generator Inboard | 2022-08-28 |  | 1 |  | Monitor |  |  |  |  | 2022-12-20 |  | 9/7 - DE ORBP signal spiking to the warning setpoint, 5g impacts, low concern, 9/30 - additional ORBP warning, 12/20 - signal reduced to normal levels, resolving | False Positive - No Inspection | 114
Upstream | Resolved | 69 | Possible Generator IDE sensor issue | Instrumentation | Generator Inboard | 2023-12-29 |  | 4 | 12/29 - specturm data looks odd when looking through specturm history, looks to be a CMSGENB issue continue to monitor direct and cms specturm for changes, timebase also looks odd. Will send out work order for sensor issue | CMSGENB | 3248589 | Closed | Closed |  |  |  |  | Case In Progress | -45289
Deuel Harvest | Resolved | 70 |  | Instrumentation | Helical High Speed Stage | 2021-07-19 |  |  |  | CMSTRBLSHOOT | 2439482 |  | Closed |  | 2022-01-13 | Carlos created WO 2439482 in June, no action yet. 2/2 - Tech found loose wire, tightened |  |  | 178
Santa Rita East | Resolved | 70 | 2nd Planetary Stage Accelerometer | Instrumentation | 2nd Planetary Stage | 2023-04-05 |  | 5 | 2nd Planetary Stage accelerometer is currently reading an open circuit, please investigate sensor wiring and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3108903 | Closed | Closed |  | 2023-04-07 |  |  | Defect Confirmed - Repair Complete | 2
Santa Rita East | Resolved | 70 | High Speed Stage Accelerometer | Instrumentation | Helical High Speed Stage | 2023-04-05 |  | 5 | High Speed Stage accelerometer is currently reading an open circuit, please investigate sensor wiring and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3108909 | Closed | Closed |  | 2023-04-07 |  |  | Defect Confirmed - Repair Complete | 2
Santa Rita East | Active | 70 | Main Bearing BS2X | GE Alert | Main Bearing | 2022-09-21 |  | 1 |  | Final Report Needed | [5 empty] | 9/21 - GE alert, requesting thrust derate, oil sample, borescope/visual inspection through the grease port, 11/4 - offline |  | Case In Progress | -44825
Bethel | Resolved | 71 |  | Alarm | Helical High Speed Stage | 2022-01-31 |  | 5 | [7 empty] | 2023-01-25 |  | Case In Progress | -44592
Deuel Harvest | Resolved | 71 |  | EOW | Main Bearing | 2022-10-13 |  | 1 |  | EOW Claim | [6 empty] | 10/13 - EOW found IRBP micropitting strips, pitting on ORBP, 11/28 - |  | -44847
Santa Rita East | Resolved | 71 |  | Instrumentation | Keyphasor | 2022-10-11 |  |  | Use attached keyphasor guide to troubleshoot | CMSTRBLSHOOT | 3033101 | Closed | Closed |  |  | 2022-11-10 |  |  | -44845
Santa Rita East | Active | 71 | Main Bearing BS2X | GE Alert | Main Bearing | 2022-12-06 |  | 2 | 6/3/24 - Some surface damage present, continue to monitor. 5/1/24 - Recommend main bearing borescope + grease purge within 2 weeks from 5/1/24. | Monitor | 3345145 | Closed | Closed |  |  | 12/6 - main bearing alert, derate to 50% and borescope |  | Case In Progress | -44901
Deuel Harvest | Resolved | 72 |  | Instrumentation | Generator Inboard | 2022-02-02 | [8 empty] | 2022-04-05 | Failed Generator |  |  | 62
Deuel Harvest | Resolved | 72 |  | EOW | Main Bearing | 2022-10-13 |  | 1 |  | EOW Claim | [6 empty] | 10/13 - EOW found ORBP micropitting and particle drag |  | -44847
Upstream | Resolved | 72 |  | Warning | Helical High Speed Stage | 2021-09-15 |  | 3 |  | Monitor | [6 empty] | 11/3 - vibration floor has risen to ~0.1g, 11/30 - potential damage to HSS downwind bearing, cage, 1/11 - continue to monitor, 5/5 - high frequency harmonics indicate damage to HSS bearings, 8/19 - Controller Comms issue, rebooting monitor, 9/7 - additional HSS GS Cage warning, 10/19 - limited progression, | Case In Progress | -44454
Santa Rita East | Resolved | 72 |  | Change 1 | 2nd Planetary Stage | 2022-07-17 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44759
Santa Rita East | Resolved | 72 |  | Warning | Main Bearing | 2022-02-23 |  | 5 |  | Replacement | [5 empty] | 2022-07-10 |  | True Positive - Other Method Detected | -44615
Sundance | Active | 72 | Generator Outboard IRBP | Warning | Generator Outboard | 2024-06-06 |  | 3 | 7/8/24 - Continue to monitor for progression. 6/6/24 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact CMSEngineers_OSW@invenergyllc.com for support | Monitor | 3364298 | Closed | Closed |  |  |  |  | Case In Progress | -45449
Deuel Harvest | Active | 72 | HSS Pinion Issue | Alarm | Helical High Speed Stage | 2024-10-14 |  | 1 | 10/14/24 - Site responded stating they found the hydraulic brake disc dragging, likely causing the CMS signature. 10/14/24 - Please perform an auditory and visual inspection of the high speed shaft, pinion, and bearings within 24-72 hours. Also recommend derating turbine to 50% until inspection can be performed. | CMSHSS | 3445403 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45579
Plymouth | Active | 72 | Potential Main Bearing Issue | Sweep | Main Bearing | 2023-03-03 |  | 2 | 2/14/24 - GE requested turbine be derated to 50%. 4/10/23 - NTN bearing Outer race: spalling at the 7 O’clock position Inner race: Excessive indentations. Peeling damage has progressed to micropitting Rollers: indentations Grease: metallic Estimated remaining useful life: 3-6 months | Final Report Needed | 3093045 | Closed | Closed |  | 2024-03-26 |  |  | Defect Confirmed - Repair Complete | 389
Upstream | Resolved | 72 | potential S1 and S2 Planetary gearing/bearing issue | Warning | 2nd Planetary Stage | 2024-07-26 |  | 1 | Currently shut down. 7/26/24 - CMS indicates potential gearing/bearing issue in the S1 and S2 stage. Direct peaked and waveform impacting is present. Request to shutdown due to particle counter, and CMS data indication of issue. 7/30 - Borescope shows 3 planetary carrier spalling and secondary gear meshing damage. Requires complete replacement. Likely primary source of damage missed. Re-borescope requested. 8/6/24 - After re-borescope it was determined by engineering to implement a 50% derate to avoid further damage. 11/13/24 - Shut down due to increase in defect signature and rate of debris accumulation step change. | Longterm Watchlist | 3392101 | Closed | Closed | Q4 2024 | 2024-11-13 |  |  | Defect Confirmed - Repair Complete | 110
Thunderhead | Active | 72 | Main Bearing Banding | Sweep | Main Bearing | 2023-09-27 |  | 6 | 9/27/23 - Possible banding showing after a long term down time | Monitor | [7 empty] | Case In Progress | -45196
Santa Rita East | Resolved | 73 |  | Warning | Generator Outboard | 2021-10-13 |  | 6 |  | Monitor | [7 empty] | Case In Progress | -44482
Santa Rita East | Resolved | 73 | Oil Particle Levels Rising | Particle Counter | Particle Counter | 2023-12-19 | 2024-01-19 | 6 | 12/19/23 - Particle counts are rising, possible CMS signature on 2nd planetary stage bearings. Check back in a month. | Monitor | [7 empty] | Case In Progress | -45279
Maverick | Active | 73 | NTN Main Bearing Damage | GE Alert | Main Bearing | 2023-06-23 |  | 1 | 9/8/23 - Main bearing direct amplitudes have drastically increase in the past few days, recommend secondary inspection and DNRing turbine. 6/27/23 - Borescope found early pitting on inner and outer races. GE recommended 50% power derate. CMS will continue to monitor for bearing degradation. Estimated bearing failure ~1-3 months from 6/27/23. Please submit EoW claim. | Final Report Needed | [7 empty] | Case In Progress | -45100
Santa Rita East | Active | 73 | Potential 2nd Planetary Stage Bearing Issue | Sweep | 2nd Planetary Stage | 2023-10-05 | 2024-12-01 | 6 | 10/22/24 - CMS trends have progressed on this turbine, initial borescope (1/26/24) did not find much damage. Recommend re-borescoping this turbine within 1 month from 10/22/24. 4/1/24 - Possible minor spalling found on 2nd stage PBs, CMS will continue to monitor for progression. 1/16/24 - Recommend full gearbox borescope with focus on 2nd planetary stage within 1 month from 1/16/24. 10/15/23 - Potential 2nd stage bearing issue beginning, awaiting more progression before escalating. | CMSGBXBORE | 3449389 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45204
Plymouth | Resolved | 73 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-11 |  | 5 | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988838 | Cancelled | Cancelled |  |  | 10/12 - firmware update failed, "3701 monitor unable to read or write file" |  |  | -44784
Plymouth | Resolved | 73 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2024-03-18 |  | 3 | 3/18/24 - CMS monitor is netcom, please ensure monitor is powered and network cable is plugged into Port A. Contact CMSEngineers_OSW@invenergyllc.com for support. | CMSTRBLSHOOT | 3318168 | Closed | Closed |  | 2024-05-07 |  |  | Defect Confirmed - Repair Complete | 50
Plymouth | Resolved | 73 | CMS Monitor Netcom/Keyphasor Issue | Instrumentation | Other | 2024-08-05 |  | 3 | 8/5/24 - Not receiving data via Onyx Insight, please investigate if monitor is netcom or not receiving a speed signal. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3397321 | Closed | Ready to Schedule |  | 2024-09-27 |  |  | Defect Confirmed - Repair Complete | 53
Upstream | Resolved | 74 |  | Warning | Helical High Speed Stage | 2022-03-29 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 | 4/15 - potential misalignment, some bearing fault harmonics at high frequencies, 8/19 - HSS bearing fault harmonics or noise near 2X, 11/29 - S2 Direct change alert |  | Case In Progress | 301
Santa Rita East | Active | 74 | SKF Main Bearing Issue | Sweep | Main Bearing | 2023-02-15 |  | 1 | Inner- small indentations Outer - indentations (some large), peeling/adhesion damage Roller - standstill mark, indentations Grease - Mobil 460, golden but still some signs of of boundary layer formation Continue to monitor - CM Unit is shut down and placed on DNR list | Final Report Needed | 3084051 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -44972
Santa Rita East | Resolved | 74 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-06-19 |  | 5 | 6/19/24 - Keyphasor currently reading 0 RPMs and showing -12V gap. Please troubleshoot using attached guide, contact CMSEngineers_OSW@invenergyllc.com for support. | CMSTRBLSHOOT | 3369264 | Closed | Ready to Schedule |  |  |  |  | Case In Progress
Plymouth | Active | 74 | Timken Main Bearing Roller Element Issue | Warning | Main Bearing | 2024-09-03 |  | 2 | 9/26/24 - Turbine derated to 50%. 9/3/24 - Recommend borescoping this main bearing within 2 weeks from 9/3/24 with focus on outer race and rollers. | Repair Pending | 3413056 | Closed | Closed |  |  |  |  | Case In Progress | -45538
Upstream | Active | 74 | 1st Stage Planetary Bearing Issue | Sweep | 1st Planetary Stage | 2023-07-17 | 2025-03-09 | 3 | 9/8/23 - Minor damages to S1 planetary bearings, estimated replacement: Q4 2024/Q1 2025. 7/17/23 - Recommend full gearbox borescope with focus on 1st planetary stage within 1 month from 7/17/23. | Longterm Watchlist | 3157114 | Closed | Closed | Q4 2024 |  |  |  | Defect Confirmed - Awaiting Repair | -45124
Bethel | Resolved | 75 |  | Warning | 2nd Planetary Stage | 2021-10-31 |  | 6 |  | Monitor | [5 empty] | 2023-01-25 |  | Case In Progress | -44500
Deuel Harvest | Resolved | 75 |  | EOW | 1st Planetary Stage | 2022-08-30 |  | 1 |  | EOW Claim | [6 empty] | 9/21 - S1 PC BRG RS micropitting, S2 Ring fretting, S2 PS BRG indents | False Negative | -44803
Santa Rita East | Resolved | 75 |  | Warning | Helical High Speed Stage | 2021-10-23 |  | 1 |  | Monitor | [5 empty] | 2022-08-08 |  | False Positive - No Inspection | -44492
Deuel Harvest | Active | 75 | Generator Outboard Bearing Issue | GE Alert | Generator Outboard | 2022-10-03 |  | 2 | Potential NDE Generator bearing issue, recommend inspecting and adding grease to both generator bearings. If abnormal issues are found, please upload grease pictures and noise recording to HUVR. | Monitor | 3086589 | Closed | Closed |  |  |  | 10/13 - sensor found loose, vibration decreasing, 11/28 - vibrations have reduced to below warning point, decrease to Cat 3 | Case In Progress | -44837
Santa Rita East | Active | 75 | SKF Main Bearing Issue | Alarm | Main Bearing | 2023-02-08 |  | 1 | Roller - indentations, spalling; OR - indentations, spalling; IR - indentations, spalling; Grease - golden, thick. DNR until replacement - CM | Final Report Needed | 3079224 | Closed | Closed |  | 2023-10-11 |  |  | Defect Confirmed - Repair Complete | 245
Thunderhead | Active | 75 | Generator Inboard ORBP | Alarm | Generator Inboard | 2024-06-24 |  | 3 | 6/24/24 - CMS spectrum data indicate generator inboard orbp defect. | CMSGENB | 3370787 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45467
Upstream | Resolved | 76 |  | Warning | 1st Planetary Stage | 2021-10-08 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 | 11/18 - occasional high amplitude periods in Stage 1 Carrier DnWind IRBP SVE lifetime, 1/11 - no fault indications in FFT, continue to monitor, 2/8 - FFT shows 0.01g gear fault sidebands in addition to stage 2 planet gear rollers and two unidentified peaks at 16.406X and 8.031X shaft speed, 5/25 - stage 1 FFT indicates damage to S1 PC BRG GS rollers, raceways, 8/19 - IRBP signal has reduced to below warning, no progression, 11/10 - spikes in the S1 Carrier DnWind IRBP SVE signal, 12/20 - monitor for progression |  | Case In Progress | 473
Santa Rita East | Resolved | 76 |  | Warning | Helical High Speed Stage | 2021-07-16 |  | 1 |  | Monitor | [6 empty] | 11/15 - peaks between 2X and 3X GMF are concerning, 12/2 - worried about stage 3 mesh, Inspection found no damage, continue to monitor, 12/28 - continue to monitor, 1/31 - sidebands between 2x and 3x GMF are increasing in amplitude, | Case In Progress | -44393
Plymouth | Resolved | 76 | S1 Planetary Bearing Issue | Alarm | 1st Planetary Stage | 2022-06-11 |  | 1 | Spalling on the RS planetary bearing and spalling of the S1 + S2 sun pinions. | Longterm Watchlist | 3041238 | Closed | Closed |  |  |  | Main Bearing ENV shows elevated floor, Health index indicates S1 PS BRG IRBP | True Positive | -44723
Deuel Harvest | Resolved | 77 |  | Warning | Helical High Speed Stage | 2021-08-19 |  | 2 |  | Monitor | 2581092 | Cancelled | Cancelled |  |  |  |  | Case In Progress | -44427
Upstream | Resolved | 77 |  | Warning | Helical High Speed Stage | 2021-08-14 |  | 3 |  | Monitor | [5 empty] | 2/10 - early S1 PS BRG harmonics occasionally | 11/3 - monitor floor on frequency spectrum, 11/18 - peak at ball spin 1X, 1/11 - occasional peaks to warning setpoint in timeseries, 2/8 - continue to monitor, 4/15 - FFT shows peak at 2X roller frequency for the HSS GS bearing, massive peak at 12X shaft speed, trend shows step up to warning setpoint, 9/7 - HSS mesh misalignment, S1 PC BRG GS roller damage, 10/19 - HSS GS roller harmonics, 11/10 - S1 PC BRG GS roller harmonics - potential end scoring | Case In Progress | -44422
Upstream | Resolved | 77 | Pinion issue | Alarm | Helical High Speed Stage | 2024-04-15 |  | 3 | 4/17/23 - Sent out for inspection for possible pinion tooth damage. Derated by 50%. | CMSHSS | 3334720 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45397
Plymouth | Active | 77 | Timken Main Bearing BS2X Signature | Warning | Main Bearing | 2024-01-11 |  | 2 | 1/11/24 - Warranty case submitted with CMS data, continue to monitor. | Final Report Needed |  |  |  |  | 2024-05-09 |  |  | Defect Confirmed - Repair Complete | 119
Plymouth | Resolved | 77 |  | Instrumentation | Keyphasor | 2022-08-11 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988839 | Cancelled | Cancelled | [5 empty] | -44784
Plymouth | Resolved | 77 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-04-10 |  | 3 | Please inspect keyphasor system using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3110519 | Closed | Closed |  | 2023-04-20 |  |  | Defect Confirmed - Repair Complete | 10
Upstream | Active | 77 | Main bearing ORBP | Sweep | Main Bearing | 2024-07-25 | 2025-03-10 | 4 | 7/25/24 - potential main beairng ORBP signature. Continue to monitor for progression. | Monitor | [7 empty] | Case In Progress | -45498
Upstream | Active | 77 | Potential HSS Bearing issue | Alarm | Helical High Speed Stage | 2024-09-06 |  | 3 | [9 empty] | Case In Progress
Bethel | Resolved | 78 | Generator Outboard ORBP | Alarm | Generator Outboard | 2023-12-28 | 2024-05-21 | 3 | 5/6/24 - Recommend 50% derate due to step change. 12/28/23 - Generator Outboard ORBP signature is showing up on the spectrum and direct trend is increasing | CMSGENB | 3246656 | Closed | Ready to Schedule |  | 2024-06-18 |  |  | Defect Confirmed - Repair Complete | 173
Deuel Harvest | Resolved | 78 |  | EOW | Main Bearing | 2022-10-13 |  | 1 |  | EOW Claim | [6 empty] | 10/13 - EOW found micropitting on raceways, 11/28 - temps look good |  | -44847
Upstream | Resolved | 78 | HSS Pinion Tooth Damage | Alarm | Helical High Speed Stage | 2022-09-28 |  | 1 | Fractured Pinion Tooth, HSS replacement pending | CMSGBXBORE | 3036161 |  | Closed |  | 2023-03-13 | 3/13 - HSS replacement complete, latch reset, resolved | 9/30 - sudden high amplitude increase in GFED, pinion fault sidebands are present at lower frequencies, Direct signal shows low ampliutde step increase, S2 direct shows coinciding small increase- and sun fault sidebands, 10/18 - borescope found fractured pinion tooth, follow up borescope scheduled for 3 months, 11/10 - additional S3 pinion fault alarm, step up in vibration signals, likely progression, 12/20 - continued progression | True Positive | 166
Santa Rita East | Active | 78 | Main Bearing BS2X | Sweep | Main Bearing | 2023-03-22 |  | 1 | Turbine placed on DNR list, to remain down until replacement can be made. | Final Report Needed | 3101734 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45007
Upstream | Resolved | 78 | S3, HSS Gearing issue | Alarm | Helical Intermediate Stage | 2024-01-31 | 2024-08-07 | 3 | repaircoplete.3/12/24 - Borescope found fractured tooth on low speed shaft. 1/31/24 - CMS indicates there is an issue in the gearing in the Helical Intermediate Stage. CMSHSS work order made to inspect T-78 | Final Report Needed | 3263782 | Closed | Closed | Q2-3 2024 |  |  |  | Defect Confirmed - Repair Complete | -45322
Bethel | Active | 79 | Main Bearing Inner Race Issue | Sweep | Main Bearing | 2023-09-25 | 2024-05-23 | 3 | 5/17/24 - considering spectrum and direct progression, would likely soon reccomend re-borescope to check on defect progression. 10/23/23 - Denting/early spalling seen on both the inner and outer races. Circumferential groove noted on the inner race as well, CMS will continue to monitor for progression. 9/25/23 - Recommend main bearing borescope within 1 month from 9/25/23. | Longterm Watchlist | 3196860 | Closed | Closed |  |  |  |  | Case In Progress | -45194
Santa Rita East | Resolved | 79 |  | Particle Counter | Particle Counter | 2022-07-22 |  | 1 |  | Replacement | 2965481 | Closed | Closed |  |  |  | 7/22 - high debris counts across bins, likely HSS GS IRBP damage with high frequency fault harmonics, pinion sidebands as well, S2 PG sidebands, S2 PC BRG GS ORBP fault peak with harmonics, 8/8 - bins 1 and 2 maxed out, 11/4 - 11,090 mg debris detected | Case In Progress | -44764
Maverick | Resolved | 79 |  | Instrumentation | Helical High Speed Stage | 2021-10-14 |  |  |  | CMSTRBLSHOOT | 2616558 |  | Closed |  | 2022-02-15 | Replace gearbox sensor 3, 1/11- an't connect to monitor for loop check, pushed monitor reboot |  |  | 124
Upstream | Resolved | 79 |  | Warning | Helical High Speed Stage | 2022-05-29 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 | 6/17 - (ZF 5/29 event) isolated peak to warning setpoint in stage 3, much higher amplitude events in lower power modes indicates early bearing damage, 11/29 - HSIS GS IRBP harmonics are well pronounced, 12/20 - potential HSS GS ORBP damage as well |  | Case In Progress | 240
Santa Rita East | Active | 79 | ZF S1 Planetary Bearing Issue | Sweep | 1st Planetary Stage | 2023-02-09 |  | 2 | 3/25/24 - Recommend 50% derate until gearbox is replaced. 4/26/23 - Moderate damage shown on the S1 planetary bearings and CMS indicates damage to the S2 carrier bearings as well. Recommend replacing gearbox in ~9-12 months from 4/26/23. 2/9/32 - CMS + borescope indicates damage on the Stage 1 Planetary bearings | Final Report Needed | 3079967 | Closed | Closed |  | 2024-04-30 |  |  | Defect Confirmed - Awaiting Repair | 446
Maverick | Active | 79 | SKF Main Bearing Issue | Sweep | Main Bearing | 2024-08-03 |  | 2 | DNRd 10/1/24 - Recommend borescoping this main bearing within 2 weeks from 10/1/24 with focus on outer race and rollers. Also recommending a 50% derate on this turbine to prolong bearing life. | Final Report Needed | 3440432 | Cancelled | Ready to Schedule |  | 2024-10-03 |  |  | Defect Confirmed - Repair Complete | 61
Plymouth | Resolved | 79 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-04-10 |  | 3 | Please inspect keyphasor system using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3110521 | Closed | Closed |  | 2023-04-20 |  |  | Defect Confirmed - Repair Complete | 10
Plymouth | Resolved | 79 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-11 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988840 | Cancelled | Cancelled | [5 empty] | -44784
Bethel | Resolved | 80 |  | Alarm | 1st Planetary Stage | 2022-04-01 |  | 3 |  | Borescope | [5 empty] | 2023-01-25 |  | Case In Progress | -44652
Deuel Harvest | Resolved | 80 |  | EOW | Main Bearing | 2022-10-13 |  | 1 |  | EOW Claim | [6 empty] | 10/13 - EOW found ORBP micropitting and particle drag |  | -44847
Santa Rita East | Resolved | 80 |  | Warning | 1st Planetary Stage | 2022-04-30 |  | 1 |  | Monitor | [7 empty] | Case In Progress | -44681
Santa Rita East | Resolved | 80 |  | Instrumentation | Main Bearing | 2022-04-25 |  |  | Shorted Sensor Wiring | CMSTRBLSHOOT | 2922956 | Closed | Closed |  | 2022-05-03 | 5/3 - Angel says he repalced sensor |  |  | 8
Santa Rita East | Resolved | 80 | Main Bearing Accelerometer | Instrumentation | Main Bearing | 2023-03-22 |  | 5 | ​Main Bearing accelerometer is currently showing a shorted circuit, please inspect wiring and connections. Replace sensor if needed. For support reach out to abarndt@invenergy.com | CMSTRBLSHOOT | 3101733 | Closed | Closed |  | 2023-03-23 |  |  | Defect Confirmed - Repair Complete | 1
Santa Rita East | Resolved | 80 | Oil Particle Levels Rising | Particle Counter | Particle Counter | 2023-12-19 | 2024-04-01 | 6 | 12/19/23 - Particle counts appear to be rising since beginning of November. No CMS signature present. | Monitor | [7 empty] | Case In Progress | -45279
Maverick | Active | 80 | Potential Main Bearing issue | Alarm | Main Bearing | 2023-12-27 |  | 2 | 12/27/23 - Inspection found cracked roller, turbine DNR'd until repair. 12/27/23 - Main bearing direct spiked at 11g with no significant progression shown (NTN) specturm data changed significantly over the past 3 days, Work order will be sent out for inspection/borescope | Final Report Needed | [7 empty] | Defect Confirmed - Awaiting Repair | -45287
Upstream | Resolved | 80 |  | Warning | Helical High Speed Stage | 2021-07-04 |  | 3 |  | Monitor | [6 empty] | 10/1 - frequency peak at stage 2 gear mesh, 11/3 - potential damage to stage 3 bearings, wait to peak amplitude to be higher then HSS check 1/11 - peaks to warning, 6/17 - High res FFT shows high frequency bearing fault harmonics, suggesting damage to HSS bearings, high vibration floor in enevelope, | Case In Progress | -44381
Upstream | Resolved | 80 |  | Alarm | Main Bearing | 2022-05-19 |  | 3 |  | Monitor | [6 empty] | 5/25 - main bearing direct has increased to the alarm setpoint since 3/11. Occasional 4-5g impacts in the timebase, temps look normal to neighbors, 8/19 - 2g impacts continue, temps look good, no fault harmonics, 9/7 - signal has reduced to below warning setpoint | Case In Progress | -44700
Bethel | Active | 81 | S2 Standstill Marks | Case Tracking | 2nd Planetary Stage | 2023-02-06 |  |  |  | Monitor | [5 empty] | 2/6 - 18x harmonics in S2, present for lifetime since replacement, likely standstills |  | Case In Progress | -44963
Maverick | Active | 81 | Main Bearing BS2X | GE Alert | Main Bearing | 2023-06-22 |  | 1 | EoW borescope found damage on the rolling elements, GE recommended shutdown until repair | Final Report Needed | [7 empty] | Case In Progress | -45099
Bethel | Active | 81 | Generator Outboard ORBP | Warning | Generator Outboard | 2024-04-23 | 2024-09-20 | 6 | 4/24/24 - Continue to monitor, awaiting direct increase. | Monitor | [7 empty] | Case In Progress | -45405
Bethel | Resolved | 81 | Gen Outboard Bearing Damage | Warning | Generator Outboard | 2023-01-26 | 2024-03-01 | 3 | 4/1/24 - Closed due to inactivity1/26/23- Add grease to both gen bearings | Monitor | 3072475 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -44952
Upstream | Resolved | 81 |  | Warning | Helical High Speed Stage | 2022-05-29 |  | 6 |  | Monitor |  |  |  |  | 2023-01-24 | 9/7 - potential HSS GS IRBP damage with pinion fault sidebands, | 6/17 - (ZF 5/29 event) isolated peak to warning setpoint in stage 3, much higher amplitude events in lower power modes indicates early bearing damage, | Case In Progress | 240
Thunderhead | Resolved | 81 | NDE Gen Bearing Sensor Issue | Instrumentation | Generator Outboard | 2023-01-24 |  | 5 | 2/26 - resolved, Check harness for open wiring | CMSTRBLSHOOT | 3071333 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -44950
Bethel | Resolved | 82 |  | Instrumentation | Main bearing | 2022-01-31 |  |  | Check for shorted sensor wiring |  | 2740321 |  | Cancelled |  |  | 2023-01-25 |  |  | -44592
Deuel Harvest | Resolved | 82 |  | Instrumentation | CMS Monitor | 2022-02-02 | [8 empty] | 2022-07-19 |  |  |  | 167
Bethel | Resolved | 82 | Thermal Event | Case Tracking | Main Bearing | 2023-09-18 |  | 1 | 9/18/23 - Turbine thermal event likely directly caused by a failure of it's main bearing. Did not catch due to the main bearing sensor having a short circuit.' | [8 empty] | Miss - Defect Not Caught | -45187
Santa Rita East | Active | 82 | Main Bearing Issue | Sweep | Main Bearing | 2023-07-24 |  | 2 | Pitting damage found on rollers and raceways, estimated replacement needed 5-8 months from 7/28/23. Continuing to monitor via CMS. | Final Report Needed | 3160598 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45131
Upstream | Resolved | 82 |  | Alarm | 2nd Planetary Stage | 2021-10-29 |  | 3 |  | Monitor | 2631282 | Closed | Closed |  |  |  | spikes on 10/29, borescope, 11/4 - no smoking gun found in borescope during inspection, Jump up to warning setpoint, monitor closely, 1/5 - sensor 2 is not ok, events are from bad sensor | False Positive - Sensor Issue | -44498
Upstream | Resolved | 82 |  | Warning | Helical High Speed Stage | 2022-05-29 |  | 1 |  | Monitor |  |  |  |  | 2022-11-10 |  | 6/17 - (ZF 5/29 event) isolated peak to warning setpoint in stage 3, much higher amplitude events in lower power modes indicates early bearing damage, 11/10 - resolving | False Positive - No Inspection | 165
Upstream | Resolved | 82 |  | Instrumentation | 2nd Planetary Stage | 2022-01-05 |  |  | Open Sensor Wiring | CMSTRBLSHOOT | 2702483 |  | Closed |  | 2022-08-29 | 1/5 - bias voltage = 22V, open sensor wiring or bad sensor, 1/11 - alarm and warning events due to sensor issue |  |  | 236
Plymouth | Active | 82 | Timken Main Bearing Rolling Element Issue | Warning | Main Bearing | 2024-03-18 |  | 2 | 4/22/24 - Turbine derated to 50%. 3/18/24 - Recommend main bearing borescope + grease purge within 2 weeks from 3/18/24. | Final Report Needed | 3318129 | Closed | Closed |  | 2024-07-12 |  |  | Defect Confirmed - Repair Complete | 116
Deuel Harvest | Active | 82 | S2 Planetary IRBP/ORBP issue | Alarm | 2nd Planetary Stage | 2025-02-20 |  | 3 | 2/10/25 - CMS shows indication of S2 Planetary IRBP/ORBP issue. | CMSGBXBORE | 3505545 |  | Ready to Schedule |  |  |  |  | Case In Progress
Bethel | Active | 83 | Main Bearing raceway damage | Case Tracking | Main Bearing | 2023-02-03 | 2024-11-25 | 6 |  | Monitor | [5 empty] | 2/3 - likely IRBP standstills, no progression in 6 mo |  | Case In Progress | -44960
Bethel | Resolved | 83 |  | Warning | Helical High Speed Stage | 2022-01-04 |  | 5 | [7 empty] | 2023-01-25 |  | Case In Progress | -44565
Santa Rita East | Resolved | 83 |  | Warning | 1st Planetary Stage | 2022-05-19 |  | 5 |  | Monitor | 2942222 | Closed | Closed |  |  | 6/6 - spike in all 3 stages on 6/4. Suspected damage to S1 PC BRG GS raceways, rollers, potentially S1 PS BRG damage as well, S2 PS BRG rollers, S3 HSS GS, Pinion fault, 6/30 - borescope didn't find major damage, continue to monitor, 8/8 - S1 Direct continues to peak below alarm setpoint, 8/31 - slow debris generation, 10/12 - reduce to cat 2, 11/28 - offline for pitch bearing |  | Case In Progress | -44700
Maverick | Resolved | 83 | Keyphasor Issue | Keyphasor Issue | Keyphasor | 2022-03-28 |  |  | Use Keyphasor troubleshoot guide | CMSTRBLSHOOT | 2892348 |  | Cancelled |  | 2022-04-11 | 3/31 - Matt bates troubleshoot, "Unplugged all the wires in that circuit. Re-ferruled the wiring coming from the Bently Nevada to the pulse expander module. We I first removed the PEM I took an OHM reading of the signal terminals and had a reading of 63.4 kOHMs. Before I put it back it was reading 13.3 kOHMs. That might be the issue, more testing needed." |  |  | 14
Maverick | Resolved | 83 | IONet Issue | Instrumentation | CMS Monitor | 2023-07-17 |  | 4 | Please perform toolbox download to CBM card. | CMSTRBLSHOOT | 3157466 | Closed | Closed |  | 2023-10-27 |  |  | Defect Confirmed - Repair Complete | 102
Bethel | Active | 83 | Potential 1st Planetary Stage Bearing Issue | Sweep | 1st Planetary Stage | 2024-05-09 |  | 3 | 5/9/24 - Please perform a full gearbox borescope with focus on the 1st planetary stage at next tower climb. | Longterm Watchlist | 3348812 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45421
Bethel | Resolved | 84 |  | Alarm | Helical High Speed Stage | 2021-10-25 |  | 6 | [7 empty] | 2023-01-25 |  | Case In Progress | -44494
Santa Rita East | Active | 84 | HSS DnWind Rear IRBP | Warning | Helical High Speed Stage | 2023-05-15 |  | 6 | 9/19/23 - Borescope did not find damages, CMS will continue to monitor. 5/9/23 - Recommend full gearbox borescope with a focus on the high speed stage within 6 months from 5/9/23. | Monitor | 3124175 | Closed | Closed |  |  |  |  | Case In Progress | -45061
Santa Rita East | Active | 84 | Potential Main Bearing Issue | Sweep | Main Bearing | 2023-12-04 | 2024-11-06 | 6 | 12/4/23 - Potential main bearing damage, monitor for progression | Monitor | [7 empty] | Case In Progress | -45264
Bethel | Active | 84 | Potential S1 Planetary IRBP Issue | Case Tracking | 1st Planetary Stage | 2024-05-20 | 2024-08-02 | 2 | 5/20/24 - CMS shows bearing defect siganture | CMSGBXBORE | 3353209 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45432
Maverick | Active | 84 | NTN Main Bearing BS2X Signature | Sweep | Main Bearing | 2024-07-03 |  | 2 | 7/31/24 - Turbine derated to 40% per customer request. 7/3/24 - Recommend borescoping this main bearing within 2 weeks from 7/3/24 with focus on outer race and rollers. | Final Report Needed | 3379475 | Closed | Closed |  | 2024-08-28 |  |  | Defect Confirmed - Repair Complete | 56
Deuel Harvest | Resolved | 84 | Missing CMS data | Instrumentation | Other | 2024-04-24 |  | 3 | 4/24/2024 - CMS data for this turbine is missing, please troubleshoot and download to CBM in toolbox. | CMSTRBLSHOOT | 3337122 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Repair Complete | -45406
Bethel | Resolved | 85 | Generator Ouboard IRBP | Warning | Generator Outboard | 2023-09-25 |  | 6 | 9/25/23 - Awaiting direct increase | Monitor | [7 empty] | Case In Progress | -45194
Santa Rita East | Resolved | 85 |  | Change 1 | Helical High Speed Stage | 2022-11-03 |  | 6 |  | Monitor | [5 empty] | 11/4 - DEI Structural change alerts for all stages, likely early HSS BRG raceways damage, 12/15 - 37mg debris detected |  |  | -44868
Santa Rita East | Resolved | 85 |  | Warning | Main Bearing | 2022-02-23 |  | 1 |  | Replacement Complete | 2910100 | Closed | Closed |  | 2022-09-27 |  | 4/7 - Main bearing shows failure harmonics in the FFT indicating damage to the rollers consistent with other SKF main bearing failures. Direct signal increase along with elevated temperatures relative to neighbors indicates progressing damage to the main bearing. Recommending borescope, 4/25 - peaks to warning setpoint, monitor for progression, tower is DNR for MB, 11/3 - borescope found turned and chipped roller, waiting on replacement config | True Positive | 216
Maverick | Active | 85 | Generator Inboard ORBP | Alarm | Generator Inboard | 2023-06-19 |  | 6 | Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | Monitor | 3144096 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45096
Maverick | Active | 85 | NTN Main Bearing BS2X Signature | Sweep | Main Bearing | 2024-03-26 |  | 2 | 5/19/24 - Turbine has faulted and was placed into DNR 5/3/24 - Turbine derated to 50%. 3/26/24 - Recommend main bearing borescope and 50% power derate at next opportunity. | Final Report Needed | 3323505 | Closed | Closed |  | 2024-05-19 |  | Case In Progress | Defect Confirmed - Repair Complete | 54
Thunderhead | Active | 85 | S1 Carrier Bearing Issue | GE Alert | 1st Planetary Stage | 2023-02-14 | 2025-03-09 | 4 | 2/8/24 - GE escalation, awaiting borescope inspection. | Monitor | 6693310 |  |  |  |  | 2/14 - S1 PS BRG fault harmoincs in the MB spectrum. 2/8/24 - Borescope WO made by GE for this turbine |  | Case In Progress | -44971
Deuel Harvest | Resolved | 86 |  | Warning | Main Bearing | 2022-06-23 |  | 2 |  | Monitor | 2950746 | Cancelled | Cancelled |  |  |  |  | Case In Progress | -44735
Santa Rita East | Resolved | 86 |  | Warning | 2nd Planetary Stage | 2022-09-12 |  | 5 |  | Monitor | [5 empty] | 9/20 - potentially suspect vibration from sensor 2, 11/4 - potential early S2 ring fault, 12/15 - recent progression in debris generation, 337mg detected, |  |  | -44816
Santa Rita East | Resolved | 86 |  | Alarm | 2nd Planetary Stage | 2022-06-26 |  | W |  | Pending Replacement |  |  |  |  | 2022-08-26 |  | 6/30 - Stage 2 SER Planet Fault signals are spiking above the alarm threshold but there isn't any sideband growth around the mesh frequencies, 7/28 - tower down for temp reading - major HSIS shaft damage, tower DNR for significant S2 tooth, bearing, and shaft damage | True Positive - Other Method | 61
Santa Rita East | Resolved | 86 | 2nd Stage Planetary Accelerometer Issue | Instrumentation | 2nd Planetary Stage | 2023-01-23 |  | 4 | 2nd Stage Planetary Stage Sensor is currently showing erroneous readings, please inspect wiring and connections. Replace sensor if needed. Please reach out to Andrew Barndt if you have any questions. | CMSTRBLSHOOT | 3071073 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -44949
Maverick | Active | 86 | Main Bearing BS2X | Sweep | Main Bearing | 2024-09-11 |  | 6 | 9/19/24 - AEP Requested 50% derated. 8/27/24 - Slight MB signature, check back in on this. | Repair Pending | [7 empty] | Defect Confirmed - Awaiting Repair | -45546
Maverick | Resolved | 86 |  | Warning | Generator Inboard | 2022-05-15 |  | 1 |  | GE request CMSGENB | 2931882 | Closed | Closed |  | 2022-11-16 | 5/17 - GE alert for inboard gen bearing. 20g impacts in the timebase and 3g peak in the FFT, 6/14 - trend is now hitting 100g, recommended derate to 40% and increased inspection priority, 6/21 - inspection found misaligned gen fan shaft, reaching out for info on repair, 8/25 - tower offline for repair, 11/16 - replaced, resolving |  | True Positive - GE Alert | 185
Thunderhead | Resolved | 86 | CMS Monitor Missing | Instrumentation | CMS Monitor | 2023-02-21 |  | 5 | 2/21/23 - Please ensure CMS monitor is receiving a power signal and ethernet is connected into Port A | CMSTRBLSHOOT | 3085874 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Repair Complete | -44978
Bethel | Active | 87 | Gen Outboard Bearing Damage | Warning | Generator Outboard | 2023-01-26 | 2024-10-12 | 3 | 5/9/23 - Grease added | Monitor | 3072476 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -44952
Bethel | Resolved | 87 |  | Warning | Helical High Speed Stage | 2021-10-12 |  | 6 | [7 empty] | 2023-01-25 |  | Case In Progress | -44481
Santa Rita East | Resolved | 87 |  | Warning | Helical High Speed Stage | 2022-11-14 |  | 6 |  | Monitor | [6 empty] | 12/15 - low concern, follow up if no flow in PC continues |  | -44879
Maverick | Active | 87 | NTN Main Bearing BS2X Signature | Alarm | Main Bearing | 2024-03-08 |  | 2 | 3/8/24 - Recommend main bearing borescope + grease purge within 2 weeks from 3/8/24. Turbine also derated to 50%. | Final Report Needed | 3314843 | Closed | Closed |  | 2024-04-05 |  |  | Defect Confirmed - Repair Complete | 28
Maverick | Resolved | 87 | High Speed Stage Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2024-07-12 |  | 4 | 7/12/24 - ​High speed stage accelerometer is reading a short circuit, please investigate wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | 3385099 | Closed | Closed |  | 2024-07-18 |  |  | Defect Confirmed - Repair Complete | 6
Deuel Harvest | Active | 87 | Early signs of potential HSS pinion issue | Alarm | Helical High Speed Stage | 2024-01-16 |  | 4 | 1/16/24 - early signs of potential HSS pinion issue is seen on CMS however it isn't consistent enough yet continue to monitor | Monitor | [7 empty] | Case In Progress | -45307
Maverick | Resolved | 87 |  | Keyphasor Issue | Keyphasor | 2022-03-28 |  |  | Use Keyphasor troubleshoot guide | CMSTRBLSHOOT | 2892349 |  | Closed |  | 2022-04-11 | 3/31 - Matt bates troubleshoot, Garrett identified wires in the wrong place " signal and common" plugged into wrong location on PLC, did not resolve issue, closing work order, investigate Ge options, 4/12 -corrected wiring based on what was written on the wires, "Swapped 70A2/SIG and 70A2/COM. " from Craig |  |  | 14
Maverick | Resolved | 87 |  | Instrumentation | Keyphasor | 2022-02-15 |  |  | Troubleshoot keyphasor | CMSTRBLSHOOT | 2802865 |  | Closed |  | 2022-02-23 | Rowdy rebooted monitor 2/23, reboot solved issue, wo closed |  |  | 8
Maverick | Resolved | 87 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-06-27 |  | 2 | Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3148601 | Closed | Ready to Schedule |  | 2024-06-27 |  |  | Defect Confirmed - Repair Complete | 366
Thunderhead | Resolved | 87 | CMS Monitor Missing | Instrumentation | CMS Monitor | 2023-02-21 |  | 5 | 2/19/23 - Please ensure CMS monitor is receiving a power signal and ethernet is connected into Port A | CMSTRBLSHOOT | 3085874 | Closed | Closed | [5 empty] | -44978
Santa Rita East | Resolved | 88 |  | Instrumentation | Helical High Speed Stage | 2022-12-12 |  | 5 | Shorted Sensor Wiring | CMSTRBLSHOOT | 3056170 | Closed | Closed | [5 empty] | -44907
Santa Rita East | Resolved | 88 | 2nd Planetary Stage Accelerometer Open Circuit | Instrumentation | 2nd Planetary Stage | 2023-10-30 |  | 5 | 10/30/23 - 2nd planetary stage accelerometer is reading an open circuit, please inspect wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3214922 | Closed | Closed |  | 2023-11-08 |  |  | Defect Confirmed - Repair Complete | 9
Santa Rita East | Active | 88 | Main Bearing BS2X | GE Alert | Main Bearing | 2023-01-04 |  | 1 | IR - indentations, OR - indentations, grease - bronze - thrust derated by GE on 1/9/23 Exp failure date Late Q2 early Q3 2023 | Final Report Needed | 3064235 | Closed | Closed |  | 2023-05-18 |  | 1/6 - GE recommends 50% derate and inspection | Defect Confirmed - Repair Complete | 134
Bethel | Resolved | 88 | Generator Outboard ORBP | Warning | Generator Outboard | 2024-04-01 |  | 3 | 4/1/24 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact CMSEngineers_OSW@invenergyllc.com for support | CMSGENB | 3326984 | Closed | Ready to Schedule |  | 2024-04-13 |  |  | Defect Confirmed - Repair Complete | 12
Maverick | Resolved | 88 | 2nd Stage Planetary Accelerometer Issue | Instrumentation | 2nd Planetary Stage | 2023-03-20 |  | 5 | ​2nd Planetary Stage Accelerometer is currently reading an open circuit, recommend inspecting wiring/harness. | CMSTRBLSHOOT | 3100979 | Closed | Closed |  | 2023-05-17 |  |  | Defect Confirmed - Repair Complete | 58
Bethel | Resolved | 89 |  | Warning | Helical High Speed Stage | 2021-10-04 |  | 6 |  | Monitor | [5 empty] | 2023-01-25 |  | Case In Progress | -44473
Bethel | Resolved | 89 |  | Warning | Helical High Speed Stage | 2021-06-22 |  | 6 |  | Monitor | [5 empty] | 2023-01-25 |  | Case In Progress | -44369
Maverick | Resolved | 89 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2024-02-06 |  | 3 | 2/6/24 - CMS monitor appears netcom, please inspect that CMS monitor is powered and ethernet cable is plugged into port A. | CMSTRBLSHOOT | 3268241 | Cancelled | Ready to Schedule |  | 2024-02-22 |  |  | Defect Confirmed - Repair Complete | 16
Deuel Harvest | Resolved | 90 |  | Warning | Main Bearing | 2021-11-12 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44512
Santa Rita East | Resolved | 91 |  | Warning | 2nd Planetary Stage | 2021-10-20 |  | W |  | Monitor |  |  |  |  | 2022-06-30 |  | 1/13 - Stage 2 FFT shows peak at 19.063, 7/21 - case resolved prior to turbine fire - unrelated alarm | False Positive - No Inspection | 253
Santa Rita East | Resolved | 91 |  | Alarm | Main Bearing | 2022-04-05 |  | W |  | Replacement |  |  |  |  | 2022-06-30 |  | 4/7 - detected via tads, turbine fire - tower offline | True Positive - Other Method Detected | 86
Bethel | Resolved | 91 | Main Bearing raceway damage | Case Tracking | Main Bearing | 2023-02-03 |  | 3 | Spalling on IR - EST failure date - Q4 2023 - Q1 2024 - CM | Repair Pending |  |  |  |  | 2024-11-08 | 2/3 - multiple fault harmonics, no progression in 6 mo |  | Defect Confirmed - Repair Complete | 644
Maverick | Active | 92 | Timken Main Bearing BS2X Signature | Sweep | Main Bearing | 2024-02-06 |  | 1 | 2/6/24 - Recommend main bearing borescope and thrust derate at next possible opportunity. | Final Report Needed | 3268246 | Closed | Closed |  | 2024-02-26 |  |  | Defect Confirmed - Repair Complete | 20
Bethel | Resolved | 93 |  | Instrumentation | Helical High Speed Stage | 2022-01-31 |  |  | Check sensor wiring and circuit |  | 2740325 |  | Closed |  |  | 2023-01-25 |  |  | -44592
Deuel Harvest | Resolved | 93 |  | Warning | Helical High Speed Stage | 2021-12-21 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44551
Santa Rita East | Resolved | 93 | Main Bearing BS2X | GE Alert | Main Bearing | 2022-01-04 |  | 1 | Signature progressed and turbine is on the DNR list until main bearing replacement. | Final Report Needed | 3064234 | Closed | Closed |  |  |  | 1/6 - GE recommends 50% derate and inspection |  | -44565
Santa Rita East | Resolved | 93 | 1st Planetary Stage Accelerometer Short Circuit | Instrumentation | 1st Planetary Stage | 2023-05-22 |  | 5 | ​1st Planetary stage accelerometer showing short circuit, please investigate wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | 3130604 | Closed | Closed |  | 2023-05-24 |  |  | Defect Confirmed - Repair Complete | 2
Bethel | Resolved | 94 |  | Alarm | Helical High Speed Stage | 2021-09-21 |  | 5 |  | Monitor | [5 empty] | 2023-01-25 |  | Case In Progress | -44460
Deuel Harvest | Resolved | 94 |  | Warning | Main Bearing | 2022-08-09 |  | 1 |  | Monitor | [8 empty] | -44782
Santa Rita East | Resolved | 94 |  | Alarm | 1st Planetary Stage | 2021-07-10 |  | 6 |  | Monitor | 2922294 | Closed | Closed |  |  |  | no damage found in borescope, 7/22 - signal reduced to normal levels in July, 8/9 - damage progression is unclear, no debris detected, S3 HSS GS raceways, 9/20 - 10g impacts, S1 Ring fault harmonics, monitor for debris generation, 11/4 - reduce to cat 2, 12/15 - 4mg debris detected, reduce to cat 1 | Case In Progress | -44387
Santa Rita East | Resolved | 94 |  | Instrumentation | 1st Planetary Stage | 2022-06-30 |  |  | Check sensor mounting | CMSTRBLSHOOT | 2953042 | Closed | Closed |  | 2022-07-07 |  |  |  | 7
Santa Rita East | Active | 94 | HSS DnWind/DnWind Rear Bearing Issue | Warning | Helical High Speed Stage | 2023-04-28 |  | 3 | 9/19/23 - Borescope did not find damages, continue to monitor via CMS and oil particle data. 4/28/23 - Recommend full gearbox borescope with a focus on the high speed stage within 6 months from 4/28/23. | Monitor | 3117990 | Closed | Closed |  |  |  |  | False Positive | -45044
Bethel | Resolved | 95 |  | Warning | Helical High Speed Stage | 2021-02-19 |  | 6 |  | Monitor | [5 empty] | 2023-01-25 |  | Case In Progress | -44246
Santa Rita East | Resolved | 95 |  | Change 1 | 2nd Planetary Stage | 2022-09-15 |  | 6 |  | Monitor | [5 empty] | 9/20 - potential S2 bearing damage, harmonics at higher frequencies, 12/15 - 12mg detected, likely S2 PC BRG GS ORBP, well pronounced harmonics in high res spectrum, |  |  | -44819
Santa Rita East | Resolved | 95 |  | Instrumentation | 2nd Planetary Stage | 2022-04-07 |  |  | Open Sensor Wiring | CMSTRBLSHOOT | 2909943 | Closed | Closed |  | 2022-05-04 | 4/25 - sensor 2 replaced, sensor 2 still showing open wiring |  |  | 27
Santa Rita East | Active | 95 | SKF Main Bearing Issue | Case Tracking | Main Bearing | 2022-04-19 |  | 1 |  | Final Report Needed | [6 empty] | 4/19 - ge alert requested derate and inspection, no data past 4/7, tower DNR for main bearing | Defect Confirmed - Repair Complete | -44670
Maverick | Active | 95 | NTN Main Bearing BS2X Signature | Sweep | Main Bearing | 2024-04-29 |  | 2 | 5/21/24 - Turbine has faulted and was placed into DNR. 4/30/24 - Turbine derated to 50%. 4/29/24 - Recommend main bearing borescope + grease purge within 2 weeks from 4/29/24. Turbine to be derated to 50%. | Final Report Needed | 3343366 | Closed | Closed |  | 2024-05-19 |  |  | Defect Confirmed - Repair Complete | 20
Plymouth | Active | 95 | 1st Stage Planetary Bearing Issue | Warning | 1st Planetary Stage | 2024-09-23 |  | 2 | 9/23/24 - Please borescope entire gearbox with focus on the 1st stage planetary bearings within 1 month from 9/23/24. | Longterm Watchlist | 3434992 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45558
Plymouth | Active | 95 | Potential Timken Main Bearing Issue | Sweep | Main Bearing | 2023-10-05 |  | 1 | 1/18/24 - Damage progression seen, recommending secondary borescope. 12/11/23 - Found indentations and spalling on inner + outer races, roller damage also present. Warranty Claim submitted. 10/5/23 - Awaiting EOW borescope | Final Report Needed | 3256341 | Closed | Closed |  | 2024-04-15 |  |  | Defect Confirmed - Repair Complete | 193
Deuel Harvest | Active | 95 | S1 Planet Bearing | Alarm | 1st Planetary Stage | 2023-02-09 |  | 2 | 8/3/23 - Borescope shows early spalling on S1 planetary bearings, estimated failure Q3-Q4 2024. Continuing to monitor CMS for damage progression. | Repair Pending | 3164754 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -44966
Bethel | Resolved | 96 | 1st Planetary Gearing Failure/Split Gearbox | Warning | 1st Planetary Stage | 2023-10-03 |  | 1 | 10/3/23 - Recommend shutting turbine down if it is not already. Also recommend borescoping gearbox at next possible opportunity. However, gearbox is likely split already, expect oil spillage. | CMSGBXBORE | 3200849 | Closed | Closed |  | 2023-12-27 |  |  | Miss - Defect Not Caught | 85
Deuel Harvest | Resolved | 96 |  | Warning | 2nd Planetary Stage | 2022-02-26 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44618
Santa Rita East | Resolved | 96 |  | Change 1 | Helical High Speed Stage | 2022-08-27 |  | 6 |  | Monitor | [5 empty] | 9/20 - early HSS bearing damage, 12/15 - 311mg debris detected, |  |  | -44800
Santa Rita East | Active | 96 | Main Bearing BS2X | Sweep | Main Bearing | 2023-03-01 |  | 1 | CMS main bearing signatures are increasing. Please shut down turbine until repair can be completed, turbine will be added to DNR list. | Final Report Needed | 3088488 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -44986
Plymouth | Resolved | 96 |  | Instrumentation | CMS Monitor | 2022-06-03 |  |  | Replace 60M100 monitor | CMSTRBLSHOOT | 2941639 | Cancelled | Cancelled | [5 empty] | -44715
Plymouth | Resolved | 96 |  | Instrumentation | Keyphasor | 2022-08-11 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988841 | Cancelled | Cancelled | [5 empty] | -44784
Maverick | Resolved | 96 | Main Bearing Accelerometer Open Circuit | Instrumentation | Main Bearing | 2022-01-27 |  | 4 | Main Bearing accelerometer is reading an open circuit, recommend inspecting sensor harness and wirings. | CMSTRBLSHOOT | 3073245 | Closed | Closed |  | 2023-07-22 |  |  | Defect Confirmed - Repair Complete | 541
Santa Rita East | Resolved | 97 |  | Warning | Generator Outboard | 2022-07-13 |  | 6 |  | Monitor | [5 empty] | 7/22 - HSS rotational warning for both gen bearings in mode 1, 12/15 - 390 mg debris detected, S3 Direct warning event, |  | Case In Progress | -44755
Santa Rita East | Active | 97 | 1st Planetary Stage Bearing Issue | Warning | 1st Planetary Stage | 2023-04-04 |  | 1 | 3/25/24 - Multiple planetary teeth fractures, turbine to be shut down until replacement is made. 3/15/24 - Damage has progressed to a 2nd planetary stage gearing failure, recommending secondary borescope. Derated turbine to 50%. 4/4/23 - Early stage pitting on the S1 RS planet bearings, TA appear slightly pulled out. Added TA inspection to PM schedule and gearbox to the MCFL. Estimate gearbox failure in 12-18 months from 5/1/23. | Final Report Needed | 3317740 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45020
Santa Rita East | Active | 97 | Main Bearing Outer Race Issue | Warning | Main Bearing | 2024-01-22 |  | 3 | 8/23/24 - Sent out for reborescope. 2/27/24 - Borescope did not find much damage, continue to monitor. 1/22/24 - Recommend main bearing borescope with 2 months from 1/22/24. | CMSMBBORE | 3408684 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45313
Plymouth | Resolved | 97 | High Speed Stage Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2022-06-03 |  | 5 | Check sensor wiring | CMSTRBLSHOOT | 2941634 | Closed | Closed |  | 2023-08-31 |  |  | True Positive | 454
Deuel Harvest | Resolved | 98 |  | Warning | Helical High Speed Stage | 2022-11-03 |  | 1 |  | EOW Claim | [5 empty] | 11/9 - EOW scope found heavy indenting and spalling on S1 and S2 PS BRGs, likely indicating catastrophic planet bearing damage that is inaccessible by borescope, CMS indicates potential damage to the S1 PS BRG, warranty claimed placed, expecting GE to deny it, monitor for failure, 11/28 - checked |  |  | -44868
Bethel | Resolved | 98 | Gen Bearing Damage | Warning | Generator Outboard | 2023-01-26 |  | 3 | Add grease to both gen bearings | CMSGENB | 3072477 | Closed | Closed |  | 2023-04-24 |  |  | Defect Confirmed - Repair Complete | 88
Bethel | Resolved | 99 |  | Alarm | Generator Outboard | 2021-10-17 |  | 3 |  | Monitor | [5 empty] | 2023-01-25 |  | Case In Progress | -44486
Deuel Harvest | Resolved | 99 |  | Warning | Helical High Speed Stage | 2021-11-16 |  | 1 |  | Monitor | [7 empty] | Case In Progress | -44516
Santa Rita East | Resolved | 99 |  | Warning | 1st Planetary Stage | 2022-04-28 |  | 5 |  | Monitor | [5 empty] | 6/6 - stage 1 direct barely hit alarm setpoint in April 2021, S1 PC BRG GS roller damage, monitor for additional increase to alarm, 7/22 - signal has reduced significantly, reducing to cat 2, envelope indicates S1 PS BRG damage, 9/20 - recent increase in stage 1 direct, increase in debris generation, 10/12 - additional peak to alarm, 11/4 - trend remains elevated, 9 mg debris detected |  | Case In Progress | -44679
Santa Rita East | Resolved | 99 |  | Warning | Generator Outboard | 2021-12-14 |  | 5 |  | Monitor | 2935237 | Closed | Closed |  |  | 5/18 - gen bearing check found audible "squeak" while running. Added half tube of Kluber to both bearings, brush box looks to have excessive carbon dust, loop Jose in once he's back, 6/6 - added grease reduced vibration temporarily, now hitting warning setpoint again. Monitor for additional increase, 7/22 - spike near alarm threshold, 8/9 - 10g impacts in the timebase, 8/31 - reduce to cat 2, 9/20 - decrease to normal levels, 12/15 - increasing trend at warning setpoint | 12/28 - Shows signs of damage to the outer race of the NDE gen bearing, amplitudes are still low, monitor for failure, 1.5g peak at ORBP frequency in the FFT, 10-20g peaks in timebase, 4/25 - recent progression on NDE bearing, continue to monitor, prep for replacement, 5/17 - max vibration just below the alarm setpoint, vibration has subsided. Recommending gen bearing check, | Case In Progress | -44544
Santa Rita East | Resolved | 99 | Generator Outboard ORBP | Alarm | Generator Outboard | 2022-02-09 |  | 3 |  | CMSGENB | 3079959 | Closed | Closed | [5 empty] | -44601
Bethel | Resolved | 99 | Gen Outboard Bearing Damage | Case Tracking | Generator Outboard | 2023-01-25 | 2024-06-01 | 3 | 2/28/24 - Replace generator outboard bearing 1/8/24 - Continue to monitor. 1/25/23 - Add grease to both gen bearings | Monitor | 3072204 | Closed | Closed |  | 2024-06-08 |  |  | Defect Confirmed - Repair Complete | 500
Santa Rita East | Active | 99 | Generator Outboard ORBP | Warning | Generator Outboard | 2023-10-04 |  | 3 | 10/11/23 - Grease added, amplitudes have decreased. CMS will continue to monitor for trend increases. 10/4/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings | Monitor | 3201708 | Closed | CLosed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45203
Bethel | Resolved | 100 | Gen Bearing Failure | Case Tracking | Generator Outboard | 2023-01-25 |  | 1 | Replace gen bearings | CMSGENB | 3072205 | Closed | Closed |  | 2023-02-28 |  |  | Defect Confirmed - Repair Complete | 34
Santa Rita East | Resolved | 100 |  | Change 1 | Helical High Speed Stage | 2022-02-01 |  | 6 |  | Monitor | [5 empty] | 6/6 - stage 3 FFT indicates damage to HSS RS raceways, 6/30 - limited progression, 8/9 - HSS GS IRBP with pinion fault harmonics |  | Case In Progress | -44593
Maverick | Active | 100 | Potential Main Bearing Issue | Sweep | Main Bearing | 2023-12-05 |  | 1 | 1/17/24 - Secondary borescope scheduled to determine derate effectiveness. 12/11/23 - Borescope found heavy damages to outer race and cage, direct levels continue to increase. Turbine DNR'd until replacement is made. 12/5/23 - Recommend main bearing borescope within 1 week from 12/5/23. | Final Report Needed | 3255288 | Closed | Closed |  |  |  |  | Case In Progress | -45265
Deuel Harvest | Resolved | 101 |  | Instrumentation | CMS Monitor | 2022-08-10 |  |  | Reboot 60M100, check LED panel for fault indication | CMSTRBLSHOOT | 2988353 | Cancelled | Cancelled |  | 2022-09-21 |  | 9/21 - low voltage from PMT |  | 42
Bethel | Active | 101 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-02-16 |  | 5 | 10/30/23 -Generator speed signal (Keyphasor) is not communicating with CMS monitor. Check gen encoder wiring and orientation, check PEM and connection to KPH. Bring a spare PEM to attempt PEM swap if needed 2/16/23 - Gap = -9V | CMSTRBLSHOOT | 3127042 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -44973
Plymouth | Resolved | 101 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-11 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2988842 | Cancelled | Cancelled |  |  | 8/29 - keyphasor is ok |  |  | -44784
Bethel | Resolved | 102 | Gen Outboard Bearing Damage | Warning | Generator Outboard | 2023-01-26 |  | 3 | 7/24/23 - Grease added, CMS will continue to monitor for progression. | Monitor | 3072478 | Closed | Closed |  | 2023-10-22 |  |  | Defect Confirmed - Repair Complete | 269
Santa Rita East | Resolved | 102 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-04-26 |  | 3 | CMS monitor is not receiving a speed signal from the generator encoder. Please inspect PEM and encoder using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3116891 | Closed | Closed |  |  |  |  | Case In Progress | -45042
Santa Rita East | Resolved | 102 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-12-04 |  | 3 | 12/4/23 - CMS monitor is not receiving a speed signal from keyphasor/PEM/Generator encoder circuit. Keyphasor circuit currently reading 4.1V. Please ensure input is on KPH2 and ensure PEM is wired correctly. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3233074 | Closed | Ready to Schedule |  | 2023-12-19 |  |  | Defect Confirmed - Repair Complete | 15
Maverick | Active | 102 | Main Bearing Outer Race Issue | Sweep | Main Bearing | 2024-02-29 |  | 2 | 3/6/24 - Turbine derated to 850kW. 2/29/24 - Recommend main bearing borescope at next opportunity, please upload results to HUVR. | Final Report Needed | 3310444 | Closed | Closed |  | 2024-04-09 |  |  | Defect Confirmed - Repair Complete | 40
Deuel Harvest | Active | 102 | Stage 2 Planertary OBRP/IRBP | Alarm | 2nd Planetary Stage | 2024-11-13 |  | 5 | 11/13/24 - CMS indicates potential secondary stage bearing ORBP/IRBP | Monitor | [7 empty] | Case In Progress | -45609
Plymouth | Resolved | 102 | S1 Planetary Bearing Issue | Alarm | 1st Planetary Stage | 2022-07-11 |  | 1 |  | Repair Pending | 3024818 | Closed | Closed |  |  |  |  | True Positive | -44753
Santa Rita East | Resolved | 103 |  | Warning | Generator Inboard | 2022-09-25 |  | 5 |  | Monitor | [5 empty] | 11/4 - early DE gen bearing damage |  |  | -44829
Santa Rita East | Resolved | 103 |  | Instrumentation | 1st Planetary Stage | 2022-04-07 |  |  | Open Sensor Wiring | CMSTRBLSHOOT | 2909944 | Closed | Closed |  | 2022-04-15 | 4/25 - work order closed, sensor 1 is still showing open wiring |  |  | 8
Maverick | Active | 103 | NTN Main Bearing BS2X Signature | Sweep | Main Bearing | 2024-02-06 |  | 1 | 4/15/24 - Turbine shutdown and DNR'd. 4/5/24 - Turbine derated to 850kW (30%). 2/9/24 - Turbine derated to 40%. 2/6/24 - Recommend main bearing borescope and thrust derate at next possible opportunity. | Final Report Needed | 3268250 | Closed | Closed |  | 2024-04-16 |  |  | Defect Confirmed - Repair Complete | 70
Plymouth | Active | 103 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2024-10-01 |  | 3 | 10/1/24 - Not receiving data via Onyx Insight, please investigate if monitor is netcom or not receiving a speed signal. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3440469 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45566
Plymouth | Active | 103 | NTN Main Bearing Outer Race Damage | Warning | Main Bearing | 2023-08-03 | 2024-11-17 | 2 | 9/11/23 - Surface damage present on MB inner race, continue to monitor via CMS. 8/3/23 - Recommend main bearing borescope at next opportunity. | Longterm Watchlist | 3169017 | Closed | Closed |  |  |  |  | Case In Progress | -45141
Deuel Harvest | Resolved | 104 |  | Warning | 2nd Planetary Stage | 2021-08-22 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44430
Thunderhead | Active | 104 | Potential S1 bearing issue | Sweep | 1st Planetary Stage | 2024-09-11 |  | 5 | 9/11/24 - CMS shows potential S1 bearing issue continue to monitor for progression. | Monitor | [7 empty] | Case In Progress | -45546
Number 3 | Active | 105 | S1 Planet Carrier Bearing Issue | GE Alert | 1st Planetary Stage | 2024-02-23 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -45345
Santa Rita East | Active | 105 | Potential Plaentary Gearing issue | Alarm | 1st Planetary Stage | 2024-11-27 |  | 1 | 11/27/24 - CMS indicates potential gearing issue. Engineering recommends full gearbox borescope within 72 hours, or as soon as possible from 11/27/24 with focus on the 1st planetary stage. Also recommend derating turbine to 50% until inspection can be performed. | CMSGBXBORE | 3469943 |  | Ready to Schedule |  |  |  |  | False Positive | -45623
Santa Rita East | Resolved | 106 |  | Warning | 1st Planetary Stage | 2022-10-13 |  | 6 |  | Monitor | [5 empty] | 11/4 - recent increase in S1 Direct, potential early bearing damage |  |  | -44847
Santa Rita East | Resolved | 107 |  | Warning | 1st Planetary Stage | 2022-02-19 |  | 6 |  | Monitor | [5 empty] | 2/21 - stage 1 direct shows early trend towards increasing amplitude, FFT shows shaft harmonics carrying sidebands, 4/7 - increase to warning setpoint for stage 2 direct signal, potential stage 2 bearing issue, 4/25 - turbine has been offline for main bearing failure, limited operation on 4/15 shows stage 1 carrier damage, 6/30 - unclear if gearbox borescope was performed, stage 1 envelope shows concerning ring fault harmonics, stage 2 indicates PS BRG damage, 7/22 - S1 direct has reduced through July, 8/31 - reduce to cat 2, 12/15 - reduce to cat 1 |  | Case In Progress | -44611
Santa Rita East | Resolved | 107 |  | Alarm | Main Bearing | 2021-12-23 |  | 1 |  | Replacement | 2691189 | Closed | Closed |  | 2022-06-30 | 1/31 - MCFL entry created, monitor for failure |  | True Positive - Other Method Detected | 189
Bethel | Active | 107 | Generator Outboard IRBP | Warning | Generator Outboard | 2023-09-18 | 2024-09-14 | 6 | 9/18/23 - Awaiting direct increase. | Monitor | [7 empty] | Case In Progress | -45187
Deuel Harvest | Resolved | 108 | Generator Inboard Accelerometer Open Circuit | Instrumentation | Generator Inboard | 2023-05-25 |  | 5 | Generator Inboard accelerometer is reading an open circuit, please inspect wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | 3132468 | Closed | Closed |  |  |  |  | Case In Progress | -45071
Santa Rita East | Resolved | 108 |  | Warning | 1st Planetary Stage | 2022-05-28 |  | 1 |  | Monitor | [5 empty] | 6/30 - potential damage to S2 PC BRG GS rollers, 9/20 - recent progression, 2,340mg debris detected, recent progression, elevate to cat 3, 10/12 - S1 bearing fault harmoincs at high frequencies, 11/4 - recent spikes in GFED 2,636 mg debris detected, abnormal peak at 268.75X, 12/15 - continued progression |  | Case In Progress | -44709
Santa Rita East | Resolved | 108 |  | Alarm | Generator Outboard | 2022-02-19 |  | 5 |  | Monitor | [5 empty] | 2/21 - peak at 1X shaft speed, 4/25 - FFT indicates damage to HSS bearing, likely, 8/9 - DE gen bearing Direct now hitting warning setpoint, occasional 15-30g impacts in the timebase, may be abnormal damage profile, 9/20 - increase to cat 2 |  | Case In Progress | -44611
Santa Rita East | Resolved | 108 |  | Alarm | Main Bearing | 2021-10-23 |  | 1 |  | Replace | [5 empty] | 10/28 - TADS and MBROC, turbine shutdown for full main bearing replacement |  | True Positive | -44492
Santa Rita East | Resolved | 108 | Main Bearing Sensor Issue | Instrumentation | Main Bearing | 2023-01-18 |  | 5 | Main bearing sensor is currently reading an open circuit, please inspect wiring and connections. Replace sensor if needed. Please reach out to Andrew Barndt if you have any questions. | CMSTRBLSHOOT | 3069383 | Closed | Closed |  | 2023-01-19 |  |  | Defect Confirmed - Repair Complete | 1
Santa Rita East | Resolved | 108 | HSS Rotational | Alarm | Other | 2023-01-30 |  | 2 | Please inspect generator and HSS coupler for possible misalignment. Please also perform an auditory and visual inspection of the generator bearings: Contact abarndt@invenergy.com for support | CMSGENB | 3073724 | Closed | Closed |  | 2023-07-12 |  |  | Defect Confirmed - Repair Complete | 163
Bethel | Active | 108 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2023-09-27 |  | 2 | 9/27/23 - CMS monitor appears netcom, please inspect that CMS monitor is powered and ethernet cable is plugged into port A. | CMSTRBLSHOOT | 3197848 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45196
Bethel | Active | 108 | Main Bearing ORBP/IRBP | Case Tracking | Main Bearing | 2023-01-25 |  | 1 | 9/27/23 - Heavy main bearing outer race damage found, turbine to be DNR'd until replacement can be made | Final Report Needed | [5 empty] | report in HUVR, purge completed last week, Q1 2024 expected failure |  | Defect Confirmed - Awaiting Repair | -44951
Santa Rita East | Resolved | 108 | ZF S2 Carrier Bearing Issue | Sweep | 2nd Planetary Stage | 2023-02-09 |  | 2 | 2/9/23 - Moderate damage to the S2 planet carrier bearings, recommend gearbox replacement by end of 2023. Added to the MCFL, CMS will continue to monitor for damage progression. | Longterm Watchlist | 3080003 | Closed | Closed |  | 2024-08-21 |  |  | Defect Confirmed - Awaiting Repair | 559
Bethel | Resolved | 109 |  | Warning | Helical High Speed Stage | 2021-02-24 |  | 6 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - Direct signal spikes below the warning setpoint. Gear/pinion fault sidebands near 2X GMF, inspect when signal hits warning |  | Case In Progress | 700
Deuel Harvest | Resolved | 109 |  | Warning | Main Bearing | 2022-06-25 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44737
Santa Rita East | Resolved | 109 |  | Warning | 1st Planetary Stage | 2022-09-16 |  | 1 |  | Monitor | [5 empty] | 9/20 - sudden increase in S1 direct vibration on 9/16, ring fault temporarily excited, otherwise limited damage indictors, 17mg debris detected with recent progression, borescope when alarm is hit or damage is apparent, 10/12 - S3 Pinion fault sidebands, 11/4 - 18 mg debris detected, trend remains elevated, 12/15 - limited progression |  |  | -44820
Santa Rita East | Resolved | 109 |  | Case Tracking | Main Bearing | 2022-04-22 |  | 1 |  | Monitor | [5 empty] | 4/22 - no data past 4/7, direct waveform shows main bearing progression at low amplitude, 10/12 - temps are ok |  | Case In Progress | -44673
Santa Rita East | Resolved | 110 |  | Change 1 | Helical High Speed Stage | 2022-08-31 |  | 1 |  | Monitor | [5 empty] | 9/20 - HSS RS IRBP damage, 10/12 - additional DEI Strucutral change events for all three stages, likely HSS bearing and pinion fault damage, 12/15 - limite progression, 19mg detected, 1/6 - MB spectrum shows S1 planet fault, borescope soon |  | Case In Progress | -44804
Santa Rita East | Resolved | 110 |  | GE Alert | Main Bearing | 2022-05-31 |  | 1 |  | Pending Replacement |  |  |  |  | 2022-08-27 |  |  | True Positive - Other Method | 88
Bethel | Resolved | 110 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-02-20 |  | 5 | Check keyphasor harness for open/short, otherwise replace transducer | CMSTRBLSHOOT | 3085515 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Repair Complete | -44977
Bethel | Active | 110 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-05-15 |  | 5 | 5/15/24 - Keyphasor is not communicating with monitor and Gap is at -9. | CMSTRBLSHOOT | 3351391 | Closed | Ready to Schedule |  |  |  |  | Case In Progress
Santa Rita East | Active | 110 | ZF S1 Planetary Bearing Issue | Alarm | 1st Planetary Stage | 2023-01-25 |  | 2 | 10/5/23 - Recommend derating to 50% until repair can be made. 8/31/23 - Heavy damage found on S1 +2 planetary bearings, debris damage seen on S1 planetary gearing as well. Recommend gearbox replacement by Q4 2023. 1/25/23 - S1 Planet Bearing issue, recommend borescope of entire gearbox with focus on 1st planetary stage. | Final Report Needed | 3072034 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -44951
Santa Rita East | Resolved | 111 |  | Warning | 1st Planetary Stage | 2021-11-09 |  | 5 |  | Monitor | [5 empty] | 12/2 - continue to monitor, 6/6 - potential S1 PC BRG GS rollers, 12/15 - 191mg debris detected, |  | Case In Progress | -44509
Santa Rita East | Resolved | 112 |  | Alarm | Main Bearing | 2021-03-29 |  | 1 |  | monitor after instrumentation is fixed |  |  |  |  | 2021-10-28 | Instrumentation resolved, continue to monitor |  | False Positive - Sensor Issue | 213
Santa Rita East | Resolved | 113 |  | Warning | 1st Planetary Stage | 2022-10-21 |  | 6 |  | Monitor | [5 empty] | 11/4 - spike above warning, low concern |  |  | -44855
Bethel | Active | 113 | Potential Main Bearing Issue | Sweep | Main Bearing | 2023-10-05 |  | 2 | 64 | CMSMBBORE | 3202388 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45204
Bethel | Active | 113 | Generator Outboard ORBP | Warning | Generator Outboard | 2023-09-18 | 2024-09-24 | 6 | 9/18/23 - Awaiting direct increase. | Monitor | [7 empty] | Case In Progress | -45187
Bethel | Resolved | 115 |  | Warning | Helical High Speed Stage | 2021-02-16 |  | 6 |  | Monitor |  |  |  |  | 2023-01-25 | 2/1 - Direct signal spikes below the warning setpoint. Gear/pinion fault sidebands near 2X GMF, inspect when signal hits warning |  | Case In Progress | 708
Bethel | Resolved | 115 | Generator Outboard ORBP | Alarm | Generator Outboard | 2023-06-19 |  | 3 | Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | CMSGENB | 3144097 | Closed | Closed |  | 2023-09-01 |  |  | Defect Confirmed - Repair Complete | 74
Santa Rita East | Resolved | 115 |  | Alarm | 1st Planetary Stage | 2022-04-06 |  | 1 |  | CMSGBXBORE | 2923282 | Closed | Closed |  | 2022-07-30 | 4/7 - sudden increase in Stage 1 Ser Planet Fault GFEd signal, FFT indicates damage to stage 1 carriers, 4/25 - new alarms in all stages, direct. Stage 1 ENV shows damage to stage 1 carrier GS, bearing fault harmonics and GMF are low. Stage 2 ENY indicates potential damage to stage 2 carriers (both), limited progression. Stage 3 direct peaks above alarm occasionally. Many alarms are concerning but the disposition isn't too compelling, recommending, 4/28 - gearbox failure, burned up HSIS bearing cover, gearbox is locked up, should've started derate conversation, tower offline, 8/9 - gearbox replaced, RTS 7/30 |  | True Positive | 115
Santa Rita East | Resolved | 115 |  | Warning | 1st Planetary Stage | 2021-01-12 |  | 1 | [6 empty] | 2022-01-31 | 12/14 - Bearing indents |  | True Positive | 384
Bethel | Resolved | 116 | Gen Bearing Failure | Case Tracking | Generator Outboard | 2023-01-25 |  | 1 | Replace gen bearings | CMSGENB | 3072207 | Closed | Closed |  | 2023-04-11 |  |  | Defect Confirmed - Repair Complete | 76
Bethel | Active | 116 | HSS Bearing + Pinion Damage | Case Tracking | Helical High Speed Stage | 2023-01-25 |  | 2 | Check HSS bearing for damage | CMSHSS | 3080379 | Closed | Closed |  |  |  |  | Case In Progress | -44951
Santa Rita East | Resolved | 117 |  | Change 1 | 1st Planetary Stage | 2022-04-24 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44675
Santa Rita East | Resolved | 117 |  | Case Tracking | Main Bearing | 2021-10-12 |  | 1 |  | Repair Pending | 2631342 | Closed | Closed |  |  | 2022-04-08 |  | True Positive | -44481
Bethel | Resolved | 118 | Elevated NDE gen bearing vibration | Alarm | Generator Outboard | 2023-04-20 |  | 5 | Add grease to both gen bearings | CMSGENB | 3115253 | Closed | Closed |  | 2023-09-11 |  |  | Defect Confirmed - Repair Complete | 144
Santa Rita East | Active | 118 | Main Bearing BS2X | Sweep | Main Bearing | 2023-03-10 |  | 1 | CMS signature has progressed, turbine should remain down until main bearing replacement occurs. DNR'd | Final Report Needed | 3096715 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -44995
Bethel | Resolved | 119 | Main Bearing Raceway Damage | Case Tracking | Main Bearing | 2023-02-03 |  | 1 | (DNR) Borescope the main bearing, 50% derate, failed main bearing | Final Report Needed | 3096736 | Closed | Closed |  | 2023-06-12 | CMSMB |  | Defect Confirmed - Repair Complete | 129
Santa Rita East | Resolved | 119 |  | Warning | Generator Outboard | 2021-10-19 |  | 6 |  | Monitor | [7 empty] | Case In Progress | -44488
Bethel | Active | 119 | 1st Stage Planetary Gearing Issue | Warning | 1st Planetary Stage | 2024-04-23 |  | 1 | 5/7/24 - This turbine is now showing signs that the planetary damage has progressed, recommend a secondary borescope on this gearbox at next possible opportunity. 5/2/24 - Returned to full power, continue to monitor. 4/25/24 - Possible secondary damages found, no primary sources. Going to re-evaluate in a week. 4/23/23 - Please perform a full gearbox borescope with focus on the 1st planetary stage at next possible opportunity. Turbine to be derate to 50% | Final Report Needed | 3347673 | Closed | Ready to Schedule |  | 2024-05-09 |  |  | Defect Confirmed - Repair Complete | 16
Santa Rita East | Resolved | 120 |  | Alarm | 1st Planetary Stage | 2022-06-14 |  | 1 |  | CMSGBXBORE | 2947723 | Closed | Closed |  |  | 8/11/22 |  | True Positive | -44726
Santa Rita East | Active | 120 | Main Bearing Accelerometer | Instrumentation | Main Bearing | 2024-10-02 |  | 4 | 10/2/24 -Main bearing sensor is currently reading an open circuit, please investigate wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | 3441263 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45567
Santa Rita East | Active | 120 | 2nd Planetary Stage Carrier Bearing Issue | Sweep | 2nd Planetary Stage | 2023-09-28 |  | 3 | 1/3/24 - Borescope found early spalling seen on 2nd planetary stage bearings, est. replacement Q1-Q2 2025. 9/28/23 - Recommend full gearbox borescope with focus on 2nd planetary stage bearings within 2 months from 9/28/23. | Longterm Watchlist | 3198018 | Closed | Closed |  | 2024-09-15 |  |  | Defect Confirmed - Awaiting Repair | 353
Beech Ridge 2 | Resolved | 202 |  | EOW | Main Bearing | 2022-03-03 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44623
Beech Ridge 2 | Resolved | 203 |  | Warning | Helical High Speed Stage | 2022-05-31 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44712
Beech Ridge 2 | Resolved | 204 |  | EOW | Main Bearing | 2022-03-01 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44621
Beech Ridge 2 | Resolved | 204 | Main Bearing Accelerometer Open Circuit | Instrumentation | Main Bearing | 2024-09-12 |  | 5 | 9/12/24 - Main bearing sensor is currently reading an open circuit. Please investigate wirings and connections, replace sensor if needed. Contact abarndt@invenergy.com for troubleshooting support. | CMSTRBLSHOOT | 3426605 | Closed | Ready to Schedule |  | 2024-09-16 |  |  | Defect Confirmed - Repair Complete | 4
Beech Ridge 2 | Resolved | 205 | Main Bearing Accelerometer Open Circuit | Instrumentation | Main Bearing | 2023-12-18 |  | 3 | 12/18/23 - Main bearing sensor is currently reading an open circuit. Please investigate wirings and connections, replace sensor if needed. Contact abarndt@invenergy.com for troubleshooting support. | CMSTRBLSHOOT | 3244247 | Closed | Ready to Schedule |  | 2024-09-16 |  |  | Defect Confirmed - Repair Complete | 273
Beech Ridge 2 | Resolved | 205 |  | EOW | Main Bearing | 2022-02-23 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44615
Beech Ridge 2 | Resolved | 206 |  | Instrumentation | 1st Planetary Stage | 2022-05-20 |  |  | Open sensor wiring | CMSTRBLSHOOT | 2936159 | Closed | Closed |  | 2022-06-24 |  |  | True Positive | 35
Beech Ridge 2 | Resolved | 206 |  | EOW | Main Bearing | 2022-03-18 |  | 1 |  | DNR | [7 empty] | Case In Progress | -44638
Beech Ridge 2 | Resolved | 207 |  | EOW | Main Bearing | 2022-03-18 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44638
Beech Ridge 2 | Resolved | 208 |  | EOW | Main Bearing | 2022-02-03 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44595
Beech Ridge 2 | Resolved | 208 |  | Warning | Main Bearing | 2021-08-17 |  | 6 | [7 empty] | same warning 1/23/21, 11/28/20 |  | False Positive - No Inspection | -44425
Beech Ridge 2 | Active | 208 | 2nd Planetary Stage Accelerometer Issue | Instrumentation | 2nd Planetary Stage | 2024-06-27 |  | 5 | 6/27/24 - ​2nd Planetary stage sensor is giving erroneous readings, please replace sensor. | CMSTRBLSHOOT | 3373714 | Ready to Schedule | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair
Beech Ridge 2 | Active | 208 | SKF Main Bearing Issue | Sweep | Main Bearing | 2023-10-05 |  | 6 | 10/10/23 - Signature appears to be from extended downtime, continue to monitor. 10/5/23 - Recommend thrust derating and performing a borescope of the main bearing at the next possible opportunity. | Monitor | 3202006 | Closed | Closed |  |  |  |  | Case In Progress | -45204
Beech Ridge 2 | Resolved | 209 | Main Bearing Accelerometer Open Circuit | Instrumentation | Main Bearing | 2023-05-22 |  | 5 | ​Main bearing sensor is currently reading an open circuit, please inspect wiring and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3130381 | Closed | Closed |  | 2023-11-22 |  |  | Defect Confirmed - Repair Complete | 184
Beech Ridge 2 | Resolved | 209 |  | EOW | Main Bearing | 2022-03-04 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44624
Beech Ridge 2 | Resolved | 210 |  | EOW | Main Bearing | 2022-03-23 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44643
Beech Ridge 2 | Resolved | 211 |  | EOW | Main Bearing | 2022-03-02 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44622
Beech Ridge 2 | Active | 211 | Main Bearing Sensor Issue | Alarm | Main Bearing | 2024-05-14 |  | 5 | 5/14/24 - CMS shows main bearing bias voltage at -22.76. | CMSTRBLSHOOT | 3350892 | Scheduled | Ready to Schedule |  |  |  |  | Case In Progress | -45426
Beech Ridge 2 | Resolved | 212 |  | EOW | Main Bearing | 2022-02-03 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44595
Beech Ridge 2 | Resolved | 213 |  | EOW | Main Bearing | 2022-02-22 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44614
Beech Ridge 2 | Resolved | 213 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2024-01-09 |  | 3 | 1/9/24 - Please ensure communication cabling is plugged into Port A and ensure that CMS monitor is powered. | CMSTRBLSHOOT | 3251727 | Closed | Closed |  | 2024-03-04 |  |  | Defect Confirmed - Repair Complete | 55
Beech Ridge 2 | Resolved | 214 | SKF Main Bearing Issue | Sweep | Main Bearing | 2023-02-14 |  | 1 | Main Bearing borescope found excessive damage, turbine is shutdown and placed on DNR list until replacement can be made | Final Report Needed | 3083678 | Closed | Closed |  | 2023-09-02 |  |  | Defect Confirmed - Repair Complete | 200
Beech Ridge 2 | Resolved | 215 |  | EOW | Main Bearing | 2022-02-09 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44601
Beech Ridge 2 | Resolved | 216 |  | EOW | Main Bearing | 2022-02-22 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44614
Beech Ridge 2 | Resolved | 216 | Main Bearing Direct Rising | Warning | Main Bearing | 2023-10-30 | 2024-03-01 | 6 | 10/30/23 - Main bearing direct rising, no signature. Continue to monitor. | Monitor | [7 empty] | Case In Progress | -45229
Beech Ridge 2 | Resolved | 217 |  | EOW | Main Bearing | 2022-04-04 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44655
Beech Ridge 2 | Resolved | 219 |  | EOW | Main Bearing | 2022-03-28 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44648
Beech Ridge 2 | Resolved | 220 |  | EOW | Main Bearing | 2022-04-14 |  | 1 |  | Longterm Watchlist | [7 empty] | Case In Progress | -44665
Bishop Hill 3 | Resolved | 301 | Generator Inboard /IRBP | Warning | Generator Inboard | 2023-10-31 | 2024-05-21 | 3 | 10/31/23 - Signature is showing signs of possible ORBP/IRBP issue in generator inboard, work order made for grease check 11/1/23 | Monitor | 3217711 | Closed | Closed |  |  |  |  | False Positive | -45230
Bishop Hill 3 | Resolved | 301 | Monitor Data Collection Issue | Instrumentation | CMS Monitor | 2023-04-19 |  | 5 | Power cycle 60M100 and flip on/off switch to restart | CMSTRBLSHOOT | 3114614 | Closed | Closed |  | 2023-07-01 |  |  | Defect Confirmed - Repair Complete | 73
Bishop Hill 3 | Resolved | 303 |  | Instrumentation | Keyphasor | 2022-02-09 |  | 6 | Replace transducer | CMSTRBLSHOOT | 2800831 |  | Closed |  | 2023-01-18 | find keyphasor part number, 3/2 - swapped in new tachometer, didn’t clear bently fault. Then tower faulted on tachometer and replaced original tachometer, faulted again, rebooted to clear fault. Keyphasor issue persists, 4/15 - provided keyphasor troubleshoot guide< 1/17/23 - gap voltage = 4.13V, check wiring in terminal X8 |  | True Positive | 343
Bishop Hill 3 | Resolved | 303 |  | Warning | Helical High Speed Stage | 2022-01-04 |  | 6 |  | Monitor | [5 empty] | 2023-01-11 |  | False Positive - Sensor Issue | -44565
Bishop Hill 3 | Resolved | 304 | Main Bearing Cracked Inner Race | Warning | Main Bearing | 2023-01-19 | 2024-05-20 | 1 | 4/21/24 - Replacement complete. 1/19/23 - Cracked inner raceway, thrust derate. | Final Report Needed | 3071322 | Closed | Closed |  |  | 2/2 - borescope found cracked inner race |  | Defect Confirmed - Repair Complete | -44945
Bishop Hill 3 | Active | 305 | Main Bearing Raceway Damage | Sweep | Main Bearing | 2023-03-08 |  | 3 | 3/8/23 - Borescope found banding and micropitting, continue to monitor. | Monitor | 3094862 | Closed | Closed |  |  |  |  | Case In Progress | -44993
Bishop Hill 3 | Resolved | 307 |  | Warning | Helical High Speed Stage | 2021-12-24 |  | 6 |  | Monitor | [5 empty] | 2023-01-11 |  | False Positive - Sensor Issue | -44554
Bishop Hill 3 | Active | 308 | S1 PS BRG Damage | EOW | 1st Planetary Stage | 2022-03-09 |  | 1 | Planetary bearing issue found via EOW inspections, continuing to monitor via CMS + Particle Counters | Longterm Watchlist | 3012924 | Closed | Closed | Q4 2024 |  | 3/2 - 29mg detected, slow progression |  | Defect Confirmed - Awaiting Repair | -44629
Bishop Hill 3 | Resolved | 312 | Potential S1 Sun Gear Issue | Warning | 1st Planetary Stage | 2023-08-18 | 2024-06-06 | 2 | 2/23/24 - depth of this spall is concerning for a gear experiencing such high loads, recomended derate to prevent tooth fracture from the sun pinion until replacement. 2/22/24- CMS shows progression of S1 Sun gearing defect. Sent out for full gearbox borescope and inspection. 8/30/23 -Denting indentations/early spalling seen on the S1 sun gear. Possible debris run over as well. Continue to monitor via CMS and particle counter data. 8/18/23 - Recommend full gearbox borescope with focus on 1st planetary stage within 24 hours. 2/22/24 - CMS indicates progression of defect, work order sent out to conduct borescope/inspection. | Longterm Watchlist | 3303954 | Closed | Closed | 2024-07-10 |  |  |  | Defect Confirmed - Repair Complete | -45156
Bishop Hill 3 | Resolved | 315 | Main Bearing Damage | Warning | Main Bearing | 2022-10-04 | 2024-07-05 | 3 | REPLACED. 8/18/23 - Spalling on OR at 6 o'clock (+clouding damage), Micropitting on IR, Roller indents; Borescoped due to temperature deviation; Replace in 3-6 months. 1/24/23 - Borescoped back in January 2023, some damage was shown but CMS indicated more than shown. CMS signature has increase and temps have begun to spike above neighbors at the beginning of this month/end of May. | Final Report Needed | 3052309 | Closed | Closed |  | 2023-11-08 | 2/2 - borescope found some roller indents and an area of micropitting continue to monitor |  | Defect Confirmed - Repair Complete | 400
Bishop Hill 3 | Resolved | 316 |  | Warning | Main Bearing | 2021-10-24 |  | 6 |  | Monitor | [7 empty] | False Negative | -44493
Bishop Hill 3 | Resolved | 317 | S2 Planet Ring/Planet Gear Issue | Alarm | 2nd Planetary Stage | 2024-04-22 | 2024-06-07 | 5 | 5/8/24 - Turbine currently under repair. Max power was set to 1265kW on 4/29/2024. | Repair Pending | 3343272 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -45404
Bishop Hill 3 | Resolved | 318 | HSS Pinion Cracked Tooth | Alarm | Helical High Speed Stage | 2023-03-31 | 2024-01-20 | 1 | 4/18/23 - Inspection found liberated HSS pinion tooth, 50% derate. Likely S2 Sun damage | Final Report Needed | 3106469 | Closed | Closed |  | 2023-10-28 |  |  | Defect Confirmed - Repair Complete | 211
Bishop Hill 3 | Resolved | 318 |  | Instrumentation | CMS Monitor | 2022-05-06 |  |  | Wait | [5 empty] | 2022-05-24 |  |  |  | 18
Bishop Hill 3 | Resolved | 318 |  | Instrumentation | CMS Monitor | 2022-03-18 | [8 empty] | 2022-04-15 |  |  |  | 28
Bishop Hill 3 | Resolved | 318 | CMS Monitor Netcomm | Instrumentation | CMS Monitor | 2023-03-08 |  | 5 | Check power supply to 60M100 and flip reset switch. Check CMS server for connection or contact CMS Team | [5 empty] | 2023-03-31 |  |  | Defect Confirmed - Repair Complete | 23
Bishop Hill 3 | Resolved | 320 | Potential S1 Planet Bearing Issue | EOW | 1st Planetary Stage | 2023-02-13 |  | 5 | 2/13/23 - Borescope in June 2022 showed signs of S1 planetary bearing damage, continue to monitor for progression. | Monitor | [5 empty] | 2/13/23 - Borescope in June 2022 showed signs of S1 planetary bearing damage, continue to monitor for progression. |  | Case In Progress | -44970
Bishop Hill 3 | Resolved | 321 | Gearbox Sensor 1 issue | Instrumentation | CMS Monitor | 2024-09-11 |  | 5 | 9/11/24 - Gearbox sensor 1 is show incorrect values for the Bias voltage, please conduct a cms troubleshoot. | CMSTRBLSHOOT | 3426087 | Closed | Closed |  |  |  |  | Case In Progress
Bishop Hill 3 | Resolved | 323 |  | Warning | 1st Planetary Stage | 2021-08-13 |  | 1 | Update configuration with new gearbox | Replacement complete | 3052345 | Closed | Closed |  | 2023-03-02 |  | 9/7 - reduced modulation, 9/21-latch reset, 10/5 - low concern, continue to monitor, 11/8 - high amplitude peak on 10/6, monitor for increased vibration amplitude, 2/28 - 0.008g peak at 6x, stage 1 carrier upwind, 3/21 - 0.024g peak at 9X in stage 2, stage 3 shows 0.3g peak at HSS DnWind Cage freq | True Positive | 566
Bishop Hill 3 | Resolved | 323 | Potential S2 Sun Fault | Sweep | 2nd Planetary Stage | 2023-04-19 |  | 4 | [9 empty] | Case In Progress | -45035
Bishop Hill 3 | Resolved | 324 | Main Bearing Outer Race Damage | Case Tracking | Main Bearing | 2023-01-12 | 2024-07-08 | 3 | repair pending. 3/5/24 - Secondary main bearing borescope performed, found pitting on outer and inner races, a well as metallic grease expected replacement in 04/2025. 6/2/23 -Outer race fault harmonics are present in the spectrum, borescope found bronze grease and indenting, monitor temps | Final Report Needed | 3067616 | Closed | Closed | Q2 2025 |  |  |  | Defect Confirmed - Repair Complete | -44938
Bishop Hill 3 | Active | 326 | S2 Planetary issue | Sweep | CMS Monitor | 2024-08-19 |  | 5 | 8/19 - CMS shows potential s2 issue continue to monitor for progression | Monitor | [7 empty] | Case In Progress
Bishop Hill 3 | Resolved | 328 | S1 Planetary gearing issue | Alarm | 1st Planetary Stage | 2021-06-26 |  | 5 | 2/19/24 - Direct event/wave form spiking on 2/15/24, recommend turbine be shutdown until secondary inspection is performed. 1/25/24 - 1st stage has some damage to the planet gears. There is a possibility that this damage came from the ring gear, but techs couldn't find the source of damage. | CMSGBXBORE | 3254953 | Closed | Closed |  |  | 4/4 - low concern | Particle Counter Installed and Communicating, 10/5 - peaks up to alarm setpoint, no characteristic fault peaks in frequency spectrum, 11/8- July borescope shows indents, ring fault is likely, 12/21 - particle counter may be installed incorrectly, Poseidon is looking into install configuration. 1/4/22 - New alarms and warnings for stage 1 and 2 direct signal, monitor, 2/9 - particle counter has been replaced by Poseidon, still not detecting as expected, remove magnetic mount, still no significant increase, monitor, 2/28 - CMS increased to alarm following gearbox high temp in 4/7/21, high amplitude vibration continued until 12/17/21 - unclear the extent of damage, 4/15 - no significant progression, 5/6 - potential damage to stage 2 carrier, no progression, 5/24 - 1000 count increase in the 0-100micron bin, no other progression | Case In Progress | -44373
Bishop Hill 3 | Resolved | 328 | Stage 1 planet gearing issue | Alarm | 1st Planetary Stage | 2024-01-16 |  | 2 | 4/4/24 - Repair complete. 2/19/24 - turbine shut down 1/25/24 - 1st stage has some damage to the planet gears. There is a possibility that this damage came from the ring gear, but techs couldn't find the source of damage. 1/16/24 - CMS indicates S1 gearing issue, sent out for borescope/inspection and derate by 50%. | Final Report Needed | 3302363 | Closed | Closed |  |  |  |  | Miss - Defect Not Caught | -45307
Bishop Hill 3 | Resolved | 334 | Stage 1 Carrier Damage | Warning | 1st Planetary Stage | 2022-01-12 |  | 5 | 1/19/24 - Repair complete, replaced with ZF. 9/22/23 - Derate approved via WEC and GE, derated to 50%. 1/12/23 - S1 and S2 PS and PC bearing damage, confirmed by borescope, debris generation is low, monitor |  | 3106481 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -44573
Bishop Hill 3 | Active | 338 | Potential S1 Planetary ORBP/IRBP Issue | Sweep | 1st Planetary Stage | 2024-06-19 |  | 2 | 6/19/24 - CMS indicates potential S1 planetary ORBP/IRBP issue, sent out for borescope | CMSGBXBORE | 3369326 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45462
Bishop Hill 3 | Resolved | 340 | Main Bearing ORBP/IRBP issue | Alarm | Main Bearing | 2021-11-24 |  | 2 | Grease has silver color, spalling/pitting on both the inner and outer races. CMS indicates possibly greater damage. Recommend replacement within 4-6 months from 2/2023. Placed on MFCL. Shutdown 6/28/23. | Final Report Needed | 3052545 | Closed | Closed |  | 2023-11-19 |  | 12/21 - ORBP frequency began peaking above alarm on 11/24, direct signal shows no change. FFT occasionally shows 0.02g peak at the ORBP fault frequency. Temps look normal to neighbors, monitor for increases 1/4/22 - peak at ORBP fault frequency in FFT is present continuously, 2/9 - ORBP frequency peaks above alarm setpoint between 11/19/21 and 1/14/22, Direct signal is low. | Defect Confirmed - Repair Complete | 725
Bishop Hill 3 | Active | 344 | Potential Main Bearing outer race Issue | Sweep | Main Bearing | 2023-03-08 |  | 5 | 6/6/23 - Borescope found standstill marks. Continue to monitor, operate as normal. | Monitor | 3113027 | Closed | Closed |  |  |  |  | False Positive | -44993
Bishop Hill 3 | Resolved | 346 | HSS Pinion Cracked Tooth | Alarm | Helical High Speed Stage | 2023-12-15 |  | 3 | 12/15/2023 - Looks like potential hss issue, specturm is showing peaks at 1 order apart , turbine shut down and work order sent out expected to be done by monday. 12/18/23 - found cracked tooth not yet liberated, turbine put into 50% derate.1/3/24 - borescope found the HSS RS bearing still alligned with casting marks, and the tooth liberated itself from the pinion | CMSGBXBORE | 3243723 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -45275
Bishop Hill 3 | Active | 347 | Potential Main Bearing ORBP/IRBP | Sweep | Main Bearing | 2024-04-29 |  | 4 | 5/7/24 - Borescope had some indents and normal wear and tear. Continue to monitor for progression. 5/2/24 - CMS shows progression and IRBP signature . Borescope requested. 4/29/24 - CMS shows potential Main bearing orbp.irbp issue, however signature just be banding/wear. Continue to monitor CMS and temperature for progression. | Monitor | 3345456 | Closed | Closed |  |  |  |  | Case In Progress | -45411
Bishop Hill 3 | Active | 347 | main bearing potential issue | Sweep | Main Bearing | 2024-07-26 |  | 4 | 7/26/24 -cms shows potential mb issue but is too early to be sure. Continue to monitor | Monitor | [7 empty] | Case In Progress | -45499
Bishop Hill 3 | Resolved | 350 | Stage 2 Sensor Issue | Instrumentation | 2nd Planetary Stage | 2022-07-05 |  | 5 | Replace sensor | CMSTRBLSHOOT | 2954599 | Closed | Closed |  |  |  |  | True Positive | -44747
Traverse 1 | Active | 1001 | Potential Timken Main Bearing BS2X Issue | Sweep | Main Bearing | 2024-06-03 |  | 2 | 7/18/24 - Roller fracture occurred, turbine is DNR'd. 6/3/24 - Customer requested MB remain at 100% power after borescope showed DLC delamination and roller damage. 6/3/24 - Turbine is showing signature progression, recommend derating turbine to 50% and borescoping the main bearing of this turbine with focus on rolling elements. | Final Report Needed | 3361070 | Closed | Closed |  | 2024-07-15 |  |  | Defect Confirmed - Repair Complete | 42
Traverse 1 | Resolved | 1002 |  | Instrumentation | CMS Monitor | 2022-08-04 |  |  | Replace 60M100 Monitor | CMSTRBLSHOOT | 2972540 | Cancelled | Cancelled |  | 2022-08-06 |  |  |  | 2
Traverse 1 | Resolved | 1002 |  | Alarm | Main Bearing | 2022-03-19 |  | 6 |  | Monitor | [5 empty] | 4/1 - no harmonics, small haystack, timeseries hitting alarm setpoint after outage, 6/20 - offline, feeder outage, 8/4 - rebooted monitor to regain data flow, no back fill, 8/22 - reduce to cat 1, 11/18 - very small impacts on timebase ~.1g, 12/9 - clear harmonics and sidebands structures at low frequencies, indicating HSIS bearing damage, limited progression, increase to cat 2 |  |  | -44639
Traverse 1 | Resolved | 1002 | Potential Brake Drag Issue | Warning | Helical High Speed Stage | 2024-07-18 |  | 3 | 7/18/24 - Potential hydraulic brake dragging issue, please inspect brake for signs of rubbing. If not found, visually inspect HSS pinion. | CMSHSS | 3388449 | Closed | Ready to Schedule |  | 2024-07-22 |  |  | Defect Confirmed - Repair Complete | 4
Traverse 1 | Resolved | 1004 |  | Warning | 2nd Planetary Stage | 2022-04-23 |  | 6 |  | CMSGBXBORE | 2945469 | Cancelled | Cancelled |  |  | 5/10 - Stage 2 bearing issue, potentially planet bearings or carrier, no progression, 6/20 - offline, feeder outage, 8/22 - limited progression, 11/18 - no fault indicators on FFT, no progression, reduce to Cat 1, 1/11 - S1 PC BRG |  |  | -44674
Traverse 1 | Active | 1004 | S1 Planetary Carrier Issue | Sweep | 1st Planetary Stage | 2023-03-06 |  | 2 | 1/31/24 - Turbine was shutdown until repair. 1/2/24 - Widespread damage found on 1st and 2nd planetary stage bearings. Debris generation hitting 6kmg+. Turbine to be derated to 50% until GE responds to warranty case. 12/20/23 - Particle counts continue to increase hitting 5.5k in 24 hours, recommend secondary borescope be performed at next possible opportunity. 3/6/23 - Borescope found pitting in 1st planetary stage. Reclaim made. | Final Report Needed | 3244830 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -44991
Traverse 1 | Resolved | 1005 |  | Warning | Main Bearing | 2022-06-30 |  | 5 |  | CMSMBBORE | 2954530 | Closed | Closed |  |  | 7/5 - main bearing direct and ORBP warnings, 2-3g impacts in the timebase, 8/3 - expecting main bearing borescope tomorrow, 8/4, 8/22 - borescope found mild grease "smearing" on outer race, likely responsible for increase in vibration, reduce to cat 2, 11/18 - increase on trend after coming online in Oct, 1g impacts on timebase, |  |  | -44742
Traverse 1 | Resolved | 1006 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-08-31 |  | 3 | 8/31/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3182529 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45169
Traverse 1 | Resolved | 1006 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-06-27 |  | 3 | 3/27/24 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3324258 | Closed | Ready to Schedule |  | 2024-09-12 |  |  | Defect Confirmed - Repair Complete | 443
Traverse 1 | Active | 1006 | Potential Main Bearing BS2X issue | Sweep | Main Bearing | 2024-05-14 |  | 4 | 7/26/24 - Turbine DNR'd6/27/24 - Turbine faulted out, customer requested derate to 50%. 6/13/24 - Borescope found roller damages. 5/14/24 - CMS shows potential main bearing roller element issue, continue to monitor for progression. | Final Report Needed |  |  | Ready to Schedule |  | 2024-07-25 |  |  | Defect Confirmed - Repair Complete | 72
Traverse 1 | Resolved | 1007 |  | Warning | 2nd Planetary Stage | 2022-03-19 |  | 6 |  | Monitor | [5 empty] | 4/1 - elevated peak at stage 2 2X GMF - likely misalignment, peak at Stage 2 Carrier GS outer race, 6/20 - offline, feeder outage, 8/4 - online, 8/22 - elevated IMS shaft harmonics, limited progression, 11/18 - limited progression, Modulation in timebase reaching 2g |  |  | -44639
Traverse 1 | Active | 1008 | Timken Main Bearing BS2X Signature | Sweep | Main Bearing | 2023-12-11 |  | 2 | 1/8/24 - Borescope found cracked roller, turbine DNR until repair. 12/11/23 - Recommend main bearing borescope, if one has not already been performed by EOW inspection campaign, with a focus on the MB's cage and roller elements. | Final Report Needed |  |  |  |  | 2024-03-19 |  |  | Defect Confirmed - Repair Complete | 99
Traverse 1 | Resolved | 1009 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-09-26 |  | 3 | 9/26/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3197129 | Closed | Ready to Schedule |  | 2023-10-12 |  |  | Defect Confirmed - Repair Complete | 16
Traverse 1 | Resolved | 1010 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-11-20 |  | 3 | 11/20/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3227523 | Closed | Ready to Schedule |  | 2024-05-03 |  |  | Defect Confirmed - Repair Complete | 165
Traverse 1 | Resolved | 1011 |  | Warning | Main Bearing | 2022-05-17 |  | 5 |  | Monitor | [5 empty] | 8/4 - step up to warning setpoint after outage in May, 4g impacts in the timebase, temps are slightly elevated in tads, no clear fault frequencies, inspect if temperatures increase, 11/18 - Significant reduction in trend, temps in line with neighbors |  |  | -44698
Traverse 1 | Resolved | 1012 |  | Warning | 2nd Planetary Stage | 2022-03-19 |  | 5 |  | Monitor | [5 empty] | 5/10 - Very low stage 2 direct signal, Stage 2 PC BRG GS ORBP peak and harmonics, 6/20 - offline, feeder outage, 8/4 - back online, no progression, 11/18 - no progression, ORBP peak still present |  |  | -44639
Traverse 1 | Resolved | 1013 |  | Warning | Generator Inboard | 2022-11-11 |  | 6 |  | Monitor | [5 empty] | 11/18 - Potential ORBP fault on Generator DE Bearing |  |  | -44876
Traverse 1 | Resolved | 1014 |  | Warning | 2nd Planetary Stage | 2022-07-31 |  | 5 |  | Monitor | [5 empty] | 8/4 - GFED peak past alarm on 8/2, envelope indicate S2 PC BRG GS ORBP and roller damage |  |  | -44773
Traverse 1 | Resolved | 1014 | 2nd Planetary Stage Accelerometer | Instrumentation | 2nd Planetary Stage | 2023-09-26 |  | 5 | 9/26/23 - ​2nd planetary stage accelerometer is currently showing a short circuit, please investigate wiring and connections, replace sensor if needed. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3197119 | Closed | Ready to Schedule |  | 2024-01-08 |  |  | Defect Confirmed - Repair Complete | 104
Traverse 1 | Resolved | 1015 |  | Warning | Main Bearing | 2022-03-28 |  | 6 |  | Monitor | [5 empty] | 4/1 - no fault harmonics, timeseries hitting warning setpoint, 5/10 - slight peak at roller fault frequency, direct signal has reduced, 6/20 - offline, feeder outage, 8/4 - operating at warning setpoint after outage, 11/18 - still at warning setpoint, slight development of ORBP fault on FFT, temps good |  |  | -44648
Traverse 1 | Active | 1017 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-09-03 |  | 5 | 9/3/24 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3413082 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45538
Traverse 1 | Active | 1017 | Potential Timken Main Bearing Rolling Element Issue | Sweep | Main Bearing | 2024-04-04 |  | 2 | 5/22/24 - Turbine derated to 50% due to borescope results. 4/4/24 - Recommend main bearing borescope + grease purge within 2 weeks from 4/4/24. | Final Report Needed | 3328838 | Closed | Closed |  | 2024-09-10 |  |  | Defect Confirmed - Repair Complete | 159
Traverse 1 | Resolved | 1018 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2023-03-28 |  | 2 | CMS monitor is not showing any communication. Ensure that monitor appears powered and ethernet is plugged into Port A | CMSTRBLSHOOT | 3103441 | Closed | Closed |  | 2023-04-17 |  |  | Defect Confirmed - Repair Complete | 20
Traverse 1 | Resolved | 1018 | Gearbox Sensor 2 + 3 Accelerometer Issue | Instrumentation | 2nd Planetary Stage | 2022-06-20 |  | 5 | Gearbox sensor 2 needs to be replaced. Gearbox sensor 3 is showing shorted sensor wiring, check loop | CMSTRBLSHOOT | 2972056 | Closed | Closed |  |  | 8/4 - WO created |  |  | -44732
Traverse 1 | Resolved | 1019 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-04 |  | 5 | Follow Keyphasor Guide to check for common issues. Verify gen encoder wiring, terminal 8X, and at the PEM, verify connection to KPH2. Gap voltage should be 0.61V | CMSTRBLSHOOT | 2987695 | Ready to Schedule | Ready to Schedule |  | 2024-10-21 |  |  | Defect Confirmed - Repair Complete | 809
Traverse 1 | Resolved | 1020 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-11-27 |  | 3 | 11/27/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3228913 | Ready to Schedule | Ready to Schedule |  | 2024-10-09 |  |  | Defect Confirmed - Repair Complete | 317
Traverse 1 | Resolved | 1021 |  | Warning | 2nd Planetary Stage | 2022-02-05 |  | 5 |  | Monitor | [5 empty] | 4/1 - elevated peak at stage 2 2X GMF - likely misalignment, harmonics in FFT may indicate damage to stage 2 carrier rollers and outer race, 6/20 - Two peaks to warning setpoint in Stage 2 Direct, envelope FFT indicates damage to S2 PC BRG RS rollers, monitor for additional peaks, 8/4 - additional warning event, direct shows recent peaks to the warning setpoint, 8/22 - potential S2 bearing progression, monitor for additional peaks to warning setpoint, 11/18 - trend has stayed at warning setpoint |  |  | -44597
Traverse 1 | Active | 1023 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-08-25 |  | 4 | 8/25/23 - Please inspect keyphasor circuit | CMSTRBLSHOOT | 3178434 | Ready to Schedule | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45163
Traverse 1 | Active | 1023 | Potential Timken Main Bearing BS2X Issue | Sweep | Main Bearing | 2024-08-12 |  | 2 | 8/12/24 - 7/24 borescope found early signs of damage, keyphasor was repaired 8/6. | Repair Pending | [7 empty] | Defect Confirmed - Awaiting Repair | -45516
Traverse 1 | Resolved | 1024 |  | Warning | Helical High Speed Stage | 2022-03-15 |  | 6 |  | Monitor | [5 empty] | 4/1 - potential damage to HSS DnWind bearing inner race, harmonics present, 5/10 - some progression in HSS GS bearing fault peaks, increase in amplitude, elevated to cat 2, 6/20 - offline, feeder outage, 8/4 - back online, resuming peaks to alarm setpoint in GFED signal, 8/22 - elevated lifetime operation, reduce to cat 1, 11/18 - no progression on trend, |  |  | -44635
Traverse 1 | Resolved | 1026 | Keyphasor Issue | Sweep | Keyphasor | 2024-03-27 |  | 3 | 3/27/24 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3324251 | Ready to Schedule | Ready to Schedule |  | 2024-10-08 |  |  | Defect Confirmed - Repair Complete | 195
Traverse 1 | Resolved | 1027 |  | Warning | 2nd Planetary Stage | 2022-04-28 |  | 6 |  | Monitor | [5 empty] | 5/10 - stage 2 planet bearing fault peaks, 6/20 - offline, feeder outage, 11/18 - potentially an IRBP fault, no development on trend |  |  | -44679
Traverse 1 | Resolved | 1027 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-09-17 |  | 3 | 9/17/24 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3428211 | Closed | Ready to Schedule |  | 2024-10-08 |  |  | Defect Confirmed - Repair Complete | 21
Traverse 1 | Resolved | 1028 |  | Alarm | 2nd Planetary Stage | 2022-03-19 |  | 6 |  | Monitor | [5 empty] | 4/1 - potential damage to Stage 2 planet gear bearing, roller fault harmonics are present but low, 6/20 - offline, feeder outage, 8/4 - tower online, S2 Planet fault sidebands in mode 1, 11/18 - no progression |  |  | -44639
Traverse 1 | Active | 1028 | Main Bearing Issue | Sweep | Main Bearing | 2023-05-24 |  | 2 | 8/25/23 - CMS will continue to monitor for any changes. | Monitor | 3132063 | Closed | Closed |  |  |  |  | Case In Progress | -45070
Traverse 1 | Active | 1028 | Main Bearing Accelerometer Open Circuit | Instrumentation | Main Bearing | 2024-09-03 |  | 5 | 9/3/24 - Main bearing accelerometer currently reading an open cicuit, please investigate wiring and connections. | CMSTRBLSHOOT | 3413080 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45538
Traverse 1 | Active | 1030 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/24 - Particle counter stopped collecting data, please ensure that counter is powered. Contact abarndt@invenergy.com for support. | GBXPARTTS | 3255302 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 1 | Resolved | 1035 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-04 |  | 3 | Follow Keyphasor Guide to check for common issues, also check that gearbox sensors are mounted tightly and check filter for debris | CMSTRBLSHOOT | 3101535 | Closed | Closed |  |  |  |  | True Positive | -44777
Traverse 1 | Resolved | 1035 |  | Warning | 2nd Planetary Stage | 2022-02-19 |  | 6 |  | Monitor | [5 empty] | 4/1 - likely misalignment in stage 2 mesh, potential damage to S2 PC BRGx GS outer race, 5/10 - no progression, 8/4 - planet fault sidebands at GMFs, especially 3X. 8/22 - keyphasor is unreliable |  |  | -44611
Traverse 1 | Resolved | 1035 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-09-26 |  | 3 | 9/26/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3197130 | Closed | Ready to Schedule |  | 2024-01-23 |  |  | Defect Confirmed - Repair Complete | 119
Traverse 1 | Active | 1035 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-10-04 |  | 4 | 10/4/24 - article counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3201853 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45569
Traverse 1 | Active | 1036 | Potential Timken Main Bearing BS2X Issue | Sweep | Main Bearing | 2024-06-10 |  | 2 | 6/25/24 - Turbine has been DNR'd. 6/11/24 - Turbine derated to 75% per customer request. 6/3/24 - Turbine is showing signature progression, recommend derating turbine to 50% and borescoping the main bearing of this turbine with focus on rolling elements. | Final Report Needed | 3365911 | Closed | Closed |  | 2024-09-06 |  |  | Defect Confirmed - Repair Complete | 88
Traverse 1 | Active | 1037 | 2nd Planetary Stage Accelerometer Short Circuit | Instrumentation | 2nd Planetary Stage | 2024-10-14 |  | 5 | 10/14/24 - 2nd planetary stage accelerometer is reading a short, please investigate wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3445589 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45579
Traverse 1 | Resolved | 1038 |  | Warning | 1st Planetary Stage | 2022-06-19 |  | 5 |  | Monitor | [5 empty] | 6/20 - Stage 1 SER Sun Fault GFED signal shows increasing trend since coming back online on 6/3, shaft harmonics are present in the envelope, no sun fault sidebands to support warning event, monitor for progression, 8/4 - GFED signal shows increasing amplitude spikes above the warning setpoint since June, invalid speed from keyphasor, instrumentation case created, 8/22 - Alarm surpassing (800g) peaks in S1 SER Sun Fault GFED and S2 SER Planet Fault GFR SR1, skeptical of alarms due to keyphasor issue, no aparent sun fault sidebands in S1, increase priority on instrumentation work order, 11/18 - still unbelievable trend amplitude compared to timebase and FFT, |  |  | -44731
Traverse 1 | Resolved | 1038 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-04 |  | 5 | Follow Keyphasor Guide to check for common issues, also check that gearbox sensors are mounted tightly and check filter for debris | CMSTRBLSHOOT | 2987693 | Closed | Ready to Schedule |  |  |  |  | True Positive | -44777
Traverse 1 | Resolved | 1038 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-09-14 |  | 3 | 9/14/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3191367 | Closed | Closed |  | 2023-11-06 |  |  | Defect Confirmed - Repair Complete | 53
Traverse 1 | Active | 1038 | S1 Planetary Gearing Issue | EOW | 1st Planetary Stage | 2023-04-17 |  | 1 | S1 SG - severe tooth spalling, S1 PG and RG - Indents, S2 PG Indents; leaving online at 50%. EoW Case Placed | Final Report Needed | 3113834 | Closed | Closed |  | 2024-02-28 |  |  | Defect Confirmed - Repair Complete | 317
Traverse 1 | Resolved | 1038 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-09-03 |  | 4 | 9/3/24 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3413086 | Closed | Closed |  | 2024-10-02 |  |  | Defect Confirmed - Repair Complete | 29
Traverse 1 | Active | 1038 | Potential Main Bearing Issue | Sweep | Main Bearing | 2024-10-04 |  | 2 | 10/24/24 - Recommend borescoping this main bearing within 2 weeks from 10/4/24 with focus on outer race and rollers. | Repair Pending | 3441975 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45569
Traverse 1 | Active | 1039 | Main Bearing Issue | GE Alert | Main Bearing | 2024-03-14 |  | 3 | 5/30/24 - Turbine overtemped and placed on DNR list. 4/22/24 - Inner and outer race damages noted, warranty claim submitted. 3/14/24 - GE Alert: Derate turbine to 50% of rated power Inspect grease in bearing and trap and take sample Ensure accelerometer and temperature sensors are securely mounted/calibrated Perform visual/borescope inspection if needed Purge grease/re-grease if needed Submit a warranty claim with the inspection results if needed | Final Report Needed | 3317435 | Closed | Closed |  | 2024-05-30 |  |  | Defect Confirmed - Repair Complete | 77
Traverse 1 | Resolved | 1041 |  | Warning | Main Bearing | 2022-03-15 |  | 6 |  | Monitor | [5 empty] | 4/1 - haystack, no other harmonics, warning/alarm level vibration at all power modes, 5/10 - vibration has reduced to warning setpoint, 6/20 - offline, feeder outage, 8/4 - signal reduced to below warning |  |  | -44635
Traverse 1 | Resolved | 1041 | Generator Outboard ORBP | Alarm | Generator Outboard | 2023-06-08 |  | 3 | 7/25/23 - CMS Signature amplitudes have increased, recommend derating turbine to 50% , performing inspection of the bearing, and adding new grease. | CMSGENB | 3140547 | Closed | Closed |  | 2023-10-24 |  |  | Defect Confirmed - Repair Complete | 138
Traverse 1 | Resolved | 1042 |  | Warning | Main Bearing | 2022-07-27 |  | 3 |  | CMSMB | 2972112 | Cancelled | Cancelled |  |  | 8/4 - Direct and ORBP signals have trended slowly up to the warning setpoint, temperatures are elevated relative to neighbors, MB Check, 11/18 - slight decrease in trend amplitude, temps marginally higher than neighbors |  |  | -44769
Traverse 1 | Active | 1042 | HSS Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2024-10-21 |  | 4 | 10/21/24 - ​HSS accelerometer is giving erroneous readings, please investigate wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3449120 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45586
Traverse 1 | Active | 1043 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-04 |  | 5 | 9/14/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 2987696 | Ready to Schedule | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -44777
Traverse 1 | Resolved | 1044 |  | Alarm | 2nd Planetary Stage | 2022-02-17 |  | 6 |  | Monitor | [5 empty] | 4/1 - potential stage 2 planet gear issue, 5/10 - no progression, implicated carrier as well, 6/20 - offline, feeder outage, 8/4 - no progression |  |  | -44609
Traverse 1 | Resolved | 1045 |  | Warning | 2nd Planetary Stage | 2022-08-03 |  | 6 |  | Monitor | [5 empty] | 8/4 - Ring fault signal has been elevated for full operating life, elevated IMS harmonics |  |  | -44776
Traverse 1 | Active | 1046 | 2nd Planetary Stage Accelerometer | Instrumentation | 2nd Planetary Stage | 2024-04-29 |  | 4 | 4/29/24 - 2nd stage accelerometer is reading uneven bias voltage. Please investigating wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | 3343179 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45411
Traverse 1 | Active | 1047 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/24 - Particle counter stopped collecting data, please ensure that counter is powered. Contact abarndt@invenergy.com for support. | GBXPARTTS | 3255304 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 1 | Active | 1047 | Main bearing BS2X rolling element | Sweep | Main Bearing | 2024-09-12 |  | 2 | 9/12/24 - Recommend borescoping this main bearing within 2 weeks from 9/12/24 with focus on outer race and rollers. | Repair Pending | 3426711 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45547
Traverse 1 | Active | 1050 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-10-04 |  | 4 | 10/4/24 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3201851 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45569
Traverse 1 | Resolved | 1051 |  | Warning | 2nd Planetary Stage | 2022-02-19 |  | 6 |  | Monitor | [5 empty] | 4/1 - shaft harmonics present, early planet fault sidebands, 5/10 - potential stage 2 carrier GS outer race, 6/20 - offline, feeder outage, 8/4 - modulation in the timebase indicates gear damage, GMFs carrying planet fault sidebands |  |  | -44611
Traverse 1 | Resolved | 1052 | Data Locked Up? | Instrumentation | Other | 2023-11-27 | 2023-12-05 | 5 | 11/27/23 - Rebooted monitor, need to check back in on this later. | Monitor |  |  |  |  | 2023-12-11 |  |  | Defect Confirmed - Repair Complete | 14
Traverse 1 | Resolved | 1053 |  | Warning | 1st Planetary Stage | 2022-03-16 |  | 5 |  | Monitor | [5 empty] | 4/1 - low concern, 5/10 - potential early faults for stage 2 carrier GS, 6/20 - offline, feeder outage, 8/4 - no data loading past the outage, tower is online. Rebooting CMS monitor to see if data flow is restored, 8/23 - rebooting again, may need to reboot uptower, 11/18 - data is back, no progression on trend |  |  | -44636
Traverse 1 | Active | 1053 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-09-26 |  | 3 | 9/26/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3197123 | Closed | Ready to Schedule |  | 2024-10-08 |  |  | Defect Confirmed - Repair Complete | 378
Traverse 1 | Resolved | 1055 |  | Change 1 | 1st Planetary Stage | 2022-06-26 |  | 5 |  | Monitor | [5 empty] | 8/4 - 2g impact on 6/26, potential damage to S1 PC BRG GS rollers, occasional 102g impacts appear in the timebase, 8/23 - potential S2 PS BRG IRBP damage, 11/18 - impacts seem to have stopped, blunted? |  |  | -44738
Traverse 1 | Resolved | 1056 |  | Warning | Helical High Speed Stage | 2022-03-16 |  | 5 |  | Monitor | [5 empty] | 4/1 - potential HSS bearing issue, several harmonics present in FFT, 5/10 - HSS GS ORBP peak with harmonics, increased from 0.03 to 0.07g, 6/20 - limited progression for HSS GS ORBP, continue to monitor, 8/4 - S3 mesh misalignment, 11/18 - alightly increased amp of S3 2x GMF, slight increase in trend, HSS GS ORBP peaks back down to ~.05g |  |  | -44636
Traverse 1 | Active | 1056 | S1 Planetary Bearing Issue | Sweep | 1st Planetary Stage | 2023-06-27 |  | 2 | 6/27/23 - Borescope found early spalling on S1 planetary bearings, CMS will continue to monitor. | Longterm Watchlist | 3148703 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45104
Traverse 1 | Resolved | 1056 | Generator Inboard ORBP | GE Alert | Generator Inboard | 2023-06-13 |  | 3 | 6/13/23 - Inspect bearing grease and re-grease if needed Test for an electrical short across bearing insulation ring and troubleshoot if necessary Ensure accelerometer is securely mounted and isolated Record any abnormal sounds during operation (before and after greasing, if possible) Submit a warranty claim with the inspection results to pursue bearing replacement if needed | CMSGENB | 3142446 | Closed | Closed |  | 2023-08-15 |  |  | Defect Confirmed - Repair Complete | 63
Traverse 1 | Resolved | 1058 |  | Warning | Main Bearing | 2022-04-23 |  | 5 |  | Monitor | [5 empty] | 5/10 - vibration increased to and decreased from warning setpoint, timebase shows impacts, 6/20 - temps are ever so slightly elevated relative to neighbors, FFT does not indicate damage, monitor for increases, 8/4 - no significant increase above the warning setpoint, temps remain elevated, potential damage to ORBP and or cage, 8/22 - occasional 2-4g impacts, slightly elevated temps |  |  | -44674
Traverse 1 | Active | 1058 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/24 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255305 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 1 | Resolved | 1059 |  | Warning | Helical High Speed Stage | 2022-03-25 |  | 6 |  | Monitor | [5 empty] | 4/1 - elevated GMF's, 5/10 - envelope FFT shows many peaks at lower frequencies, potentially indiciating roller damage to the HSIS RS rollers, 6/20 - potential misalignment as well |  |  | -44645
Traverse 1 | Resolved | 1062 |  | Warning | Helical High Speed Stage | 2022-02-07 |  | 5 |  | Monitor | [5 empty] | 4/1 - elevated stage 3 2X GMF. Likely mesh misalignment, potential HSS bearing outer race damage, 6/20 - Power Mode 3 pinion fault sidebands are present, may indicate bearing damage as well. Envelope shows HSS RS fault peaks, occasional HSIS GS outer race fault peaks, temps are slightly elevated, elevating to cat 2, 8/4 - pinion fault sidebands are most pronounced in mode 3, envelope indicates HSIS RS IRBP, 8/23 - low amplitude pinion fault sidebands, monitor for timebase increase, 11/18 - pinion fault sidebands have reduced in size and number, 2g floor on timebase |  |  | -44599
Traverse 1 | Resolved | 1064 | Gearbox 2 Sensor Issue | Instrumentation | 2nd Planetary Stage | 2022-06-20 |  |  | Shorted sensor wiring | CMSTRBLSHOOT | 2947750 | Cancelled | Cancelled |  |  | 2023-01-27 |  |  | -44732
Traverse 1 | Resolved | 1064 | High Speed Stage Accelerometer Short Circuit | Instrumentation | Helical High Speed Stage | 2023-01-27 |  | 5 | High Speed stage accelerometer is currently reading an short circuit. Please inspect wiring harness, replace sensor if needed. | CMSTRBLSHOOT | 3073257 | Closed | Closed |  | 2023-03-16 |  |  | Defect Confirmed - Repair Complete | 48
Traverse 1 | Resolved | 1064 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-06-27 |  | 3 | Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3148628 | Closed | Ready to Schedule |  | 2023-07-20 |  |  | Defect Confirmed - Repair Complete | 23
Traverse 1 | Resolved | 1065 | Keyphasor Issue | Keyphasor Issue | Keyphasor | 2022-08-04 |  | 5 | Follow Keyphasor Guide to check for common issues | CMSTRBLSHOOT | 2987700 | Closed | Closed | [5 empty] | -44777
Traverse 1 | Active | 1065 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-06-27 |  | 3 | Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3148632 | Ready to Schedule | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45104
Traverse 1 | Resolved | 1067 |  | Warning | Helical High Speed Stage | 2022-11-13 |  | 6 | [7 empty] | 11/18 - trend has slightly peaked over warning threshold, misalignment suggested by elevated 2x GMF, potential HSS BRG IRBP GS damage |  |  | -44878
Traverse 1 | Resolved | 1067 | Main Bearing Accelerometer Open Circuit | Instrumentation | Main Bearing | 2024-03-27 |  | 4 | 3/27/2024 - Main bearing accelerometer is currently reading an open circuit, please investigate connections and wirings, replace sensor if needed | CMSTRBLSHOOT | 3324253 | Ready to Schedule | Ready to Schedule |  | 2024-05-18 |  |  | Defect Confirmed - Repair Complete | 52
Traverse 1 | Resolved | 1068 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-04 |  | 5 | Follow Keyphasor Guide to check for common issues | CMSTRBLSHOOT | 2987694 | Closed | Closed |  | 2023-04-21 |  |  | True Positive | 260
Traverse 1 | Resolved | 1068 |  | Warning | 2nd Planetary Stage | 2022-03-14 |  | 6 |  | Monitor | [5 empty] | 4/1 - Stage 2 FFT indicates planet gear bearing issue, stage 3 pinion fault sidebands, 5/10 - stage 2 carrier damage potentially, stage 3 FFT is not conclusive, 6/20 - limited progression, 8/4 - keyphasor issue, instrumentation case created |  |  | -44634
Traverse 1 | Resolved | 1068 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-11-27 |  | 3 | 11/27/23 - Keyphasor signal not working properly, appears to be reading .8V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3228877 | Ready to Schedule | Ready to Schedule |  | 2024-11-01 |  |  | Defect Confirmed - Repair Complete | 340
Traverse 1 | Resolved | 1070 |  | Warning | Main Bearing | 2022-06-16 |  | 5 |  | Monitor | [5 empty] | 6/20 - main bearing direct jumped to warning setpoint in late May, trend is matched by ORBP signal, temps look normal, continue to monitor, 8/4 - temps look normal, reduce to cat 2, 8/23 - signal reduced, 11/18 - signal still reduced, temps good |  |  | -44728
Traverse 1 | Resolved | 1070 | Generator Inboard Accelerometer Issue | Instrumentation | Generator Outboard | 2023-12-11 |  | 4 | 12/11/23 - Generator Inboard accelerometer issue, sensor is giving erroneous readings. Please replace sensor at next tower climb. | CMSTRBLSHOOT | 3240317 | Closed | Closed |  | 2023-12-12 |  |  | Defect Confirmed - Repair Complete | 1
Traverse 1 | Resolved | 1071 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-04-21 |  | 3 | 9/14/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3115499 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45037
Traverse 1 | Resolved | 1072 |  | Alarm | 2nd Planetary Stage | 2022-01-14 |  | 6 |  | Monitor | [5 empty] | 4/1 - stage 2 planet gear bearing fault harmonics present in FFT, 5/10 - potential samge to stage 2 carrier GS, 6/20 - limited progression, 8/4 - limited progression in bearing damage, |  |  | -44575
Traverse 1 | Resolved | 1072 | HSS Hydraulic Brake Issue | Alarm | Other | 2023-02-27 |  | 2 | Please inspect HSS brake disc pads for any signs of rubbing or dragging. If no signs of issues with brake are found, please inspect HSS pinion for signs of tooth breakage. | CMSHSS | 3087652 | Closed | Closed |  | 2023-03-09 |  |  | Defect Confirmed - Repair Complete | 10
Traverse 1 | Resolved | 1073 |  | Warning | Helical High Speed Stage | 2022-03-19 |  | 6 |  | Monitor | [5 empty] | 4/1 - potential misalignment, 5/10 - high res FFT shows some mesh sidebands, along with high frequency bearing faults harmonics, early damage to HSS RS bearing, 6/20 - offline, feeder outage, 8/4 - misalignment in S3 mesh, potential early damage to HSS GS rollers |  |  | -44639
Traverse 1 | Resolved | 1073 |  | Warning | Main Bearing | 2022-07-28 |  | 5 |  | Monitor | [5 empty] | 8/4 - direct signal increase to just below alarm threshold, temps match 1072, 11/18 - temps good, decline in amp on trend |  |  | -44770
Traverse 1 | Resolved | 1075 |  | Warning | 1st Planetary Stage | 2022-01-14 |  | 6 |  | Resolve | [5 empty] | 4/1 - likely start up vibration, 5/10 - 3g impacts in stage 1 timebase, suspecting damage to stage 1 planet bearing rollers, 6/20 - offline, feeder outage, 8/4 - amplitude reduced after outages, now below warning setpoint, low concern |  |  | -44575
Traverse 1 | Resolved | 1077 |  | Instrumentation | CMS Monitor | 2022-02-18 |  |  | Wait | [5 empty] | 2022-06-20 |  |  |  | 122
Traverse 1 | Resolved | 1078 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-09-26 |  | 3 | 9/26/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3197131 | Closed | Ready to Schedule |  | 2024-02-09 |  |  | Defect Confirmed - Repair Complete | 136
Traverse 1 | Resolved | 1080 |  | Warning | Helical High Speed Stage | 2022-01-13 |  | 6 |  | Monitor | [5 empty] | 4/1 - early HSS DnWind bearing damage to the rollers, 5/10 - harmonics present, no progression, 6/20 - offline, feeder outage, 8/4 - likely S3 mesh misalignment |  |  | -44574
Traverse 1 | Active | 1082 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/24 - ​Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255306 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 1 | Resolved | 1083 |  | Change 1 | 1st Planetary Stage | 2022-06-26 |  | 6 |  | Monitor | [5 empty] | 8/4 - first peak in S1 Direct, envelope indicates S1 PC BRG GS rollers, |  |  | -44738
Traverse 1 | Active | 1085 | 1st Stage Planetary Bearing Issue | Particle Counter | Particle Counter | 2023-04-15 | 2024-11-15 | 3 | 6/6/24 - Borescoped showed early spalled, recommend replacement in Q2-Q3 2025. 5/28/24 - Please perform a full gearbox borescope with focus on the 1st planetary stage at next tower climb. 5/16/24 - S1 spectrum data has check back in another month. 4/15/24 - Particle counts rising, check back in a month. | Longterm Watchlist | 3355381 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45031
Traverse 1 | Active | 1086 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/24 - ​Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255307 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 1 | Resolved | 1087 | HSS Hydraulic Brake Issue | Alarm | Other | 2023-03-16 |  | 2 | Please inspect HSS brake disc pads for any signs of rubbing or dragging. If no signs of issues with brake are found, please inspect HSS pinion for signs of tooth breakage. | CMSHSS | 3099959 | Closed | Closed |  | 2023-04-09 |  |  | Defect Confirmed - Repair Complete | 24
Traverse 1 | Active | 1087 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/24 - Particle counter stopped collecting data, please ensure that counter is powered. Contact abarndt@invenergy.com for support. | GBXPARTTS | 3255299 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 1 | Resolved | 1088 |  | Warning | Helical High Speed Stage | 2022-03-26 |  | 5 |  | Monitor | [5 empty] | 4/1 - early pinion fault sidebands, FFT peak at 2X shaft, 5/10 - bearing fault harmonics with sidebands in the high res FFT, 6/20 - monitor for progression, 8/4 - pinion fault sidebands remain, increase to cat 2, 11/18 - significant increas in 2x S3 GMF, sidebands seem to have gone away, |  |  | -44646
Traverse 1 | Resolved | 1091 |  | Alarm | Helical High Speed Stage | 2022-04-29 |  | 3 |  | Monitor |  |  |  |  | 2022-08-23 | 5/10 - Excessively high vibration in stage 1, FFT shows noise, no faults, suspected poor sensor mounting, creating instrumentation case to check sensor, 6/20 - offline, feeder outage, |  | False Positive - Sensor Issue | 116
Traverse 1 | Resolved | 1091 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-04 |  | 3 | Follow Keyphasor Guide to check for common issues, also check that gearbox sensors are mounted tightly and check filter for debris | CMSTRBLSHOOT | 3101538 | Closed | Closed |  |  |  |  | True Positive | -44777
Traverse 1 | Active | 1091 | High Speed Stage Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2022-04-01 |  | 5 | Sensor is showing suspect vibration, may be a mounting issue or bad sensor | CMSTRBLSHOOT | 2907169 |  | Ready to Schedule |  |  |  | 4/1 - monitor lost comms with server after trying to connect to check sensor status | Case In Progress | -44652
Traverse 1 | Resolved | 1091 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-11-27 |  | 3 | 11/27/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3228892 | Closed | Ready to Schedule |  | 2024-10-18 |  |  | Defect Confirmed - Repair Complete | 326
Traverse 1 | Active | 1092 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/24 - ​Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255308 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 1 | Active | 1093 | 1st Planetary Stage Carrier Bearing Issue | Particle Counter | Particle Counter | 2024-04-11 |  | 3 | 9/30/24 - Moderate damage to the 1st planetary stage bearing and some damage to the 2nd planetary stage bearings. Recommend replacing this gearbox Q2 of 2025 4/11/24 - Recommend full gearbox borescope with focus on the 1st planetary stage within 3 months from 4/11/24. | CMSGBXBORE | 3332076 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45393
Traverse 1 | Resolved | 1095 |  | Warning | 2nd Planetary Stage | 2022-03-25 |  | 6 |  | Monitor | [5 empty] | 4/1 - shaft harmonics present, 6/20 - offline, feeder outage, 8/4 - 13.094 peak and harmonics indicate S2 PS BRG roller damage |  |  | -44645
Traverse 1 | Resolved | 1095 |  | Warning | Main Bearing | 2022-01-13 |  | 5 |  | Monitor | [5 empty] | 4/1 - alarm level vibration, haystack, no harmonics yet, 5/10 - rising vibration floor, vibration has reduced to below alarm setpoint, 6/20 - offline, feeder outage, 8/4 - signal is reduced to mostly below warning setpoint, |  |  | -44574
Traverse 1 | Active | 1095 | Generator Inboard Accelerometer Open Circuit | Instrumentation | Generator Inboard | 2024-04-01 |  | 4 | 4/1/24 - Generator inboard accelerometer is reading an open circuit, please inspect wiring and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3327366 | Ready to Schedule | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45383
Traverse 1 | Resolved | 1096 |  | Warning | Main Bearing | 2022-03-31 |  | 6 |  | Monitor | [5 empty] | 4/1 - alarm level vibration, haystack, no harmonics yet, 5/10 - vibration has reduced to the warning setpoint, 6/20 - offline, feeder outage, 8/4 - signal reduced to normal levels |  |  | -44651
Traverse 1 | Resolved | 1097 |  | Alarm | 1st Planetary Stage | 2022-04-01 |  | 3 |  | Monitor | [5 empty] | 4/1 - stage 1 direct increasing to warning setpoint, FFT shows 3X shaft harmonics, 5/10 - timeseries shows siginificant progression above and back below the alarm setpoint. Occasional 10g impacts in the timebase account for pronounced shaft harmonics, potentially indicating damage to stage 1 bearings, 6/20 - Direct signal has remained below warning setpoint since 4/30, FFT indicates damage to S1 PC BRG GS rollers, 8/4 - tower offline, 8/23 - direct signal reduced after April/May peaks, 11/18 - trend still at normal levels, |  |  | -44652
Traverse 1 | Resolved | 1098 | Gearbox 2 Sensor Issue | Instrumentation | 1st Planetary Stage | 2022-06-20 |  | 5 | Shorted sensor wiring | CMSTRBLSHOOT | 2947751 | Closed | Closed |  | 2023-02-17 |  |  | True Positive | 242
Traverse 1 | Active | 1098 | Main bearing BS2X rolling element | Sweep | Main Bearing | 2024-05-14 |  | 2 | 6/5/24 - Roller spalls found during borescope. 5/16/24 - Turbine derated to 50%. 5/15/24 - CMS indicates BS2X rolling element issue, sent out for main bearing borescope | Final Report Needed | 3351217 | Closed | Closed |  | 2024-07-20 |  |  | Defect Confirmed - Repair Complete | 67
Traverse 1 | Resolved | 1099 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-05-06 |  | 3 | 5/6/24 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3346786 | Closed | Ready to Schedule |  | 2024-10-09 |  |  | Defect Confirmed - Repair Complete | 156
Traverse 1 | Resolved | 1100 | HSS Hydraulic Brake Issue | GE Alert | Other | 2023-03-27 |  | 1 | • Derate turbine to 50% or rated power. • Visually inspect gearbox internals for cracks or broken teeth on the HSS Pinion within 48 hours • Ensure brake disc pads are not rubbing • Photograph findings and submit a warranty claim • If a crack or broken tooth is found, shutdown turbine until further notice | CMSHSS | 3103118 | Closed | Closed |  | 2023-04-06 |  |  | Defect Confirmed - Repair Complete | 10
Traverse 1 | Resolved | 1100 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-01-31 |  | 5 | Please ensure keyphasor signal is plugged into KPH2 instead of KPH1. Ensure PEM is properly wired. Contact abarndt@invenergy.com for support.​ | CMSTRBLSHOOT | 3074132 | Closed | Closed |  | 2024-02-19 |  |  | Defect Confirmed - Awaiting Repair | 384
Traverse 1 | Active | 1101 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/24 - ​Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255309 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 1 | Active | 1102 | Potential 1st Stage Planetary Gearing + Bearing Issue | Particle Counter | 1st Planetary Stage | 2024-06-17 |  | 1 | 6/19/24 - Turbine offline until replacement. 6/17/24 - CMS Data + oil particle data indicates possible 1st Planetary Stage gearing fracture and damage to the planet bearings as well. Recommend full gearbox borescope with focus on the 1st planetary stage at next possible opportunity and derating turbine to 50%. | Final Report Needed | 3367967 | Closed | Closed |  | 2024-06-21 |  |  | Defect Confirmed - Repair Complete | 4
Traverse 1 | Resolved | 1104 |  | Warning | 1st Planetary Stage | 2022-05-02 |  | 3 |  | Monitor | [5 empty] | 5/10 - increase stage 1 direct peak amplitude, now past alarm threshold. Envelop FFT indicates damage to stage 1 carrier GS rollers, monitor after outage, 5/24 - peaks above alarm setpoint after the outage, then decrease to normal levels. AEP wants to file a warranty claim, recommeded waiting for particle counter install to avoid borescope in the mean time, 6/20 - Stage 1 direct has reduced to below warning setpoint, keyphasor isn't reading shaft speed correctly, adding instrumentation case, 11/18 - keyphasor fixed now, S1 direct still looks good, MB was reaching warning level but has since dropped below threshold |  |  | -44683
Traverse 1 | Resolved | 1104 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-07-18 |  | 3 | 7/18/24 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3388451 | Closed | Ready to Schedule |  | 2024-07-21 |  |  | Defect Confirmed - Repair Complete | 3
Traverse 1 | Resolved | 1106 |  | Warning | 1st Planetary Stage | 2022-04-14 |  | 5 |  | Monitor | [5 empty] | 5/10 - peak to alarm setpoint on 4/15/22, keyphasor is not reading speed correctly, added to instrumentation cases, 11/18 - occasional 1g impacts on timebase |  |  | -44665
Traverse 1 | Resolved | 1106 |  | Warning | Main Bearing | 2022-07-05 |  | 5 |  | Monitor | [5 empty] | 8/4 - direct remains at warning setpoint, 11/18 - trend still at warning setpoint, potential ORBP damage seen on FFT |  |  | -44747
Traverse 1 | Active | 1106 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-05-10 |  | 5 | 9/14/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 2947752 | Ready to Schedule | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -44691
Traverse 1 | Resolved | 1108 |  | Alarm | Main Bearing | 2022-02-18 |  | 6 |  | Monitor | [5 empty] | 4/1 - haystack, no other harmonics, warning/alarm level vibration at all power modes, 5/10 - suspected start up vibration or poorly mounted sensor, 6/20 - vibration has reduced to below the warning setpoint, semi-frequent 1g impacts in the timebase suggest potential blunted damage |  |  | -44610
Traverse 1 | Resolved | 1109 |  | Warning | 2nd Planetary Stage | 2022-01-10 |  | 6 |  | Monitor | [5 empty] | 4/1 - potential damage to stage 2 planet gear bearing inner race, 5/10 - additional stage 3 SER pinion fault event, some modulation in the timebase, 6/20 - some misalignment, envelope indicates mild HSS GS roller damage, 8/4 - S2 GMFs carrying planet fault sidebands |  |  | -44571
Traverse 1 | Resolved | 1110 |  | Warning | Main Bearing | 2022-06-16 |  | 5 |  | Monitor | [5 empty] | 6/20 - temps look normal, direct signal hit the alarm setpoint after outage, occasional 1g impacts in the timebase, monitor for damage indicators, 8/4 - Direct signal remains between warning and alarm threshold, temps look normal, 11/18 - returned to service and the trend is below warning levels now, temps good |  |  | -44728
Traverse 1 | Resolved | 1111 |  | Warning | Helical High Speed Stage | 2022-01-14 |  | 6 |  | Monitor | [5 empty] | 4/1 - low concern, 6/20 - offline, feeder outage, 8/4 back online, now operating at the warning setpoint in mode 5 |  |  | -44575
Traverse 1 | Resolved | 1111 | IONet Issue | Instrumentation | CMS Monitor | 2023-07-25 |  | 5 | CMS monitor not receiving power signal, please perform toolbox download to CBM card. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3161683 | Closed | Ready to Schedule |  | 2024-09-06 |  |  | Defect Confirmed - Repair Complete | 409
Traverse 1 | Active | 1111 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-10-04 |  | 4 | 1/17/24 - ​Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3201852 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45569
Traverse 1 | Resolved | 1112 |  | Warning | 2nd Planetary Stage | 2022-01-11 |  | 6 |  | Monitor | [5 empty] | 4/1 - likely start up vibration and misalignment, 5/10 - no data past 2/20, 6/20 - offline, feeder outage, 8/4 - potential damage to S2 PC BRG GS ORBP |  |  | -44572
Traverse 1 | Active | 1112 | Potential Main Bearing Issue | Sweep | Main Bearing | 2023-11-27 |  | 2 | 7/1/24 - Turbine faulted out on EM81 again, turbine DNR'd. 6/24/24 - Turbine faulted out on EM81 and derated to 50%. 11/27/23 - Potential main bearing issue, awaiting signature progression | Final Report Needed | [7 empty] | Case In Progress | -45257
Traverse 1 | Active | 1112 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/24 - ​Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3201860 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 1 | Resolved | 1113 |  | Warning | Helical High Speed Stage | 2022-01-12 |  | 6 |  | Monitor | [5 empty] | 4/1 - misalignment in stage 3 mesh, 8/4 - pinion fault sidebands, envelope indicates HSS GS rollers, 11/18 - sidebands b/w 2x and 3x GMF continue to develop , trend steady |  |  | -44573
Traverse 1 | Resolved | 1114 |  | Change 1 | 1st Planetary Stage | 2022-08-20 |  | 6 |  | Monitor | [8 empty] | -44793
Traverse 1 | Resolved | 1115 |  | Warning | Main Bearing | 2022-01-11 |  | 6 |  | Monitor | [5 empty] | 4/1 - main bearing direct hitting alarm setpoint, 1X harmonics a low frequencies, 5/10 - latch reset when possible, 6/20 - additional warning event, temps look fine, 8/4 - potential cage wear, max around 6/15 |  |  | -44572
Traverse 1 | Resolved | 1115 | Generator Inboard ORBP | GE Alert | Generator Inboard | 2023-06-21 |  | 3 | 8/11/23 - GE recommends 50% derate until repair can be completed. | CMSGENB | 3145077 | Closed | Closed |  | 2023-09-23 |  |  | Defect Confirmed - Repair Complete | 94
Traverse 1 | Resolved | 1117 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-01-31 |  | 5 | Please ensure keyphasor signal is plugged into KPH2 instead of KPH1. Ensure PEM is properly wired. Contact abarndt@invenergy.com for support.​ | CMSTRBLSHOOT | 3074136 | Closed | Ready to Schedule |  | 2024-03-15 |  |  | Defect Confirmed - Repair Complete | 409
Traverse 1 | Resolved | 1118 |  | Warning | 2nd Planetary Stage | 2022-01-11 |  | 6 |  | Monitor |  |  |  |  | 2022-05-10 | 4/1 - low concern |  |  | 119
Traverse 1 | Resolved | 1119 |  | Warning | 2nd Planetary Stage | 2022-01-13 |  | 6 |  | Monitor | [5 empty] | 4/1 - low concern, 6/20 - offline, feeder outage, 8/4 - S2 Sun Fault sidebands are present in the high res spectrum, envelope indicates S2 PS BRG |  |  | -44574
Traverse 1 | Resolved | 1121 |  | Warning | 2nd Planetary Stage | 2022-01-14 |  | 6 |  | Monitor | [5 empty] | 4/1 - low concern, 5/10 - shaft harmonics in envelop FFT, peak at 13.094X with harmonics, does not align with any bearing faults, monitor, 6/20 - offline, feeder outage, 8/4 - elevated IMS harmonics |  |  | -44575
Traverse 1 | Resolved | 1122 |  | Warning | 2nd Planetary Stage | 2022-01-13 |  | 6 |  | Monitor | [5 empty] | 4/1 - potential damage to stage 1 planet gear IRBP, 5/10 - potentiald amage to stage 2 carrier GS outer race, 6/20 - offline, feeder outage, 8/4 - limited progression |  |  | -44574
Traverse 1 | Resolved | 1122 |  | Warning | Main Bearing | 2022-07-28 |  | 5 |  | Monitor | [5 empty] | 8/4 - step up to warning setpoint, occasional 4g impacts, low temps, 11/18 - temps good, continued operation at warning setpoint, no indicators on FFT |  |  | -44770
Traverse 1 | Active | 1122 | 2nd Planetary Stage Bearing IRBP Issue | Sweep | 2nd Planetary Stage | 2023-10-03 |  | 3 | 4/22/24 - Initial borescope (1/4/24) was denied by GE, recommend secondary borescope. 10/3/23 - Recommend full gearbox borescope with focus on 2nd planetary stage bearings within 2 months from 10/3/23. | CMSGBXBORE | 3200512 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45202
Traverse 1 | Resolved | 1126 |  | Warning | Main Bearing | 2022-04-28 |  | 5 |  | Monitor | [5 empty] | 5/10 - Increase in main bearing direct signal since March. FFT does not indicate specific faults and temps look normal compared to neighbors. Continue to monitor, 6/20 - offline, feeder outage, 8/4 - back online, reduce to cat 2, 11/18 - temps good, trend low |  |  | -44679
Traverse 1 | Resolved | 1128 |  | Warning | 2nd Planetary Stage | 2022-01-13 |  | 6 |  | Monitor | [5 empty] | 4/1 - potential damage to stage 1 planet gear IRBP, 6/20 - offline, feeder outage, 8/4 - back online |  |  | -44574
Traverse 1 | Resolved | 1128 |  | Alarm | Main Bearing | 2022-04-28 |  | 3 |  | Monitor | [5 empty] | 5/10 - Increase in main bearing direct signal since March. FFT does not indicate specific faults and temps look normal compared to neighbors. Continue to monitor, 6/20 - offline, feeder outage, 8/23 - temps remain normal, 11/18 - temps in line with neighbors, potential roller damage on FFT |  |  | -44679
Traverse 1 | Resolved | 1129 |  | Warning | Main Bearing | 2022-11-13 |  | 3 | [7 empty] | 11/18 - trend increased to warning threshold after return to service and lookks to still be increasing, potential roller damage seen on FFT, temps are in line with neighbors, |  |  | -44878
Traverse 1 | Resolved | 1130 |  | Warning | Helical High Speed Stage | 2022-03-17 |  | 6 |  | Monitor | [5 empty] | 4/1 - potential misalignment in stage 3 mesh, low sidebands, 5/10 - envelope FFT suggest damage to HSIS RS races or GS rollers, 6/20 - offline, feeder outage, 8/4 - Stage 1 change alert, S2 GFED, monitor for progression |  |  | -44637
Traverse 1 | Resolved | 1130 |  | Warning | Main Bearing | 2022-06-24 |  | 5 |  | Monitor | [5 empty] | 8/4 - direct is operating at the warning setpoint, 11/18 - operating well below warning threshold, temps good |  |  | -44736
Traverse 1 | Active | 1131 | 1st Planetary Stage Carrier Bearing Issue | Particle Counter | Particle Counter | 2024-04-11 |  | 3 | 4/11/24 - Recommend full gearbox borescope with focus on the 1st planetary stage within 3 months from 4/11/24. | CMSGBXBORE | 3332165 | Closed | Ready to Schedule |  |  |  | Case In Progress | Case In Progress | -45393
Traverse 1 | Resolved | 1131 |  | Warning | Main Bearing | 2022-02-18 |  | 5 |  | Monitor | [5 empty] | 4/1 - warning level direct vibration, no faults in FFT, 5/10 - hitting alarm threshold, similar to 1126 and 1128, suspecting high winds? 6/20 - offline, feeder outage, 8/4 - still offline, 11/18 - trend much lower when back online, temps good |  |  | -44610
Traverse 1 | Active | 1131 | Potential Main Bearing Issue | Sweep | Main Bearing | 2022-03-21 |  | 2 | 3/1/23 - roller micropitting, raceway standstill marks and micropitting, claim rejected | Longterm Watchlist | 3101539 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -44641
Traverse 1 | Resolved | 1132 |  | Warning | Main Bearing | 2022-10-25 | [12 empty] | -44859
Traverse 1 | Active | 1133 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-04 |  | 5 | 9/14/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 2987702 | Ready to Schedule | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -44777
Traverse 1 | Resolved | 1134 |  | Warning | Main Bearing | 2022-01-27 |  | 6 |  | Monitor |  |  |  |  | 2022-06-20 | 4/1 - not enough data, 5/10 - latch reset when possible, 6/20 - latch reset |  |  | 144
Traverse 1 | Active | 1134 | Potential 1st Planetary Stage Bearing Issue | Sweep | 1st Planetary Stage | 2023-07-28 |  | 2 | 5/15/24 - Possibly consider to reborescope soon due to step change from 15,000 cummulitive to 32,000mg of debri. Slight progression of defect signature in spectrum as well. 7/28/23 - Recommend full gearbox borescope with focus on 1st planetary stage within 1 month from 7/28/23. | Longterm Watchlist | 3163468 | Closed | Closed |  |  |  |  | Case In Progress | -45135
Traverse 1 | Resolved | 1138 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-06-27 |  | 3 | Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3148647 | Closed | Closed |  | 2024-09-18 |  |  | Defect Confirmed - Repair Complete | 449
Traverse 1 | Resolved | 1139 |  | Alarm | Helical High Speed Stage | 2022-02-12 |  | 5 |  | Monitor | [5 empty] | 4/1 - stage 3 HSS dnwind shows damage to the outer race with clear harmonics, no data past 2/13/22, 5/10 - data restored, missing keyphasor speed, 6/20 - speed available on 6/8, likely damage to HSS GS outer race, limited progression, 8/23 - potential blunting, HSS GS ORBP harmonics present at high frequencies |  |  | -44604
Traverse 1 | Resolved | 1141 |  | Alarm | 1st Planetary Stage | 2022-03-30 |  | 3 |  | Monitor | [5 empty] | 4/1 - Sudden increase in stage 1 direct vibration, FFT shows well-developed harmonics, indicating damage to stage 1 bearings and/or stage 1 ring gear. Timebase shows successive impacts ~15g. Monitor for progression, prepare to inspect, 5/10 - sudden decrease as well, post elevated vibration, the FFT shows shaft harmonics, 6/20 - monitor for increases, 8/4 - no progression, 11/18 - no progression |  |  | -44650
Traverse 1 | Resolved | 1141 |  | Warning | Main Bearing | 2022-06-16 |  | 6 |  | Monitor | [5 empty] | 6/20 - increase to warning setpoint after outage on 5/21, mystery peak at 268.625X in high res spectrum, ORBP signal shows slight increase along with direct trend, temps look normal, 8/4 - now hitting alarm threshold, temps are normal |  |  | -44728
Traverse 2 | Resolved | 2002 |  | Warning | Main Bearing | 2021-12-29 |  | 6 |  | Monitor | [5 empty] | 5/11 - elevated main bearing vibration, no fault indication in FFT, 8/2 - signal has reduced from the warning setpoint, 11/14 - continued reduction in trend, no faults on FFT, 12/6 - no concerning signals, consider resolving |  |  | -44559
Traverse 2 | Resolved | 2002 | Generator Inboard ORBP | Warning | Generator Inboard | 2024-02-12 |  | 3 | 3/22/24 - Warranty approved, turbine down until gen bearing replacement. 2/12/24 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | Repair Pending | 3298675 | Closed | Closed |  | 2024-04-05 |  |  | Defect Confirmed - Repair Complete | 53
Traverse 2 | Resolved | 2003 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-08-03 |  | 3 |  | CMSTRBLSHOOT | 3168955 | Closed | Closed |  | 2023-09-05 |  |  | Defect Confirmed - Repair Complete | 33
Traverse 2 | Resolved | 2003 | Keyphasor Issue | Warning | 2nd Planetary Stage | 2022-02-12 |  | 6 |  | CMSTRBLSHOOT | 3038404 | Cancelled | Closed |  |  | 5/11 - low concern, 6/21 - potential damage to S2 PS BRG rollers, 8/2 - Keyphasor issue, no shaft speed after 6/11, no FFT either, instrumentation case created, 11/14 - WO still Ready to Schedule, 12/6 - |  |  | -44604
Traverse 2 | Resolved | 2003 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-10-26 |  | 4 | Follow Keyphasor Guide to check for common issues | CMSTRBLSHOOT | 3038404 | Cancelled | Cancelled | [5 empty] | -44860
Traverse 2 | Resolved | 2003 | Data Locked Up? | Instrumentation | Other | 2023-11-27 | 2023-12-05 | 5 | 11/27/23 - No data producing, rebooted monitor. | Monitor | [8 empty] | -45257
Traverse 2 | Active | 2003 | Timken Main Bearing Rolling Element Issue | Sweep | Main Bearing | 2024-07-08 |  | 2 | 9/9/24 - Turbine faulted out and placed into DNR. 7/28 - Not much damage seen, continue to monitor. 7/8/24 - Recommend borescoping this main bearing within 2 weeks from 7/8/24 with focus on rollers. | Repair Pending | 3380282 | Closed | Closed |  |  |  |  | Case In Progress | -45481
Traverse 2 | Resolved | 2004 |  | Change 1 | 1st Planetary Stage | 2022-06-21 |  | 6 |  | Monitor | [5 empty] | 8/2 - step change in DEI Structural signal after outage in early June, fault peak at S1 PC BRG GS rollers, minor harmonics, 11/14 - no progression, 12/6 - no progression |  |  | -44733
Traverse 2 | Resolved | 2005 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-09-26 |  | 3 | 9/26/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3197103 | Closed | Closed |  | 2023-11-27 |  |  | Defect Confirmed - Repair Complete | 62
Traverse 2 | Resolved | 2005 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-10-27 |  | 4 | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 3038846 | Closed | Closed |  | 2023-08-31 |  |  | True Positive | 308
Traverse 2 | Active | 2005 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-06-20 |  | 3 | 6/20/24 -CMS monitor is not receiving a speed signal from the generator encoder. Please inspect PEM and encoder using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3369425 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45463
Traverse 2 | Resolved | 2006 |  | Change 1 | 1st Planetary Stage | 2022-08-02 |  | 6 |  | Monitor | [5 empty] | 8/2 - direct signal shows recent peaks just below warning setpoint, potential bearing damage, 11/14 - no progression on trend, potential roller damage on S1 GS CB, 12/6 - NP |  |  | -44775
Traverse 2 | Resolved | 2006 |  | Warning | Helical High Speed Stage | 2022-03-25 |  | 6 |  | Monitor | [5 empty] | 3/29 - 1.5g peak at 2X GMF, misalignment, 6/21 - peak on 3/25 has reduced to normal levels, misalignment is clear in both S3 and on DE Gen, 11/14 - normal levels on trend, misalignment still clear, 12/6 - trend has flatlined, consider resolving if no progression |  |  | -44645
Traverse 2 | Resolved | 2007 |  | Warning | Main Bearing | 2022-05-02 |  | 3 |  | Monitor | 3045565 | Closed | Closed |  |  | 5/11 - increase to warning setpoint in direct signal, FFT shows elevated vibration floor, potential roller damage, temps are not elevated relative to neighbors, 6/21 - 2-4g impacts in the timebase, direct signal peaks are sustained above the alarm setpoint, temps look ok, 8/2 - no major progression, direct remains elevated, temps look normal, 8/24 - reduce to cat 2, 10/27 - missing data between 9/1 and now, resatisfied warning event, 11/14 - slight reduction in trend since data returned, elevated temperature compared to neighbors, increasing Severity to 3 and submitted CMSMB WO, 12/6 - temps good, trend continues to be elevated, potential roller damage seen on FFT |  |  | -44683
Traverse 2 | Active | 2007 | Potential Main Bearing Inner Race Issue | Sweep | Main Bearing | 2024-09-30 | 2024-11-14 | 6 | 9/30/24 - Possible signs of MB inner race damage, check back in two weeks. | Monitor | [7 empty] | Case In Progress | -45565
Traverse 2 | Resolved | 2009 | Generator Inboard ORBP | Warning | Generator Inboard | 2024-06-14 |  | 2 | 6/14/24 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact CMSEngineers_OSW@invenergyllc.com for support | CMSGENB | 3367446 | Closed | Closed |  | 2024-08-05 |  |  | Defect Confirmed - Repair Complete | 52
Traverse 2 | Resolved | 2010 |  | Alarm | Helical High Speed Stage | 2022-02-19 |  | 6 |  | Monitor | [5 empty] | 3/29 - stage 3 FFT shows potential HSS bearing issue, 8/2 - no progression, HSS bearing fault harmonics are still present, 11/14 - clear HSS misalignment indicators on FFT, no progression on trend, 12/6 - NDE bearing shows ORBP indicator on FFT |  |  | -44611
Traverse 2 | Resolved | 2010 |  | Warning | Main Bearing | 2022-06-10 |  | 3 |  | Monitor | [5 empty] | 6/21 - main bearing is following site trend for increasing main bearing vibrations, 3g impacts in the timebase, limited evidence of damage in the FFT, 11/14 - trend has steadily declined to below the warning threshold, FFT indicates roller fault, temps good, 12/6 - trend has intensified again, 1-4g impacts on timebase, temps in line with neighbors, increase to Cat 3 |  |  | -44722
Traverse 2 | Resolved | 2011 | Potential Sensor Issue | Instrumentation | Main Bearing | 2022-05-11 |  | 5 | Check sensor mounting | CMSTRBLSHOOT | 2930145 | Closed | Closed |  |  | 5/11 - check sensor mounting |  |  | -44692
Traverse 2 | Resolved | 2011 |  | Warning | Main Bearing | 2022-03-17 |  | 6 |  | Check Main Bearing Sensor | [5 empty] | 3/29 - 0.01g peak at 1X shaft speed, 5/11 - main bearing direct has been elevated for operating life, suspected poor mounting. Adding instrumentation case to check sensor, 8/24 - signal reduced to below warning threshold, 11/14 - continued reduction of trend, 12/6 - more trend reduction, potential roller fault, temps good, reduce to Cat 1 |  |  | -44637
Traverse 2 | Resolved | 2013 | Generator Outboard Accelerometer Open Circuit | Instrumentation | Generator Outboard | 2024-01-22 |  | 5 | 1/22/24 - Generator outboard accelerometer dropping in and out of an open circuit, possible loose accelerometer. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3257220 | Closed | Closed |  | 2024-02-01 |  |  | Defect Confirmed - Repair Complete | 10
Traverse 2 | Resolved | 2021 |  | Warning | Helical High Speed Stage | 2022-07-13 |  | 6 |  | Monitor | [5 empty] | 8/2 - gear mesh misalignment, 11/14 - no progression on trend, 12/6 - increase of pinion fault sidebands between 2x and 3x GMF, 4x GMF high amp on FFT |  |  | -44755
Traverse 2 | Resolved | 2021 |  | Warning | Generator Outboard | 2022-03-18 |  | 3 | [7 empty] | 11/14 - significant increas to above warning level and clear ORBP damage from FFT, 20g impacts on timebase, watch for increase in timebase, 12/6 - increase in Gen NDE ORBP to above alarm setpoint in last 2 weeks, continued impacts of ~20g, assigned WO to RMORRIS |  |  | -44638
Traverse 2 | Resolved | 2026 |  | Warning | 2nd Planetary Stage | 2022-05-01 |  | 6 |  | Monitor | [5 empty] | 5/11 - low concern, 6/21 - potential damage to S2 PS BRG rollers or S2 PC BRG ORBP, 8/2 - peak in GFED signal, 11/14 - no progression on timebase, S2 ring fault indicators, 12/6 - S2 RG sidebands around 3x and 4x GMF are nearing GMF amps |  |  | -44682
Traverse 2 | Active | 2027 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255317 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 2 | Resolved | 2028 |  | Alarm | 2nd Planetary Stage | 2022-02-18 |  | 6 |  | Check Gearbox CMS Sensors | [5 empty] | 3/29 - extremely elevated stage 2 vibration without any indicators in the FFT, likely sensor issue, instrumentation case created, 11/14 - No progression, 12/6 - HSS 1x freq elevated, S1 PC GS possible IRBP damage, |  |  | -44610
Traverse 2 | Resolved | 2028 | Potential Sensor Issue | Instrumentation | 2nd Planetary Stage | 2022-03-29 |  | 5 | Check sensor mounting | CMSTRBLSHOOT | 2904261 | Closed | Closed | [5 empty] | -44649
Traverse 2 | Resolved | 2028 | Generator Inboard ORBP | Alarm | Generator Inboard | 2023-06-23 |  | 2 | 8/3/23 - CMS levels have increased further, recommend this turbine be shut down until repair. 7/25/23 - Bearing signature has greatly increased in amplitude over the past month, recommend derating this turbine to 50%. | CMSGENB | 3146247 | Closed | Closed |  | 2023-09-10 |  |  | Defect Confirmed - Repair Complete | 79
Traverse 2 | Active | 2029 | Main Bearing Inner + Outer Race Issue | Sweep | Main Bearing | 2024-09-30 |  | 2 | 9/30/24 - Please borescope with focus on MB outer race within 2 weeks from 9/30/24. | CMSMBBORE | 3439132 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45565
Traverse 2 | Resolved | 2030 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-02 |  | 4 | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2971143 | Closed | Closed |  |  |  |  | True Positive | -44775
Traverse 2 | Resolved | 2030 | IONet Issue | Instrumentation | CMS Monitor | 2023-11-09 |  | 3 | 11/9/23 - CMS monitor not receiving power signal, please perform toolbox download to CBM card. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3223562 | Closed | Closed |  | 2023-11-28 |  |  | Defect Confirmed - Repair Complete | 19
Traverse 2 | Resolved | 2032 |  | Warning | 2nd Planetary Stage | 2022-08-04 |  | 5 |  | Monitor | [5 empty] | 8/24 - S2 PC BRG GS ORBP, 11/14 - no progression on trend, misalignment indicators on FFT, 12/6 - no progression |  |  | -44777
Traverse 2 | Resolved | 2033 |  | Instrumentation | CMS Monitor | 2022-08-02 |  |  | Replace 60M100 monitor | SVC-CMSINSTALL | 2971123 |  | Cancelled |  | 2022-08-24 | 8/24 - monitor left state |  |  | 22
Traverse 2 | Resolved | 2033 | Stage 3 Pinion Damage | Alarm | 2nd Planetary Stage | 2022-02-19 |  | 5 |  | CMSHSS | 2998455 | Closed | Closed |  |  | 3/29 - Stage 2 FFT shows planet fault sidebands throughout with 0.1g bearing fault peaks, Stage 3 FFT shows pinion fault sidebands surrounding 2X GMF, around 0.2g. Stage 3 direct remains at warning setpoint, 5/11 - Stage 1 envelop suggests damage to stage 1 carrier GS rollers, Stage 2 evelope suggests damage to stage 2 carrier GS, stage 3 still shows pinion fault sidebands, limited progression overall, continue to monitor, 5/24 - AEP wants to file a warranty claim, recommended waiting for particle counter install due to lack of obvious progression, 6/21 - No data collected after 6/4, retrieved configuration and pushed firmware update, misalignment at coupler, 2X GMF surrounded by mesh fault sidebands, data flow restored, 8/24 - prominent pinion fault sidebands, impacts in the timebase, 11/14 - pinion fault sidebands still prominent, no progression in amplitude, 12/6 - S2 SER PG GFR1 SR1 consistently popping above alarm level |  |  | -44611
Traverse 2 | Active | 2033 | Potential 1st/2nd Stage Planetary Gearing Issue | Warning | 1st Planetary Stage | 2023-06-09 |  | 2 | CMS indicates possible damage to this turbine’s 1st stage planetary gearing. Particle counts are also rising. Recommend full gearbox borescope within 1 month from 6/9/23. | Repair Pending | 3141239 | Closed | Closed |  |  |  |  | Case In Progress | -45086
Traverse 2 | Resolved | 2036 |  | Warning | Helical High Speed Stage | 2022-02-19 |  | 6 |  | Monitor | [5 empty] | 3/29 - FFT shows peaks at HSS cage and ORBP, near 0.08g, 5/11 - potential misalignment, 6/21 - envelope has a peak at HSS GS roller fault frequency, limited progression, 11/14 - no progression, 12/7 - Roller fault has gone away on FFT, a couple of Large pinion fault sidebands on S3 2x GMF, NP on trends |  |  | -44611
Traverse 2 | Resolved | 2036 |  | Warning | Main Bearing | 2022-03-27 |  | 6 |  | Monitor | [5 empty] | 3/29 - Main Bearing direct shows increases nearing alarm setpoint, 8/2 - low concern, reduce to cat 1, 11/14 - No progression, temps look good compared to neighbors |  |  | -44647
Traverse 2 | Active | 2037 | 1st Planetary Stage Bearing Issue | Sweep | 1st Planetary Stage | 2024-07-18 |  | 3 | 9/3/24 - Moderate damage to PBs and planetary gearing, est. replacement early Q3 2025. 7/18/24 - Recommend full gearbox borescope with focus on the 1st planetary stage within 3 months from 7/18/24. | Longterm Watchlist | 3388454 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45491
Traverse 2 | Active | 2038 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255317 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 2 | Resolved | 2039 |  | Warning | 2nd Planetary Stage | 2022-08-16 |  | 6 |  | Monitor | [5 empty] | 8/24 - potential early S2 planet fault, 11/14 - trend amp still- elevated, more sidebands in between 1x and 2x GMFs, 12/7 - NP |  |  | -44789
Traverse 2 | Resolved | 2040 |  | Warning | 2nd Planetary Stage | 2022-06-17 |  | 5 |  | Monitor | [5 empty] | 6/21 - potential damage to S2 PC BRG GS ORBP, 8/3 - S3 shows HSS RS raceway faults with harmonics, amplitude is still low, tower offline since 6/27 for PMT, 11/14 - No progression since tower has come back online, 12/7 - a few spikes on DEI Intermediate trend to near warning, Direct looks good |  |  | -44729
Traverse 2 | Resolved | 2042 |  | Warning | Main Bearing | 2022-03-20 |  | 6 |  | Monitor | [5 empty] | 3/29 - peaks to warning setpoint following outage, all shaft harmonics present, 8/3 - direct signal below the warning setpoint, still peaking throughout July, 8/24 - reduce to cat 1, 11/14 - shaft harmonics gone on FFT, amps on trend show no progression, 12/7 - temps good |  |  | -44640
Traverse 2 | Active | 2045 | 1st Planetary Stage Bearing Issues | Sweep | 1st Planetary Stage | 2023-10-25 |  | 2 | 7/8/24 - S1 Planet Bearing damage, particle indentation on S1 planet + sun gears and on S2 carrier bearings. and gearing. Estimated replacement Q2-3 2025. 5/20/24 - CMS indicates stage 1 IRBP issue. Signature is seen 6 months ago but has progressed. The particle counter shho past month cumnuluative FE mass is at 15,00mg. 10/25/23 - With EOW borescopes coming up, just an alert to focus on the 1st planetary stage carrier + planetary bearings on this turbine in particular. | Longterm Watchlist | 3353269 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45224
Traverse 2 | Resolved | 2049 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-08-02 |  | 4 | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2971144 | Closed | Closed |  |  |  |  | True Positive | -44775
Traverse 2 | Active | 2049 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-11-09 |  | 3 | 11/9/23 - CMS monitor is not receiving a speed signal from the generator encoder. Please inspect PEM and encoder using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3223563 | Ready to Schedule | Ready to Schedule | [5 empty] | -45239
Traverse 2 | Resolved | 2051 |  | Instrumentation | CMS Monitor | 2022-03-29 |  | 5 | Check monitor power supply or reboot | CMSTRBLSHOOT | 2947966 | Cancelled | Cancelled | [5 empty] | -44649
Traverse 2 | Resolved | 2052 |  | Warning | 2nd Planetary Stage | 2022-04-01 |  | 6 |  | Monitor | [5 empty] | 5/11 - potential stage 2 carrier GS damage, 6/21 - S2 PC BRG GS ORBP damage, limited progression, 11/14 - sidebands in between 1x and 2x S2 GMF beginning to show up, 12/5 - S2 Ring Fault sidebands look to be elevating around 3x GMF, trend steady, HSS harmonics presence |  |  | -44652
Traverse 2 | Resolved | 2053 |  | Warning | Main Bearing | 2022-05-02 |  | 6 |  | Monitor | [5 empty] | 5/11 - increase to warning setpoint in direct signal, temps are not elevated relative to neighbors, 6/21 - trend follows site main bearing increase trend, 8/3 - signal reduced to normal levels, 8/24 - reduce to cat 1, 11/14 - .25-1g impacts on timebase, temps ok, 12/7 - trend reduction continues, potential roller damage on FFT, temps good |  |  | -44683
Traverse 2 | Active | 2054 | 1st Stage Planetary Bearing/Gearing Issue | Sweep | 1st Planetary Stage | 2024-07-02 |  | 3 | 10/11/24 - Turbine DNR'd due to gearing defect. 9/3/24 - Moderate damage to PBs and planetary gearing, est. replacement early Q2 2025. 7/2/24 - Recommend full gearbox borescope with focus on 1st stage within 3 months from 7/2/24. | Final Report Needed | 3376543 | Closed | Closed |  | 2024-10-11 |  |  | Defect Confirmed - Repair Complete | 101
Traverse 2 | Active | 2055 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255321 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 2 | Active | 2060 | NTN Main Bearing Rolling Element Issue | Sweep | Main Bearing | 2024-02-12 | 2024-10-30 | 6 | 4/15/24 - Parking mark/damage on inner race, CMS will continue to monitor. 2/12/24 - Recommend main bearing borescope with focus on main bearing rolling elements at next opportunity, please upload results to HUVR. | Monitor | 3298693 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45334
Traverse 2 | Resolved | 2062 | Keyphasor Issue | Keyphasor Issue | Keyphasor | 2022-08-02 |  | 5 | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2971145 | Closed | Closed | [5 empty] | -44775
Traverse 2 | Resolved | 2062 |  | Processor Hardware Diagnostic Event | CMS Monitor | 2022-06-21 |  |  | Replace 60M100 monitor | SVC-CMSINSTALL | 2947967 |  | Cancelled |  | 2022-08-24 | 8/24 - monitor left state |  |  | 64
Traverse 2 | Resolved | 2062 | Keyphasor Issue/Monitor Netcom | Instrumentation | Keyphasor | 2023-04-17 |  | 3 | Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3113549 | Closed | Closed |  | 2023-11-30 |  |  | Defect Confirmed - Repair Complete | 227
Traverse 2 | Active | 2063 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255323 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 2 | Active | 2063 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-09-25 |  | 3 | 9/25/24 - CMS monitor is not receiving a speed signal from the generator encoder. Please inspect PEM and encoder using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3436017 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45560
Traverse 2 | Resolved | 2067 |  | Warning | 2nd Planetary Stage | 2022-06-17 |  | 6 |  | Monitor | [5 empty] | 6/21 - low concern, 8/3 - slightly noisy floor in high res spectrum, envelope indicates damage to S2 PC BRG GS rollers and ORBP, limited harmonics, SER ring fault has been elevated for full operating life, 11/17 - limited progression, 12/7 - no progression |  |  | -44729
Traverse 2 | Active | 2068 | 1st Stage Planetary Bearing Issue | Particle Counter | 1st Planetary Stage | 2024-10-14 |  | 3 | 10/14/24 - Recommend full gearbox borescope within 1-2 months from 10/14/24 with focus on the 1st planetary stage. | CMSGBXBORE | 3445603 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45579
Traverse 2 | Resolved | 2069 |  | Warning | Main Bearing | 2022-02-18 |  | 6 |  | Monitor | [5 empty] | 3/29 - peaks to warning setpoint between outages, very low vibration in FFT, 5/11 - vibration settles at warning setpoint, monitor, 6/21 - vibration signal continues to reduce, temps are relatively low, 12/7 - temps good |  |  | -44610
Traverse 2 | Resolved | 2069 | Gearbox 1 Sensor Issue | Instrumentation | 1st Planetary Stage | 2022-10-26 |  | 4 | Swap sensor 1 and 2 and check voltage. Replace sensor 1 if voltage remains around -5V | CMSTRBLSHOOT | 3038407 | Closed | Closed |  |  |  |  | True Positive | -44860
Traverse 2 | Active | 2070 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255324 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 2 | Resolved | 2071 |  | Warning | 2nd Planetary Stage | 2022-04-23 |  | 6 |  | Monitor | [5 empty] | 5/11 - stage 2 ring and planet fault sidebands, very low. Potential damage to stage 2 bearings, 8/3 - low concern, 11/17 - increased harmonics in between S2 1x and 2x GMF, misalignment likely, 12/7 - sidebands starting to pop up in between 1x and 2x S2 GMF |  |  | -44674
Traverse 2 | Resolved | 2074 |  | Warning | Helical High Speed Stage | 2022-03-28 |  | 6 |  | Monitor | [5 empty] | 3/29 - Stage 3 FFT show elevated GMF 1X and 2X peaks, limited sidebands, 5/11 - no progression, low concern, 6/21 - likely misalignment, 11/17 - trend amp is decreasing slightly, 2x GMF amp has increased, 12/7 - no progression |  |  | -44648
Traverse 2 | Resolved | 2079 | CMS Monitor Netcom/IONet Issue | Instrumentation | Main Bearing | 2023-03-15 |  | 3 | Keyphasor\Netcom issue appears fixed, CBM download to turbine controller is now needed. | CMSTRBLSHOOT | 3099336 | Closed | Closed |  | 2023-06-13 |  |  | Defect Confirmed - Repair Complete | 90
Traverse 2 | Resolved | 2080 | Potential Sensor Issue | Instrumentation | 1st Planetary Stage | 2022-06-21 |  | 5 | Check sensor mounting | CMSTRBLSHOOT | 2947987 | Closed | Closed | [5 empty] | -44733
Traverse 2 | Active | 2080 | Oil Particle Communication Issue | Particle Counter | Particle Counter | 2023-10-05 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3202568 | Ready to Schedule | Ready to Schedule | [5 empty] | -45204
Traverse 2 | Resolved | 2081 |  | Warning | 2nd Planetary Stage | 2022-05-02 |  | 6 |  | Monitor | [5 empty] | 5/11 - low concern, 6/21 - potential damage to S2 PC BRG GS ORBP, 8/3 - limited progression, 11/17 - limited progression |  |  | -44683
Traverse 2 | Resolved | 2084 | Gearbox 1 Sensor Issue | Instrumentation | 1st Planetary Stage | 2022-08-02 |  | 5 | Check sensor harness for shorts | CMSTRBLSHOOT | 2971146 | Closed | Closed |  |  | 8/2 - originally keyphasor issue, no longer and issue, changed to sensor 1 shorted wiring troubleshoot |  |  | -44775
Traverse 2 | Resolved | 2084 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-04-17 |  | 3 | Please inspect gen encoder and keyphasor PEM using attached guide. | CMSTRBLSHOOT | 3113559 | Closed | Closed |  | 2023-05-19 |  |  | Defect Confirmed - Repair Complete | 32
Traverse 2 | Active | 2084 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-09-25 |  | 3 | 9/25/24 - CMS monitor is not receiving a speed signal from the generator encoder. Please inspect PEM and encoder using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3436021 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45560
Traverse 2 | Resolved | 2086 |  | Warning | 2nd Planetary Stage | 2022-06-20 |  | 6 |  | Monitor | [5 empty] | 6/21 - S2 PC BRG GS ORBP fault and harmonics peaks, 8/3 - limited progression, minor impacts in the timebase, 11/17 - periodic spikes in DEI Intermediate trend above threshold, but immediate drop to baseline, HSS shaft harmonics, Stage 2 Sun 1x and 2x peaks shown on FFT, 12/7 - Spike up to near alarm again |  |  | -44732
Traverse 2 | Resolved | 2089 | Generator Inboard ORBP | Warning | Generator Inboard | 2024-07-12 |  | 3 | 7/12/24 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact CMSEngineers_OSW@invenergyllc.com for support | CMSGENB | 3385124 | Closed | Ready to Schedule |  | 2024-08-14 |  |  | Defect Confirmed - Repair Complete | 33
Traverse 2 | Resolved | 2093 | 1st Planetary Stage Accelerometer | Instrumentation | 1st Planetary Stage | 2023-09-12 |  | 5 | 9/12/23 - First planetary stage + high speed stage accelerometers are reading a short circuits at ~0.1V, please investigate wirings and connections, replace sensors if needed.​ | CMSTRBLSHOOT | 3189931 | Closed | Ready to Schedule |  | 2023-12-06 |  |  | Defect Confirmed - Repair Complete | 85
Traverse 2 | Resolved | 2095 | Data Locked Up? | Instrumentation | Keyphasor | 2023-11-27 | 2023-12-05 | 3 | 11/27/23 - No data producing, rebooted monitor. | Monitor | [8 empty] | -45257
Traverse 2 | Active | 2097 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-04-17 |  | 3 | 7/8/24 -Bently now reading a speed signal but no power signal, please download to turbine's CBM card in toolbox. Contact abarndt@invenergy.com for support and validation. 4/17/23 - Please inspect gen encoder and keyphasor PEM using attached guide. | CMSTRBLSHOOT | 3113551 | Ready to Schedule | Ready to Schedule |  |  |  |  | Defect Confirmed - Repair Complete | -45033
Traverse 2 | Resolved | 2098 | Oil Particle Counts Rising | Instrumentation | Particle Counter | 2024-01-17 |  | 6 | 1/17/24 - Particle counts rising, continue to monitor. | Monitor | [7 empty] | Case In Progress | -45308
Traverse 2 | Resolved | 2100 |  | Warning | Main Bearing | 2022-02-18 |  | 6 |  | Monitor | [5 empty] | 3/29 - main bearing direct hit alarm sepoint, timebase shows occational impacts, 6/21 - signal reduced to below warning setpoint, 11/14 - slight increase in signal after coming back online, periodic 2g impacts on timebase, lots of shaft harmonics on FFT, temps good, 12/7 - trend has been consistently above warning, 12x shaft harmonic elevated, temps good |  |  | -44610
Traverse 2 | Active | 2101 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255325 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 2 | Resolved | 2102 |  | Warning | 2nd Planetary Stage | 2022-04-24 |  | 5 |  | Monitor | [5 empty] | 5/11 - early stage 2 bearing damage, 6/21 - potentially carrier or planet damage, limited progression, 8/3 - S2 PS BRG IRBP, potentially carrying ring fault sidebands, 8/24 - mode 3 shows PS BRG IRBP progression, 11/17 - HSS harmonics present, 12/7 - trend steady even after being offline |  |  | -44675
Traverse 2 | Resolved | 2104 | Data Locked Up? | Instrumentation | Other | 2023-11-27 | 2023-12-05 | 5 | 11/27/23 - No data producing, rebooted monitor. | Monitor | [8 empty] | -45257
Traverse 2 | Active | 2105 | DE Gen Bearing Damage | Alarm | Generator Inboard | 2024-10-17 |  | 2 | 10/17/24 Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly 10/17/24 - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact CMSEngineers_OSW@invenergyllc.com for support | CMSGENB | 3447601 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45582
Traverse 2 | Resolved | 2109 | Keyphasor Issue | Keyphasor Issue | Keyphasor | 2022-08-02 |  | 5 | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2971147 | Closed | Closed | [5 empty] | -44775
Traverse 2 | Resolved | 2109 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2023-04-17 |  | 3 | CMS monitor stopped producing data, please ensure CMS monitor is lit up and communication channel is plugged into Port A on the monitor. | CMSTRBLSHOOT | 3113555 | Closed | Closed |  | 2023-04-17 |  |  | Defect Confirmed - Repair Complete | 0
Traverse 2 | Resolved | 2109 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-11-27 |  | 3 | 11/27/23 - Keyphasor signal not working properly, appears to be reading .62V. Please inspect PEM and gen encoder, ensure keyphasor communication is plugged into KPH2 port. | CMSTRBLSHOOT | 3229007 | Closed | Closed |  | 2024-02-09 |  |  | Defect Confirmed - Repair Complete | 74
Traverse 2 | Resolved | 2110 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-11-03 |  | 3 | 11/3/23 - CMS monitor is not receiving a speed signal from the generator encoder. Please inspect PEM and encoder using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3219100 | Closed | Closed |  | 2023-11-27 |  |  | Defect Confirmed - Repair Complete | 24
Traverse 2 | Active | 2110 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255328 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 2 | Resolved | 2112 | Keyphasor Issue | Keyphasor Issue | Keyphasor | 2022-08-02 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2971148 | Cancelled | Cancelled | [5 empty] | -44775
Traverse 2 | Resolved | 2114 |  | Alarm | 2nd Planetary Stage | 2022-03-21 |  | 6 |  | Monitor | [5 empty] | 3/29 - stage 2 FFT shows bearing fault peaks, max 0.1g, 5/11 - no progression, stage 2 planet bearing fault peaks remain, 8/24 - limited progression reduce to cat 1, 11/17 - S2 PB IRBP peak on FFT, limited progression , 12/7 - NP on trend, FFT doesn't show fault indicators |  |  | -44641
Traverse 2 | Resolved | 2116 |  | Warning | Helical High Speed Stage | 2022-02-19 |  | 5 |  | Monitor | [5 empty] | 3/29 - stage 3 pinion fault sidebands in FFT, max 0.1g, 5/11 - potential HSIS bearing damage, inner race, 6/21 - potential damage to HSIS IRBP, 8/5 - pinion fault sidebands most prominent in mode 3, 8/24 - limited progression, 11/17 - increase in pinion fault sidebands between 2x and 3x S3 GMF, trend has reduced, 12/7 - More pinion sideband progression, but trend has lowered to near the warning setpoint |  |  | -44611
Traverse 2 | Resolved | 2116 |  | Warning | Main Bearing | 2022-04-27 |  | 5 |  | Monitor | [5 empty] | 5/11 - increase to warning setpoint in direct signal, temps are slightly elevated relative to neighbors, 6/21 - temps remain slightly elevated, likely damage to ORBP, 8/5 - following site trend for FAG bearings, 8/24 - signal reduced, reduce to cat 2, 11/17 - continued reduction in MB signal, 12/7 - NP on trend, temps good |  |  | -44678
Traverse 2 | Resolved | 2116 | Generator Inboard ORBP | Sweep | Generator Inboard | 2023-04-26 |  | 3 | Recommend inspecting the bearing noise + grease quality, recommend ensuring that the accelerometer is not loose as well. | Monitor | 3116872 | Closed | Closed |  | 2023-07-30 |  |  | Defect Confirmed - Repair Complete | 95
Traverse 2 | Resolved | 2117 |  | Alarm | Helical High Speed Stage | 2022-02-18 |  | 3 |  | CMSHSS | 3054899 | Closed |  |  |  | 3/29 - stage 3 pinion fault sidebands around 2X GMF, 5/11 - no progression, 6/21 - S2 PC BRG GS ORBP. potential HSS damage, 8/5 - misalignment in S3 mesh, limited progression, 11/17 - limited progression, 12/7 - Major intensification of pinion fault sidebands around 2x S3 GMF, increasing to Cat 3 and submitting WO |  |  | -44610
Traverse 2 | Active | 2117 | NTN Main Bearing Rolling Element Issue | Sweep | Main Bearing | 2024-07-18 |  | 2 | 8/5/24 - Derated to 50%. 7/18/24 - Recommend borescoping this main bearing within 2 weeks from 7/18/24 with focus on outer race and rollers. | Repair Pending | 3388466 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45491
Traverse 2 | Resolved | 2118 | Keyphasor Issue | Keyphasor Issue | Keyphasor | 2022-08-02 |  |  | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2971149 | Closed | Closed | [5 empty] | -44775
Traverse 2 | Resolved | 2118 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2023-11-09 |  | 3 | 11/9/23 - CMS monitor appears netcom, please inspect that CMS monitor is powered and ethernet cable is plugged into port A. | CMSTRBLSHOOT | 3222835 | Closed | Closed |  | 2023-12-11 |  |  | Defect Confirmed - Repair Complete | 32
Traverse 2 | Resolved | 2119 |  | Warning | Main Bearing | 2022-02-18 |  | 5 |  | Monitor | [5 empty] | 3/29 - Main bearing direct hit warning setpoint, harmonics present in FFT, 5/11 - direct continues to peak at or below the warning setpoint, 6/21 - direct remains largely below the warning setpoint, no significant progression in sub-signals, 8/24 - tower offline since 8/9, 11/17 - still offline |  |  | -44610
Traverse 2 | Resolved | 2120 |  | Warning | Helical High Speed Stage | 2022-02-18 |  | 5 |  | Monitor | [5 empty] | 3/29 - low level pinion fault sidebands, 5/11 - low amplitude HSS bearing fault frequencies in the envelopem 6/21 - potential HSIS GS roller damage, 8/5 - misalignment in S3 mesh, HSIS GS rollers and IRBP damage, increase to cat 2, 11/17 -potential HSIS GS IRBP fault, 12/7 - NP on trend, |  |  | -44610
Traverse 2 | Resolved | 2121 |  | Warning | 2nd Planetary Stage | 2022-03-19 |  | 6 |  | Monitor | [5 empty] | 3/29 - potential stage 2 bearing issue, 5/11 - stage 2 carrier GS outer race fault frequency with harmonics, 6/21 - Stage 2 sensor may be picking up S1 Carrier vibration, 8/5 - limited progression, no shaft speed since 6/16, instrumentation case created, 11/17 - still no shaft speed, 12/7 - still nothing |  |  | -44639
Traverse 2 | Resolved | 2121 | Keyphasor Issue | Keyphasor Issue | Keyphasor | 2022-08-02 |  | 5 | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2971150 | Closed | Closed | [5 empty] | -44775
Traverse 2 | Resolved | 2121 | 2nd Planetary Stage Accelerometer | Instrumentation | 2nd Planetary Stage | 2024-04-15 |  | 5 | 4/15/24 - ​2nd planetary stage accelerometer is reading a short circuit, please inspect wirings and connections, replace sensor if needed. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3333958 | Closed | Closed |  | 2024-04-22 |  |  | Defect Confirmed - Repair Complete | 7
Traverse 2 | Resolved | 2122 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2022-06-21 |  | 3 | Check monitor power supply or reboot | CMSTRBLSHOOT | 2947969 | Closed | Closed |  | 2024-01-02 |  |  | Defect Confirmed - Repair Complete | 560
Traverse 2 | Active | 2122 | Oil Particle Communication Issue | Instrumentation | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255330 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 2 | Resolved | 2123 | Keyphasor Issue | Keyphasor Issue | Keyphasor | 2022-08-02 |  | 4 | Troubleshoot keyphasor per attached guide | CMSTRBLSHOOT | 2971151 | Closed | Closed |  |  |  |  | True Positive | -44775
Traverse 2 | Resolved | 2125 |  | Warning | 2nd Planetary Stage | 2022-03-24 |  | 6 |  | Monitor | [5 empty] | 3/29 - 0.01g ring fault sidebands, 5/11 - dense sidebands at GMFs, potential stage 2 carrier GS outer race damage, 6/21 - S1 PC BRG GS roller damage indicated by Stage 1 envelope, S2 PC BRG GS ORBP fault and harmonics are still present, no progression, 11/17 - no progression, 12/7 - NP |  |  | -44644
Traverse 2 | Resolved | 2126 |  | Warning | 2nd Planetary Stage | 2022-03-19 |  | 6 |  | Monitor | [5 empty] | 3/29 - 0.01g ring fault sidebands, 5/11 - potential stage 2 carrier GS outer race damage, 6/21 - noisy vibration floor in high res FFT, 8/5 - Ring fault sidebands are present, S2 PC BRG GS ORBP, 11/17 - no progression, 12/7 - slight reduction on trend |  |  | -44639
Traverse 2 | Resolved | 2128 |  | Warning | 2nd Planetary Stage | 2022-02-18 |  | 6 |  | Monitor | [5 empty] | 3/29 - stage 2 FFT indicated damage to the planet gear bearing, 5/11 - no progression, 11/17 - likely S2 PG BRG IRBP damage |  |  | -44610
Traverse 2 | Resolved | 2129 |  | Warning | 1st Planetary Stage | 2022-03-26 |  | 5 |  | Monitor | [5 empty] | 3/29 - Potential stage 1 carrier damage to rollers, stage 3 FFT indicates damage to HSS DnWind, 5/11 - no significant progression, 6/21 - misalignment, 8/5 - limited progression in stage 1, S3 indicates HSIS RS rollers and raceways, 11/17 - S1 indicates S1 PC GS roller damage, S1 & S3 show limited progresion |  |  | -44646
Traverse 2 | Resolved | 2129 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-04-26 |  | 3 | 4/26/23 - CMS monitor is not receiving a speed signal from the generator encoder. Please inspect PEM and encoder using attached guide. Reach out to abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3116894 | Closed | Closed |  | 2023-12-12 |  |  | Defect Confirmed - Repair Complete | 230
Traverse 2 | Active | 2131 | 1st Planetary Stage Accelerometer Issue | Instrumentation | 1st Planetary Stage | 2024-09-03 |  | 4 | 9/3/24 - 1st planetary stage accelerometer is currently reading a short, please investigate wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | 3413695 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45538
Traverse 2 | Resolved | 2134 |  | Warning | 2nd Planetary Stage | 2022-04-24 |  | 6 |  | Monitor | [5 empty] | 5/11 - elevated vibration floor in high res fft, potential carrier GS outer race damage, 6/21 - no progression, 8/5 - S2 PC BRG GS ORBP, |  |  | -44675
Traverse 2 | Resolved | 2138 |  | Warning | Helical High Speed Stage | 2022-02-19 |  | 5 |  | Monitor | [5 empty] | 3/29 - FFT shows peaks at 1X and 2X shaft speed, 5/11 - damage to HSS GS inner and outer races is aparent, monitor for progression, 6/21 - likely damage to HSS GS Rear raceways, elevate to cat 2, 8/5 - limited progression, monitor timebase for increasing vibration floor, 11/17 - timebase shows vibration floor around 2g, continue to monitor |  |  | -44611
Traverse 2 | Resolved | 2139 |  | Warning | 2nd Planetary Stage | 2022-03-26 |  | 6 |  | Monitor | [5 empty] | 3/29 - low concern, 6/21 - no progression, 11/17 - slight progression of Ring fault sidebands on S2 1x, 2x, 3x GMFs |  |  | -44646
Traverse 2 | Resolved | 2140 |  | Warning | 2nd Planetary Stage | 2022-03-24 |  | 6 |  | Monitor | [5 empty] | 3/29 - elevated shaft harmonics in stage 2 FFT may indicate bearing issue, 5/11 - stage 2 carrier GS outer race harmonincs, 11/17 - potential damage to S2 RG IRBP |  |  | -44644
Traverse 2 | Resolved | 2140 |  | Warning | Main Bearing | 2022-03-15 |  | 6 |  | Monitor | [5 empty] | 3/29 - peaks to warning setpoint, 5/11 - elevated main bearing direct signal, 8/5 - occasional 2-5g impacts, temps look normal, 11/17 - slight decline in trend amplitude, potential roller damage, temps look good |  |  | -44635
Traverse 2 | Resolved | 2142 |  | Warning | Main Bearing | 2022-07-19 |  | 5 |  | Monitor | [5 empty] | 8/5 - site trend for elevated FAG bearing vibration, 8/24 - temps are normal, 11/17 - return to warning level after return to service, no fault indicators on FFT, slightly elevated temps, increase to Cat 2 |  |  | -44761
Traverse 3 | Resolved | 3002 |  | Warning | Generator Outboard | 2022-03-10 |  | 6 |  | Monitor | [5 empty] | 3/30 - 20g impacts in timebase, 2g peak at ORBP for NDE bearing on 3/10, return to normal levels after, 6/22 - reduce to cat 1, 8/5 - low concern, 11/17 - impacts on timebase down to 5g, 12/8 - NP |  |  | -44630
Traverse 3 | Active | 3002 | Oil Particle Communication Issue | Particle Counter | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255342 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 3 | Active | 3003 | Oil Particle Communication Issue | Particle Counter | Particle Counter | 2024-01-17 |  | 4 | 1/17/2024 - Particle counter does not appear to be communicating. Please ensure communication cabling is secured from the AP2200 to the DM4500 and hardware is powered. Contact abarndt@invenergy.com or PISupport@invenergy.com for support. | GBXPARTTS | 3255343 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45308
Traverse 3 | Resolved | 3005 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-01-30 |  | 4 | ​Please inspect keyphasor PEM and ensure connection is made into KPH2 port instead of KPH1. Please contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3073769 | Closed | In Progress |  | 2023-02-27 |  |  | Defect Confirmed - Repair Complete | 28
Traverse 3 | Resolved | 3005 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-07-03 |  | 3 | 7/3/24 - CMS monitor not receiving speed signal. Please investigate keyphasor circuit using attached guide. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3379477 | Ready to Schedule | Ready to Schedule |  | 2024-08-22 |  |  | Defect Confirmed - Repair Complete | 50
Traverse 3 | Resolved | 3011 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-09-08 |  | 3 | 9/8/23 - Please troubleshoot keyphasor using attached guide. | CMSTRBLSHOOT | 3187802 | Closed | Ready to Schedule |  | 2023-09-19 |  |  | Defect Confirmed - Repair Complete | 11
Traverse 3 | Resolved | 3012 |  | Warning | 2nd Planetary Stage | 2022-05-01 |  | 5 |  | Monitor | [5 empty] | 5/12 - Stage 2 envelope FFT indicates damage to stage 2 planet bearing rollers. Harmonics are already present, suggesting some progression. 6/22 - potential damage to S2 PC BRG ORBP, limited progression, 8/5 - minor ring fault sidebands, limited evidence of bearing damage, reduce to cat 2, 8/26 - elevated IMS, 11/17 - ring fault sidebands have progressed slightly, 12/8 - NP |  |  | -44682
Traverse 3 | Resolved | 3012 |  | Warning | Main Bearing | 2022-11-16 |  | 5 |  | Monitor | [5 empty] | 11/17- MB signal has steadily increased to above the warning threshold, potential ORBP damage seen on FFT, temps in line with neighbors, 12/8 - trend has stopped increasing but is still near warning setpoint, temps in line with neighbors |  |  | -44881
Traverse 3 | Resolved | 3013 |  | Warning | Main Bearing | 2022-03-24 |  | 6 |  | Monitor | [5 empty] | 3/30 - increase to warning setpoint following outage, low concern, 5/12 - vibration has reduce to normal operation, 6/22 - potential roller damage, 8/5 - normal temps, continue to monitor, 8/26 - signal reduced, 11/17 - no change in signal, 12/8 - temps and signals look good |  |  | -44644
Traverse 3 | Resolved | 3015 |  | Alarm | 1st Planetary Stage | 2022-03-19 |  | 5 |  | Monitor | [5 empty] | 3/30 - Stage 1 direct shows sudden increase in vibration along with well-developed shaft harmonics throughout the FFT, Stage 2 FFT indicates damage to the planet gear bearing, 5/12 - stage 1 direct has returned to normal levels, harmonics are significantly reduced, mild damage to stage 1 carrier GS has likely been sustained, 6/22 - S2 PS BRG roller damage may be present, 8/5 - reduce to cat 2, limited progression, 11/17 - 5g impacts on timebase, no progression on trend, 12/8 - NP |  |  | -44639
Traverse 3 | Resolved | 3016 | Main Bearing High Direct | Warning | Main Bearing | 2023-08-16 | 2023-10-16 | 3 | 8/16/23 - Main bearing direct appears elevated and temperature is deviating from neighboring turbines. Recommend coverplate removal and inspection of grease. | Monitor | 3174955 | Closed | Closed |  |  |  |  | Case In Progress | -45154
Traverse 3 | Active | 3016 | Possible Main Bearing ORBP Damage | Sweep | Main Bearing | 2024-09-16 | 2024-10-16 | 3 | 9/16/24 - Possible main bearing outer race issue, please borescope with focus on MB outer race within 1 month from 9/16/24. | Repair Pending | 3427580 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45551
Traverse 3 | Resolved | 3017 |  | Alarm | Helical High Speed Stage | 2022-02-19 |  | 5 |  | Monitor | [5 empty] | 3/30 - Stage 3 pinion fault sidebands around 2X GMF, 5/12 - sidebands and harmonics around 2X GMF in stage 3 with mild modulation in the timebase waveform, envelope FFT shows fault peak and harmonics for HSS GS outer race, Stage 2 envelope FFT indicates damage to stage 2 carrier, unclear which bearing, 6/22 - HSS GS ORBP, modulation in timebase, potentially some pinion damage. S2 PS BRG IRBP, S2 PC BRG RS roller damage, monitor for progression, 8/26 - Increase in S3 Pinion fault sidebands, likely mild progression, increase to cat 2, 11/17 - Progressed to above threshold again, progression of S3 pinion fault sidebands indicating further pinion damage, 12/8 - slight progression of S3 pinion fault sidebands, looks liuke trend just has an elevated normal operating amp, |  |  | -44611
Traverse 3 | Resolved | 3018 |  | Alarm | Helical High Speed Stage | 2022-09-27 |  | 2 |  | GE HSS Check | [5 empty] | 9/27 - GE alert, step change in S3 SER signal after outage, low amplitude pinion fault suggest minor pinion damage, 11/17 - trend has returned back to normal levels, potential HSS misalignment suggested by elevated to 2x GMF, 12/8 - trend shows return to normal operation |  |  | -44831
Traverse 3 | Resolved | 3018 | Main Bearing Accelerometer Short Circuit | Instrumentation | Main Bearing | 2023-07-06 |  | 5 | ​Main bearing sensor is reading a short circuit. Please inspect wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | 3153356 | Closed | Ready to Schedule |  | 2024-02-23 |  |  | Defect Confirmed - Repair Complete | 232
Traverse 3 | Resolved | 3020 |  | Warning | 2nd Planetary Stage | 2022-02-10 |  | 6 |  | Monitor | [5 empty] | 3/30 - stage 2 peak on 2/11 reduced after outage, stage 3 FFT shows pinion fault sidebands, max 0.275g, maintained after outage, stage 3 timebase shows modulation, 5/12 - stage 2 envelope shows fault frequency peaks and harmonics for stage 2 planet bearing inner race. Likely damage to stage 3 pinion gear, 6/22 - tower offline since 4/22, waiting on slip ring inspection, 12/8 - now online again, no data before 12/2/22, |  |  | -44602
Traverse 3 | Resolved | 3020 |  | Warning | Main Bearing | 2022-02-11 |  | 6 |  | Monitor | [5 empty] | 3/30 - low concern, 6/22 - tower offline for slip ring, 8/26 - tower online, signal reduced, 12/8 - no data before 2/11 |  |  | -44603
Traverse 3 | Resolved | 3021 |  | Warning | 2nd Planetary Stage | 2022-02-18 |  | 6 |  | Monitor | [5 empty] | 3/30 - stage 2 FFT shows shaft harmonics along with potential damage to stage 2 planet gear bearings, 5/12 - stage 3 instrumentation, stage 2 shows evidence of planet bearing inner race damage, 12/8 - NP |  |  | -44610
Traverse 3 | Resolved | 3021 | Gearbox 3 Sensor Replacement | Instrumentation | Helical High Speed Stage | 2022-05-12 |  | 4 | Replace sensor | CMSTRBLSHOOT | 2930896 | Closed | Closed |  | 2023-02-22 | 8/5 - sensor needs to be replaced, setting work order to Ready to Schedule |  | True Positive | 286
Traverse 3 | Resolved | 3021 | Generator Inboard Bearing Issue | GE Alert | Generator Inboard | 2023-03-09 |  | 2 | • Inspect bearing grease and re-grease if needed • Test for an electrical short across bearing insulation ring and troubleshoot if necessary • Ensure accelerometer is securely mounted and isolated • Record any abnormal sounds during operation (before and after greasing, if possible) • Submit a warranty claim with the inspection results to pursue bearing replacement if needed | CMSGENB | 3095074 | Closed | Closed |  | 2023-05-31 |  |  | Defect Confirmed - Repair Complete | 83
Traverse 3 | Resolved | 3021 | HSS Brake Drag/Pinion Issue | Warning | Helical High Speed Stage | 2024-10-21 |  | 3 | 10/21/24 - Please perform an auditory and visual inspection of the high speed shaft, gears, and bearings: -check pinion and gear for any tooth damage -record a video if there is any noise while running -check gearbox oil filter for shavings, take a picture if present - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact CMSEngineers_OSW@invenergyllc.com for support | CMSHSS | 3448866 |  | Ready to Schedule |  | 2024-11-07 |  |  | Defect Confirmed - Repair Complete | 17
Traverse 3 | Resolved | 3023 |  | Warning | Helical High Speed Stage | 2022-02-19 |  | 6 |  | Monitor | [5 empty] | 3/30 - low level pinion fault sidebands, 5/12 - some bearing fault harmonics at higher frequencies in mode 3, 6/22 - elevated 2X indicates misalignment, potential HSS GS roller damage |  |  | -44611
Traverse 3 | Resolved | 3025 |  | Warning | Main Bearing | 2022-08-01 |  | 5 |  | Monitor | [5 empty] | 8/5 - main bearing shows steady increase from normal operation. Temps looks normal in TADs, 8/26 - occasional 1-4g impacts in the timebase, temps remain low, 12/8 - no data since 11/28, |  |  | -44774
Traverse 3 | Resolved | 3028 |  | Warning | Main Bearing | 2022-08-23 |  | 6 |  | Monitor | [5 empty] | 8/26 - increase to warning setpoint, following site average, remains at warning threshold, occastional impacts, temps are low, 10/26 - additional warning, trend continues to increase |  |  | -44796
Traverse 3 | Resolved | 3028 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-01-30 |  | 4 | Please inspect keyphasor PEM and ensure connection is made into KPH2 port instead of KPH1. Please contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3073775 | Closed | Closed |  | 2023-04-16 |  |  | Defect Confirmed - Repair Complete | 76
Traverse 3 | Resolved | 3028 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-07-25 |  | 4 | CMS monitor not receiving speed signal. Please investigate keyphasor circuit using attached guide. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3161687 | Closed | Ready to Schedule |  | 2023-09-11 |  |  | Defect Confirmed - Repair Complete | 48
Traverse 3 | Resolved | 3028 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-09-25 |  | 3 | 9/25/24 - CMS monitor not receiving speed signal. Please investigate keyphasor circuit using attached guide. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3436023 | Ready to Schedule | Ready to Schedule |  | 2024-10-10 |  |  | Defect Confirmed - Repair Complete | 15
Traverse 3 | Resolved | 3029 |  | Warning | 2nd Planetary Stage | 2022-03-10 |  | 6 |  | Monitor | [5 empty] | 3/30 - shaft harmonics may indicate damage to the planet gear, 5/12 - likely inner race and roller damage to stage 2 planet bearings, 6/22 - S2 PS BRG IRBP, 8/26 - limited progression, S3 mesh misalignment, 12/8 - slight reduction in trend after coming back onlne |  |  | -44630
Traverse 3 | Resolved | 3030 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-03-28 |  | 2 | Please troubleshoot keyphasor using attached guide. | CMSTRBLSHOOT | 3103797 | Closed | Closed |  | 2023-04-06 |  |  | Defect Confirmed - Repair Complete | 9
Traverse 3 | Resolved | 3031 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-07-25 |  | 4 | CMS monitor not receiving speed signal. Please investigate keyphasor circuit using attached guide. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3161691 | Closed | Ready to Schedule |  | 2024-10-20 |  |  | Defect Confirmed - Repair Complete | 453
Traverse 3 | Resolved | 3033 |  | Warning | 2nd Planetary Stage | 2022-11-12 |  | 6 |  | Monitor | [5 empty] | 11/18 - S2 GMF harmonics and ring fault sidebands present, S1 FFT shows potential roller damage to S1 PC GS, 12/8 - small increase in sidebands in between GMFs especially 3x and 4x |  |  | -44877
Traverse 3 | Resolved | 3035 |  | Warning | Main Bearing | 2022-03-13 |  | 5 |  | Monitor | [5 empty] | 3/30 - Main bearing direct hitting alarm setpoint, occasional shaft harmonics in FFT, potential sensor mounting issue? 5/12 - vibration somewhat reduced, 6/22 - signal has reduced monitor for progression, 8/5 - temps look normal, 12/8 - continued reduction in trend, temps slightly elevated ~3C, increase to Cat 2 |  |  | -44633
Traverse 3 | Resolved | 3039 |  | Alarm | Helical High Speed Stage | 2022-02-19 |  | 6 |  | Monitor | [5 empty] | 3/30 - 2g peak at 2X GMF - likely misalignment, 6/22 - potential damage to HSS GS IRBP, 8/26 - limited progression, 12/8 - trend has reduced, BRG damage not evident anymore |  |  | -44611
Traverse 3 | Resolved | 3042 |  | Instrumentation | CMS Monitor | 2022-03-30 |  |  | Wait | [5 empty] | 2022-06-22 |  |  |  | 84
Traverse 3 | Resolved | 3042 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2024-01-11 |  | 4 | 1/11/24 - Please ensure communication cabling is plugged into Port A and ensure that CMS monitor is powered. | CMSTRBLSHOOT | 3336516 | Closed | Ready to Schedule |  | 2024-05-17 |  |  | Defect Confirmed - Repair Complete | 127
Traverse 3 | Resolved | 3044 |  | Instrumentation | CMS Monitor | 2022-03-30 |  |  | Wait | [5 empty] | 2022-06-22 |  |  |  | 84
Traverse 3 | Resolved | 3045 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-03-28 |  | 2 | Please troubleshoot keyphasor using attached guide. | CMSTRBLSHOOT | 3103796 | Closed | Ready to Schedule |  | 2024-02-23 |  |  | Defect Confirmed - Repair Complete | 332
Traverse 3 | Resolved | 3046 |  | Alarm | 2nd Planetary Stage | 2022-02-10 |  | 5 |  | Monitor | [5 empty] | 3/30 - potential early stage 2 bearing issue, 5/12 - likely damage to stage 2 planet bearings inner race, 6/22 - limited progression, potential damage to S2 PC BRG ORBP as well, 12/8 - NP |  |  | -44602
Traverse 3 | Resolved | 3046 |  | Warning | Main Bearing | 2022-06-17 |  | 5 |  | Monitor | [5 empty] | 6/22 - main bearing direct shows increasing trend since late April, 4g impacts in the timebase, likely damage to ORBP, temps are slightly elevated relative to neighbors, 8/5 - vibration remains elevated, no fault indicated, site trend, 8/26 - reduce to cat 2, 12/8 - trend is back to normal level, temps ok |  |  | -44729
Traverse 3 | Resolved | 3050 |  | Warning | 2nd Planetary Stage | 2022-06-18 |  | 6 |  | Monitor | [5 empty] | 6/22 - potential damage to S2 PC BRG GS ORBP, 8/5 - limited progression, 8/26 - tower offline since 8/9, 12/8 - trend above warning and sometimes alarm setpoint since coming back online, no bad indicators on FFT |  |  | -44730
Traverse 3 | Resolved | 3053 |  | Warning | Helical High Speed Stage | 2022-03-10 |  | 5 |  | Monitor | [5 empty] | 8/5 - elevated main bearing vibration and temperature, 5g impacts, CMSMB recommended, |  |  | -44630
Traverse 3 | Resolved | 3053 |  | Warning | Main Bearing | 2022-08-01 |  | 3 |  | CMSMBBORE | 3041390 | Cancelled | Cancelled |  |  | 8/5 - increase in main bearing vibration, temps look normal, 8/26 - tower offline since 8/11, 10/28 - tower back online with high amplitude spike and Direct alarm, no fault indicators in the spectrum, 11/18 - high amplitudes have persisted, roller damage now evident on FFT, elevated temps, already a WO for CMSMBBORE on EAM, 12/8 - trend still elevated, temps good |  |  | -44774
Traverse 3 | Resolved | 3055 |  | Warning | Main Bearing | 2022-08-05 |  | 3 |  | CMSMB | 2973165 | Cancelled | Cancelled |  |  | 8/5 - elevated main bearing vibration and temperature, 5g impacts, CMSMB recommended, 12/8 - temps ok now, occasional 3g impacts on timebase, trend below warning, potential blunting |  |  | -44778
Traverse 3 | Active | 3055 | 2nd Stage Planetary Bearings | Particle Counter | 2nd Planetary Stage | 2024-10-14 |  | 3 | 10/14/24 - Recommend full gearbox borescope within 1-2 months from 10/14/24 with focus on the 2nd planetary stage. | CMSGBXBORE | 3445600 | Ready to Schedule | Ready to Schedule |  |  |  |  | Case In Progress | -45579
Traverse 3 | Resolved | 3056 |  | Warning | 2nd Planetary Stage | 2022-03-12 |  | 6 |  | Monitor | [5 empty] | 3/30 - shaft harmonics present, 0.05g, 5/12 - potential planet bearing damage, inner race and rollers, 6/22 - potential damage to S2 PC BRG GS ORBP, 8/26 - tower offline since 8/17, concerning increase in GFR SR1, 11/18 - occassional peaks over warning point continue, no change on FFT, 12/8 - NP |  |  | -44632
Traverse 3 | Resolved | 3059 |  | Warning | Helical High Speed Stage | 2022-02-19 |  | 6 |  | Monitor | [5 empty] | 3/30 - 1.3g peak at 2X, 5/12 - potential damage to HSS UpWind rollers, 6/22 - no progression, 12/8 - NP |  |  | -44611
Traverse 3 | Resolved | 3060 |  | Warning | Main Bearing | 2022-08-01 |  | 6 |  | Monitor | [5 empty] | 8/5 - potential damage to ORBP, temps look normal, elevated main bearing vibration, 8/26 - additional warning event, temps look ok, 11/18 - additional alarm, but no real progression since Aug, temps good, looks like roller damage, 12/9 - signal trending downwards, temps good |  |  | -44774
Traverse 3 | Resolved | 3061 |  | Instrumentation | CMS Monitor | 2022-03-30 |  | 5 | Check power supply and reboot | CMSTRBLSHOOT | 2948412 | Cancelled | Cancelled |  |  | 6/22 - monitor has been lost comms since 3/30, 12/7 - comms returned WO still ready to schedule |  |  | -44650
Traverse 3 | Resolved | 3061 | 1st Stage Planetary Accelerometer Short Circuit | Instrumentation | 1st Planetary Stage | 2023-01-30 |  | 4 | ​1st planetary stage accelerometer is reading a short circuit, recommend replacing sensor. Please contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3073895 | Closed | Closed |  | 2023-02-22 |  |  | Defect Confirmed - Repair Complete | 23
Traverse 3 | Resolved | 3061 | Gearbox sensor 1 and 2 issue | Instrumentation | 1st Planetary Stage | 2024-05-14 |  | 5 | 5/14/24 - CMS shows -22 voltage for earbox sensor 1 and 2. | CMSTRBLSHOOT | 3350921 | Closed | Ready to Schedule |  | 2024-05-21 |  |  | Case In Progress | 7
Traverse 3 | Resolved | 3062 |  | Change 1 | Helical High Speed Stage | 2022-04-21 |  | 6 | [7 empty] | 6/22 - misalignment, |  |  | -44672
Traverse 3 | Resolved | 3062 |  | Warning | Generator Outboard | 2022-03-10 |  | 6 |  | Monitor | [5 empty] | 3/30 - spike to warning setpoint after outage, 20g impacts, 2.5g peak at ORBP, reduced to lower operation following, 6/22 - 5g impacts, low concern, 12/9 - still 5g impacts |  |  | -44630
Traverse 3 | Resolved | 3065 |  | Warning | Helical High Speed Stage | 2022-04-27 |  | 5 |  | Monitor | [5 empty] | 5/12 - Envelope FFT shows clean fault frequency peak and harmonics at HSS GS Rear inner race, 6/22 - tower has been offline since 5/25, tower online, inconsisten KPH readings, 11/18 - jusmp in amp after coming back online but then immediate dip back below warning point, no FFT bc of keyphasor issue, 12/8 - NP on trend, no FFT |  |  | -44678
Traverse 3 | Resolved | 3065 | Keyphasor Issue | Instrumentation | Keyphasor | 2022-03-30 |  | 4 | Since inspection was made, the CMS monitor appears netcom and connection cannot be established. Please inspect monitor lights are turned on and appears to be operating correctly, also inspect that network connection is plugged into Port A. | CMSTRBLSHOOT | 2904427 | Closed | Closed |  |  | 6/22 - tower is offline, wait to come back online to troubleshoot keyphasor, 12/7 - tower back online |  | True Positive | -44650
Traverse 3 | Active | 3065 | Generator Outboard ORBP | Warning | Generator Outboard | 2023-10-09 |  | 3 | 10/9/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings | Monitor | 3204137 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45208
Traverse 3 | Resolved | 3067 |  | Warning | Main Bearing | 2022-08-01 |  | 6 |  | Monitor | [5 empty] | 8/5 - elevated main bearing vibration, temps are low, 12/9 - main bearing trend is subsiding, temps good |  |  | -44774
Traverse 3 | Resolved | 3069 |  | Warning | 1st Planetary Stage | 2022-11-13 |  |  |  | Monitor | [5 empty] | 11/18 - huge spike in trend on 11/13, but nothing before or after that, nothing concerning on FFT, monitor for progression |  |  | -44878
Traverse 3 | Resolved | 3071 | Gearbox sensor 1 issue | Instrumentation | 1st Planetary Stage | 2024-05-14 |  | 5 | 5/14/24 - CMS shows bias volatge of -22, for gearbox sensor 1 | CMSTRBLSHOOT | 3350919 | Closed | Ready to Schedule |  |  |  |  | Case In Progress | -45426
Coyote Ridge | Active | A01 | Potential S1 Issue | Sweep | 1st Planetary Stage | 2024-04-18 | 2025-03-02 | 4 | 4/18/24 - CMS shows potential S1 issue (potentially IRBP, seeing 3 order apart signature), continue to monitor via CMS until progression | Monitor | [7 empty] | Case In Progress | -45400
Jayhawk | Active | A03 | Potential S2 Issue | Sweep | 2nd Planetary Stage | 2024-07-10 |  | 5 | 7/10/24 - potential s2 issue, could just be noisy bearing | Monitor | [7 empty] | Case In Progress | -45483
Coyote Ridge | Active | A03 | Generatr Inboard ORBP/IRBP | Alarm | Generator Inboard | 2025-01-22 |  | 3 | 1/22/25 - CMS indicates Generator Inboard issue. | CMSGENB | 3498335 |  | Ready to Schedule |  |  |  |  | Case In Progress
Jayhawk | Resolved | A04 |  | Instrumentation | 1st Planetary Stage | 2022-06-13 |  |  | Check gearbox sensors 1 and 2 for open wiring | CMSTRBLSHOOT | 2944789 | Closed | Closed |  | 2022-08-08 |  |  |  | 56
Coyote Ridge | Active | A06 | S1 Planetary stage IRBP/ORBP Issue | Sweep | 1st Planetary Stage | 2024-04-18 | 2025-03-01 | 2 | 4/18/24 - CMS indicates S1 Planetary IRBP/OBRP issue. Please perform full gearbox borescope/inspection. | Repair Pending | 3335527 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45400
Jayhawk | Resolved | A08 | Main Bearing BS2X | Sweep | Main Bearing | 2024-06-13 | 2024-12-07 | 2 | 11/19/24 - replaced 7/22/24 - metal chunks found in inspection port, turbine DNR'd. 6/13/24 - Main bearing BS2X signature present. Request main bearing borescope | Final Report Needed | 3346160 | Closed | Closed | Q3-Q4 2024 |  |  |  | Defect Confirmed - Repair Complete
Jayhawk | Active | A08 | Main Bearing potential IBRP/ORBP issue | Sweep | Main Bearing | 2024-05-08 |  | 2 | 7/23/24- main bearing failed and going on DNR list. request reborescope in 2-3 months following progression. 5/7/24 - Normal wear and tear. Continue to monitor for progression via CMS. 5/3/24 - CMS indicates potential main bearing inner race damage | Monitor | 3346160 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -45420
Coyote Ridge | Resolved | A2 | SKF Main Bearing Issue | Sweep | Main Bearing | 2023-02-27 |  | 2 | (DNR) Failed main bearing, replaced, update new MB config | Final Report Needed | 3087678 | Closed | Closed |  | 2023-05-26 | 3/17 - https://invenergy.huvrdata.app/projects/5475 |  | Defect Confirmed - Repair Complete | 88
Coyote Ridge | Resolved | A5 | HSS Bearing Damage | Warning | Helical High Speed Stage | 2021-10-26 |  | 5 |  | Monitor | [5 empty] | 2/9 - Borescope didn't find any damage, continue to run, 3/22 - 2X-3X sidebands, 5g floor in timebase, 5/23 - offline for failed PMT, 6/15- back online, potential misalignment, 7/7 - direct signal now hitting alarm threshold, potential HSS bearing damage, elevating to cat 2, 8/15 - high res spectrum shows mesh misalignment and HSS bearing fault harmonics, 9/26 - 5g average in the timebase, early S2 Ring fault, 11/29 - offline for about a month and trend has lowered after coming back online, 5g avg on timebase still, 2x GMF on S3 SER Pinion fault elevated with sidebands between 2x and 3x GMF |  | Case In Progress | -44495
Asa Branca | Resolved | ASB04-12 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2025-05-29 |  | 3 | 5/29/25 - CMS Monitor is netcom, please ensure monitor is power and communications is plugged into Port A | CMSTRBLSHOOT | SR 00218
Asa Branca | Resolved | ASB04-11 | Generator Outboard IRBP | Warning | Generator Outboard | 2026-01-06 |  | 3 | 1/6/26 - NDE generator bearing is showing signs of damage in the CMS data. Please inspect generator bearing noise and grease quality, take photos of grease and videos of noise for review. Add grease to both bearings. | CMSGENB | SR 00431
Asa Branca | Active | ASB04-20 | High Speed Stage Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2024-11-07 |  | 4 | 11/7/24 - O acelerômetro do estágio de alta está lendo como circuito aberto. Por favor investigar os enrolamentos e as conexões. Trocar o sersor se for necessário. | CMSTRBLSHOOT | SS00044
Asa Branca | Resolved | ASB05-03 | Planetary Bearing Issue | Alarm | 1st Planetary Stage | 2024-09-01 | 2025-03-01 | 2 | 9/1/24 - Late stage planetary bearing issue, gearbox likely needs to be replaced within the next 6 months. | Repair Pending
Asa Branca | Resolved | ASB06-03 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2025-05-29 |  | 3 | 5/29/25 - CMS Monitor is netcom, please ensure monitor is power and communications is plugged into Port A | CMSTRBLSHOOT | SR 00219
Asa Branca | Active | ASB05-01 | Planetary Bearing Issue | Alarm | 1st Planetary Stage | 2026-07-08 |  |  | Solicitamos uma boroscopia da gearbox da AB05-01 com foco nos rolamentos traseiros dos planetas. | CMSTRBLSHOOT | SS00708
Asa Branca | Resolved | ASB05-10 | Main Bearing ORBP | Alarm | Main Bearing |  |  | 2 | 6/10/25 - DNR requested due to borescope results | Repair Pending
Asa Branca | Resolved | ASB06-03 | Main Bearing ORBP | Alarm | Main Bearing |  |  | 2 |  | CMSMBBORE
Asa Branca | Active | ASB05-03 | High Speed Stage Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2026-01-27 |  | 5 | 1/27/26 - O acelerômetro do estágio de alta está lendo como circuito aberto. Por favor investigar os enrolamentos e as conexões. Trocar o sersor se for necessário. | CMSTRBLSHOOT | SR 00449
Asa Branca | Resolved | ASB06-13 | Planetary Bearing Issue | Alarm | 1st Planetary Stage |  |  | 2 | 4/15/25 - May 2023 borescope showed damages to planetary bearings, recommend re-borescope to show current extent of damages. Due to timeline of the defect, also recommending that we derate this turbine to 50%. 9/1/24 - Late stage planetary bearing issue, gearbox likely needs to be replaced within the next 6 months. | Repair Pending | SS00189
Asa Branca | Resolved | ASB07-05 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2025-02-27 |  | 3 | 2/27/25 - CMS Monitor is not currently collecting data, please ensure montiro is powered and ethernet is plugged into Port A
Asa Branca | Resolved | ASB06-13 | HSIS Stage Accelerometer Issue | Instrumentation | Helical Intermediate Stage | 2024-11-07 |  | 4 | 11/7/24 - O acelerômetro de estágio intermediário está lendo como circuito aberto. Por favor, investigue os enrolamentos e conexões. Troque o seridor, se necessário. | CMSTRBLSHOOT | SS00045
Asa Branca | Active | ASB05-19 | HSS Pinion Issue | Alarm | Helical High Speed Stage | 2026-07-27 |  |  | Prováveis marcas de parada | Monitor
Asa Branca | Active | ASB06-08 | Potential Planetary Gearing Damage/Standstill Marking | Warning | 1st Planetary Stage | 2025-05-29 |  | 6 | 5/29/25 - Planetary stage is showing signs of potential planetary gearing marking after long outage. Continue to monitor
Asa Branca | Active | ASB07-02 | Planetary Bearing Issue | Alarm | 1st Planetary Stage | 2025-05-07 |  | 2 | 5/7/25 - Recommend borescoping gearbox with focus on planetary stage within 3 months from 5/7/25. Please also take photos of oil filter inspection or sump sweep and attach these photos to HUVR report. | CMSGBXBORE | SR 00200
Asa Branca | Resolved | ASB07-11 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-06-30 |  | 4 | 6/30/25 - Recommend borescoping gearbox with focus on planetary stage within 3 months from 6/30/25. | CMSGBXBORE | SR 00266
Asa Branca | Resolved | ASB07-13 | HSIS Accelerometer Issue | Instrumentation | Helical Intermediate Stage | 2026-01-27 |  | 5 | 1/27/26 - O acelerômetro de estágio intermediário está lendo como circuito aberto. Por favor, investigue os enrolamentos e conexões. Troque o seridor, se necessário. | CMSTRBLSHOOT | SR 00450
Asa Branca | Active | ASB07-03 | Planetary Stage Accelerometer issue | Instrumentation | 1st Planetary Stage | 2026-07-27 |  |  | Solicitamos uma inspeção nos sensores dos estágio planetário. | CMSTRBLSHOOT | SS00745
Asa Branca | Active | ASB07-05 | HSS Accelerometer Open Circuit | Instrumentation | Helical High Speed Stage | 2025-11-10 |  | 4 | 11/10/25 - HSS accelerometer is currently reading an open circuit, please inspect wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | SR 00396
Asa Branca | Resolved | ASB08-06 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2025-10-22 |  | 3 | 10/22/25 - CMS Monitor is netcom, please ensure monitor is power and communications is plugged into Port A | CMSTRBLSHOOT
Asa Branca | Active | ASB07-05 | Planetary Stage Accelerometer issue | Instrumentation | 1st Planetary Stage | 2025-12-30 |  | 3 | 12/30/25 - Planetary Stage accelerometer is currently reading an open circuit, please inspect wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | SR 00428
Chapada I | Resolved | JOA09-01 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2023-04-01 | 2025-04-10 | 2 | 9/24/24 - Signature has been arounds since ~April 2023, recently showed signs of damage to sun gear. Turbine derated to 50% on 9/20/24. Turbine is on Essentia MCE list for 2025 | Longterm Watchlist
Chapada II+III | Resolved | AUG03-05 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-06-02 |  | 2 | 6/2/25 - CMS indicates potential damage to the gearbox's planetary stage. Recommend full gearbox borescope within 2 weeks from 6/2/25 with focus on the planetary stage. | CMSGBXBORE | SR 00230
Chapada II+III | Resolved | AUG03-06 | 1st Planetary Stage Sensor Open Circuit | Instrumentation | 1st Planetary Stage | 2024-10-11 |  | 4 | 10/11/24 - Planetary stage sensor open circuit, please investigate wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | SS00099 |  | TBD |  |  |  |  | Case In Progress
Chapada II+III | Active | AUG03-04 | Main Bearing ORBP | Warning | Main Bearing | 2025-05-14 |  | 3 | 5/14/2025 - Main bearing outer race issue detected, recommend borescope with focus on outer raceway within 3 months from 5/14/25. | CMSMBBORE
Chapada II+III | Active | AUG03-05 | HSIS Accelerometer Issue | Instrumentation | Helical Intermediate Stage | 2025-07-25 |  | 3 | 7/25/25 - HSIS sensor is giving erroneous readings, recommend inspecting wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | SR 00280
Chapada II+III | Active | AUG03-05 | 1st Planetary Stage Accelerometer Issues | Instrumentation | 1st Planetary Stage | 2026-04-28 |  | 3 | 4/28/26 - 1st planetary stage sensor is currently reading an open circuit, recommend inspecting wiring and connections. Replace sensor if needed, | CMSTRBLSHOOT | SR 00568
Chapada II+III | Active | AUG03-06 | Planetary Bearing Issue
Chapada II+III | Resolved | AUG04-06 | HSS DnWind Rear IRBP | Warning | Helical High Speed Stage | 2024-10-11 |  | 5 | 5/26/26 - HSS bearing energy increasing, likely needing bearing replacement within 6-9 months from 10/11/24 - HSS Bearing issue, continue to monitor for progression. | Monitor | [7 empty] | Case In Progress | -45576
Chapada II+III | Active | AUG03-15 | HSS DnWind Rear IRBP | Warning | Helical High Speed Stage | 2025-12-30 |  | 6 | 12/30/25 - Awaiting signature progression.
Chapada II+III | Resolved | AUG04-03 | High Speed Stage Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2026-01-27 |  | 5 | 1/27/26 - High speed stage sensor is currently showing an short circuit, please investigate wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | SR 00451
Chapada I | Active | JOA09-02 | HSIS Accelerometer Short Circuit | Instrumentation | Helical Intermediate Stage | 2024-12-31 |  | 4 | 12/31/24 - HSIS sensor is currently reading a short circuit. Please inspect wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | SS00101
Chapada II+III | Active | AUG04-02 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-11-04 |  | 3 | 11/4/25 - Turbine is showing signs on planetary bearing spalling recommend full gearbox borescope inspection within 3 months from 11/4/25. | CMSGBXBORE | SR 00376
Chapada II+III | Active | AUG04-03 | HSIS Stage Accelerometer Issue | Instrumentation | Helical Intermediate Stage | 2026-04-28 |  | 3 | 4/28/26 - Intermediate stage accelerometer is reading a short circuit, recommend inspecting wiring and connections. Replace sensor if needed, | CMSTRBLSHOOT | SR 00543
Chapada II+III | Resolved | AUG04-14 | HSIS Accelerometer Open Circuit | Instrumentation | Helical Intermediate Stage | 2025-09-16 |  | 4 | 9/16/25 - HSIS accelerometer reading an open circuit, recommend inspecting wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | SR 00323
Chapada II+III | Active | AUG04-07 | HSS DnWind Rear IRBP | Warning | Helical High Speed Stage | 2024-10-11 |  | 5 | 10/11/24 - HSS Bearing issue, continue to monitor for progression. | Monitor | [7 empty] | Case In Progress | -45576
Chapada II+III | Active | AUG04-08 | HSS UpWind ORBP | Warning | Helical High Speed Stage | 2025-06-18 |  | 6 | 6/18/25 - Low level HSS UpWind ORBP, continue to monitor.
Chapada I | Active | JOA09-02 | HSIS Accelerometer Short Circuit | Instrumentation | Helical Intermediate Stage | 2024-12-31 |  | 4 | O acelerômetro do estágio paralelo está indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00682
Chapada I | Active | JOA09-02 | HSS UpWind ORBP | Warning | Helical High Speed Stage | 2025-06-24 |  | 3 | 6/24/25 - August 2024 borescope revealed HSS upWind ORBP damage, confirm via secondary borescope for HSS replacement
Chapada II+III | Active | AUG04-09 | HSS 1X rotacional | Warning | Generator Inboard | 2026-07-08 |  |  | Unbalance was identified probably due to the wye ring repair. | Monitor
Chapada II+III | Active | AUG04-11 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-06-02 |  | 2 | 6/2/25 - CMS indicates potential damage to the gearbox's planetary stage. Recommend full gearbox borescope within 2 weeks from 6/2/25 with focus on the planetary stage. | CMSGBXBORE | SR 00232
Chapada I | Active | JOA09-06 | Possible Ring Gear Issue | Warning | 1st Planetary Stage | 2025-03-07 |  | 6 | 3/7/25 - Intermittent ring gear signature, direct increasing. Continue to monitor.
Chapada I | Active | JOA09-08 | Planetary Sensor Open Circuit | Instrumentation | 1st Planetary Stage | 2025-03-25 |  | 5 | 3/25/25 - Planetary accelometer currently reading an open circuit, ensure sensor is plugged in. Check wirings and connections for any breakages. Replace sensor if needed. Acelerômetro do planetário está lendo como circuito aberto. Certifique-se que o sensor está conectado. Cheque os condutores e conexões em busca de alguma falha. Troque o sensor caso seja necessário. | CMSTRBLSHOOT | SS00161
Chapada II+III | Active | AUG04-12 | HSIS Sensor Issue | Instrumentation | Helical Intermediate Stage | 2024-10-11 |  | 4 | 10/11/24 - Possible HSIS sensor issue, please investigate wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | SS00100 |  | TBD |  |  |  |  | Case In Progress
Chapada II+III | Resolved | AUG04-12 | HSIS Sensor Issue | Instrumentation | Helical Intermediate Stage | 2026-07-08 |  | 4 | 10/11/24 - Possible HSIS sensor issue, please investigate wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | SS00706 |  | TBD |  |  |  | Case In Progress
Chapada I | Resolved | JOA09-09 | HSS DnWind ORBP | Warning | Helical High Speed Stage | 2024-09-05 | 2024-12-01 | 5 | 9/24/24 - Progressing HSS bearing issue. | Monitor | [7 empty] | Defect Confirmed - Awaiting Repair | -45540
Tatanka Ridge | Resolved | B01 | EOW Gearbox Claim | EOW | Helical High Speed Stage | 2021-12-10 |  | 1 | Replace for EOW claim - swap complete, wait for MB swap info | Final Report Needed |  |  |  |  | 2022-11-02 | 12/27 - small spikes to the warning setpoint in December, 4/1 - borescope on 7/11/21 found indents throughout stage 1 planet bearings, particle mesh in stage 1 mesh, monitor for progression, 4/11 - stage 3 2X GMF peak indicates mild misalignment, evidence of stage 1 planet bearing damage in FFT - haystack with bearing fault harmonics at high frequencies, 5/27 - minor progression in stage 1. 6/13 - Stage 3 FFT indicated HSS RS inner race damage, carrying pinion fault sidebands, GMF carrying sidebands as well, limited progression, 9/9 - Spike in S2 SER Ring Fault GFED, 11/8 - spike in S3 SER Pinion Fault GFED trend, S3 FFT shows very high 12x harmonic of S2 GMF, 12/5 - no clear progression |  | Defect Confirmed - Repair Complete | 327
Tatanka Ridge | Resolved | B01 | Generator DE Sensor Issue | Instrumentation | Generator Inboard | 2023-01-30 |  | 2 | 1/30/23 - Suspect vibration indicates loose mounting or bad sensor | CMSTRBLSHOOT | 3073779 | Closed | Closed |  |  | 1/30 - suspect de gen vibration, potential bad sensor or mounting |  | Case In Progress | -44956
Tatanka Ridge | Resolved | B01 | EOW Main Bearing Claim | EOW | Main Bearing | 2022-05-16 |  | 1 | Replace for EOW claim | Final Report Needed | [5 empty] | 5/16 - CMS shows main bearing fault harmonics higher than 1X GMF, 6/13 - no grease sample in fluidlife, 11/8 - still no grease in fluidlife, 11/23 - no grease, 12/5 - no grease |  | Case In Progress | -44697
Tatanka Ridge | Active | B01 | Generator Inboad ORBP/IRBP | Alarm | Generator Inboard | 2025-01-29 |  | 3 | 1/29/25 - CMS indicates generator inboad orbp/irbp issue | CMSGENB | 3500537 |  | Ready to Schedule |  |  |  |  | Case In Progress
Coyote Ridge | Active | B01 | 1st stage Planetary bearing issue | Alarm | 1st Planetary Stage | 2024-12-17 |  | 3 | 12/17/24 - CMS indicates potential 1st stage planetary IRBP/ORBP Issue | Longterm Watchlist | 3480623 | [6 empty] | Case In Progress
Jayhawk | Resolved | B02 |  | Warning | Helical High Speed Stage | 2022-03-01 |  | 5 |  | Monitor | [6 empty] | 3/7 - elevated stage 3 GMF peaks, stage 2 direct shows clear ring fault sidebands, potential damage to stage 2 planet gears, 6/13 - stage 3 FFT indicates early HSS Gear mesh and HSS bearing rollers, limited progression, 10/18 - No progression - still sitting at warning threshold, possible stage 3 gear fault - 1g harmonics on FFT, 2g on timebase, 11/10 - No progression - still looks like S3 Gear Fault 2x harmonic much higher than 1x | Case In Progress | -44621
Tatanka Ridge | Resolved | B03 |  | Alarm | 1st Planetary Stage | 2021-08-29 |  | 2 |  | Monitor | [6 empty] | 10/26 - high amplitude peaks at the end of August at the Ring Fault frequency. Small sidebands match ring fault frequency, 12/3 - continue to monitor 1/18 - potential damage to hss bearing, 2/10 - all direct signals below warning setpoint, 0.03g peak at HSS DnWind Ball Spin 2X, monitor, | Case In Progress | -44437
Jayhawk | Resolved | B03 |  | Warning | Helical High Speed Stage | 2022-02-03 |  | 5 |  | Monitor | [6 empty] | 12/28 - Latch Reset, 2/8 -direct vibration remains near 4g, 1.5g peak at 2X GMF, 3/7 - elevated stage 3 GMF peaks monitor, 4/8 - keyphasor is not functioning, 5/24 - still no keyphasor, potential misalignment, 10/18 - Keyphasor works now, 2.x GMF peak has gone down, but pinion fault sidebands have developed, Vibration of around 2g on timebase, 11/10 - no progression, likely misalignment | Case In Progress | -44595
Jayhawk | Resolved | B03 |  | Keyphasor Issue | Keyphasor | 2022-03-07 |  |  | keyphasor isn't reading speed | CMSTRBLSHOOT | 2813074 |  | Closed |  | 2022-06-28 | 9/9 - keyphasor came back online after feeder outage on 6/28 |  |  | 113
Jayhawk | Resolved | B03 |  | Warning | Main Bearing | 2022-07-29 |  | 5 |  | Monitor | [6 empty] | 10/18 - Direct signal took off in June/July and has remained elevated since with amplitudes nearing alarm setpoint. No indicators in FFT of MB damage. Slightly elevated temps compared to neighbors but still in normal range, 11/10 - No progression in trend, 1g impacts on timebase, potential ORBP damage from FFT | Case In Progress | -44771
Coyote Ridge | Resolved | B03 | Main bearing, gearbox 1,2 & 3 sensor issue | Instrumentation | CMS Monitor | 2024-05-22 |  | 5 | 5/22/24 - CMS shows main bearing, gearbox sensor 1, 2, and 3 are all at -22 v. | CMSTRBLSHOOT | 3353801 |  | Ready to Schedule |  |  |  |  | Case In Progress
Coyote Ridge | Resolved | B1 | SKF Main Bearing Issue - swap complete, update config | Sweep | Main Bearing | 2023-02-23 |  | 2 | Elevated temps and vibrations indicate progressing failure, thrust derated, 4/3 - shutdown + visual inspection, DNR, swap complete, waiting on config info | Final Report Needed | 3107704 | Closed | Closed |  | 2023-07-06 |  |  | Defect Confirmed - Repair Complete | 133
Coyote Ridge | Resolved | B3 | SKF Main Bearing Issue roller elements | Warning | Main Bearing | 2021-11-05 | 2024-10-03 | 4 | 5/8/4 -Turbine shut down due to pitch bearing issue, likely main bearing will be swapped in a month. 9/7/23 - Main bearing borescoped due to high temps. Borescope showed signs of cage damage and surface damage. Continue to monitor CMS + Temps. Non-CMS thrust derate. | Longterm Watchlist | 2725805 | Cancelled | Cancelled | Q2-3 2024 |  | 3/14 - damage isn't aparent in CMS | 11/15 - SKF bearing - vibrations increased gradually, likely damage to main bearing, WO 2645566, 2725805, 3/3 - bearing looks good some damage to DLC, unclear if grease purge was performed, 3/7 - no purge performed, work order cancelled, 5/23 - no significant progression, 6/15 - Main Bearing Ball Spin 1X shows some recent progression, 7/7 - spike in cage signal on 5/28, temps still elevated, 8/15 - vibration signal has slowly reduced, temps are still slightly elevated, below 55, borescope completed 7/13/22, minor indents and one spall found on rollers, 9/9 - temps remain elevated, below 55C, 11/29 - temps still elevated compared to neighbors, not >50C in past 20 days, | Defect Confirmed - Repair Complete | -44505
Coyote Ridge | Resolved | B5 |  | Case Tracking | Main Bearing | 2022-06-15 |  | 5 |  | Pending Replacement | [5 empty] | 8/20/22 |  | True Positive - Other Method | -44727
Coyote Ridge | Resolved | B5 | Stage 3 Sensor Issue | Instrumentation | Helical High Speed Stage | 2022-09-09 |  | 5 | Sensor is reading an open circuit, please inspect wiring and connections. | CMSTRBLSHOOT | 3053231 | Closed | Ready to Schedule |  |  |  | 12/2 - faulting again, making another WO | Case In Progress | -44813
Coyote Ridge | Resolved | B8 |  | Warning | Main Bearing | 2021-09-05 |  | 5 |  | Monitor | 2725808 | Cancelled | Cancelled |  |  |  | 8/15 - borescope complete, found minor damage, indents on rollers, small spall, evidence of sela spacer spinning, monitor for progression, 9/9 - no evidence of progression in CMS, 11/29 - no progression, temps good | Case In Progress | -44444
Jayhawk | Resolved | C02 |  | Warning | Helical High Speed Stage | 2022-02-27 |  | 5 |  | Monitor | [6 empty] | 3/7 - 1g @ 2X GMF stage 3, lower amplitude harmonics are present at high frequencies, not clearly sidebands of a particular faults, may be damage pinion, monitor trend for increases, 4/8 - likely misalignment, 5/24 - potential damage to S2 PC BRG GS inner race, peak at fault frequency with harmonics, 6/13 - no progression, 10/18 - No Progression on trend, one bigger sideband on Stage 3 2x GMF, 11/10 - no progression on trend | Case In Progress | -44619
Jayhawk | Resolved | C03 |  | Alarm | 1st Planetary Stage | 2022-04-06 |  | 5 |  | Monitor | [6 empty] | 4/8 - Stage 1 direct signal shows peaks to warning setpoint, the frequency spectrum shows shaft harmonics that may indicate damage to stage 1 bearings. Monitor for progression or characteristic fault frequencies, 5/24 - no additional peaks to warning or alarm setpoint. 6/13 - stage 1 direct has returned to normal levels, damage may already be sustained. New warning in stage 3, Stage 3 shows elevated GMFs, 10/18 - Increase in Stage 3 2x GMF to 1.5g, slight increase in trend to warning levels recently, reduce to cat 2, 11/10 - no progression in S3 trend, potential misalignment shown by 2x harmonic | Case In Progress | -44657
Jayhawk | Resolved | C03 |  | Keyphasor Issue | Keyphasor | 2022-02-08 |  |  | Check wiring next climb, replace monitor if necessary | CMSTRBLESHOOT | 2800312 |  | Closed |  | 2022-03-25 | Replace monitor if sensor troubleshoot doesn't work, 3/7 - techs checked wiring and found no issues |  |  | 45
Jayhawk | Resolved | C04 |  | Warning | Main Bearing | 2022-03-10 |  | 5 |  | Monitor | [6 empty] | 4/8 - direct signal trends between alarm and warning setpoint, timebase shows occasional 3g impacts, minor haystack, temps looks normal to neighbors, 5/24 - trend now remains at or below warning setpoint, no clear faults in the FFT, 6/13 - peak at 2.175x; 10/18 - Slight increase in trend since early September but below warning threshold, temps looks good, 11/10 - No progression on trend, potential Roller damage indicated by Ball spin freq | Case In Progress | -44630
Tatanka Ridge | Resolved | C05 |  | Warning | Helical High Speed Stage | 2022-11-19 |  | 5 | Monitor HSS BRGs | Monitor | [6 empty] | 11/23 - S3 SER Pinion GFED signal has been at warning level over lifetime, recent spike up to almost alarm level, Pinion fault sidebands emerging between 2x and 3x GMFs, potential HSS GS IRBP dmaage seen on Direct FFT, |  | -44884
Tatanka Ridge | Resolved | C05 | Failed Timken Main Bearing | Case Tracking | Main Bearing | 2023-01-19 |  | 1 | Thrust derate, bearing failed 4/2/23, | Final Report Needed | [6 empty] | 1/19/23 - early roller fault harmonics above 300x | Defect Confirmed - Repair Complete | -44945
Jayhawk | Active | C07 | Main Bearing BS2X issue | Sweep | Main Bearing | 2024-10-07 |  | 2 | Borescope shows no significant damage, continue to monitor for progression. 10/7 - CMS indicates Main Bearing BS2X issue | Monitor | 3442849 | Closed | Closed |  |  |  |  | Case In Progress | -45572
Coyote Ridge | Active | C2 | Potential Planetary IRBP issue | Alarm | 1st Planetary Stage | 2024-10-29 |  | 3 | 10/29/24 - CMS indictates s1 planetary IRBP issue | Longterm Watchlist |  |  | Ready to Schedule |  |  |  |  | Defect Confirmed - Awaiting Repair | -45594
Coyote Ridge | Resolved | C7 |  | Instrumentation | CMS Monitor | 2022-08-15 |  |  | Reboot 60M100, check LED panel for fault indication, verify correct installation | CMSTRBLSHOOT | 2989827 | Cancelled | Cancelled |  | 2022-08-16 | Data issues resolved with firmware update/reboot |  |  | 1
Coyote Ridge | Resolved | C7 | Potential HSS Bearing Damage | Warning | Helical High Speed Stage | 2022-02-23 |  | 2 | HSS bearing fault harmonics present in the spectrum | Monitor | 2919842 | Cancelled | Cancelled |  |  | 1/27/23 - HSS harmonics | 3/3 - 0.047g @ HSS DnWind ORBP, very likely damage to stage 3 HSS DnWind bearing. Monitor for now, 4/12 - clear fault harmonics for outer racer damage to HSS GS bearing, recommending HSS check, 7/7 - increasing work order priority, 8/15 - keyphasor/IONet Speed not reading correctly, doesn't match PI, resending configuration, 9/9 - HSS GS ORBP peak with harmonics and pinion fault sidebands, HSS bearing fault harmonics at high frequencies, 11/29 - HSIS GS BRG IRBP fault frequency, no increase in trend | Case In Progress | -44615
Coyote Ridge | Resolved | C8 |  | Case Tracking | Main Bearing | 2022-05-09 |  | 5 |  | Thrust Derate | [5 empty] | 9/8/22 |  | True Positive - Other Method | -44690
Coyote Ridge | Active | C9 | Main bearing sensor issue | Instrumentation | Main Bearing | 2023-03-08 |  | 5 | Main Bearing CMS sensor is showing an open in the wiring. Check harness for opens Bias = -22V, should be Bias = -13V | CMSTRBLSHOOT | 3094928 | Closed | Closed |  |  |  |  | Case In Progress | -44993
Coyote Ridge | Active | D01 | Generator Inboard Potential ORBP issue | Alarm | Generator Inboard | 2025-02-20 |  | 5 | 2/20/25 - Potential Generator Inbard orbp issue | Monitor
Jayhawk | Resolved | D02 | S1 + S2 Sensor Issue | Instrumentation | 1st Planetary Stage | 2023-04-13 |  | 5 | Check both S1 and S2 sensor harnesses for opens | CMSTRBLSHOOT | 3112483 | Closed | Closed |  | 2023-05-25 |  |  | Defect Confirmed - Repair Complete | 42
Coyote Ridge | Active | D02 | Potential Gearing issue | Alarm | 1st Planetary Stage | 2024-09-11 |  | 2 | 9/11/24 - CMS indicates potential gearing issue. Please conduct gearbox borescoe. | CMSGBXBORE | 3426100 | Closed | Closed |  | 2024-09-26 |  |  | Defect Confirmed - Repair Complete | 15
Coyote Ridge | Resolved | D10 |  | Alarm | Helical High Speed Stage | 2021-11-24 |  | 5 |  |  | 2651731 | Closed | Closed |  |  |  |  | True Positive | -44524
Coyote Ridge | Active | D11 | Main Bearing ORBP damage | Sweep | Main Bearing | 2023-01-24 | 2025-03-04 | 4 | No longer derated. Main bearing is showing roller damage, monitor for damage progression (non-DLC SKF). Thrust derate requested on 3/9/23. | Longterm Watchlist | 3095090 | Closed | Closed | Q3 2024 |  | 3/9 - RCS-20230309-0882 requesting thrust derate, 3/14 - Ge declined thrust derate, 3/22 - non-DLC SKF | 1/24 - minor ORBP harmonics above 300x | Defect Confirmed - Awaiting Repair | -44950
Coyote Ridge | Active | D2 | Main Bearing Roller damage | Sweep | Main Bearing | 2023-02-15 |  | 3 | Main bearing shows roller damage, recommend borescope (non-DLC SKF). | CMSMBBORE | 3103261 | Closed | Ready to Schedule |  |  | 3/22 - non-DLC SKF |  | Case In Progress | -44972
Coyote Ridge | Active | D2 | Potential S1 gearing issue | Alarm | 1st Planetary Stage | 2024-09-11 |  | 1 | 9/11/24 - CMS indicates potential gearing issue. 9/19- Borescope doesn't show defect indication, secondary borescope requested, and derate due to nature of defect and CMS signature progression. 9/25 - Turbine shutdown and DNR'd due to CMS signature showing potential gearing failure. | CMSGBXBORE | 3426100 | Closed | Closed |  | 2024-09-26 |  |  | Defect Confirmed - Repair Complete | 15
Coyote Ridge | Active | D3 | Main Bearing ORBP damage | Sweep | Main Bearing | 2023-02-08 |  | 4 | No longer derated. Main bearing is showing roller damage, borescope (non-DLC SKF). Thrust derated 3/9/23 | Longterm Watchlist | 3095084 | Closed | Closed | Q3 2024 |  | 2/15 - persistant 13.5x harmonics above 2x GMF, 3/14 -GE declined thrust derate request, 3/22 - non-DLC SKF | 2/8 - main bearing roller signature present in spectrum, found in SKF sweep | Defect Confirmed - Awaiting Repair | -44965
Coyote Ridge | Resolved | D5 |  | Instrumentation | Helical High Speed Stage | 2022-02-09 |  |  | Check for shorted sensor wiring, gearbox 3 | CMSTRBLSHOOT | 2800817 |  | Closed |  | 2022-04-28 | 4/28 - sensor mount found loose, tightened |  |  | 78
Coyote Ridge | Resolved | D5 |  | Warning | Main Bearing | 2021-08-29 |  | 3 |  | Monitor | 2645569 | Cancelled | Cancelled |  |  |  | 10/29 - vibrations have been elevated since 8/2020, continue to monitor, 3/22 - cancelled work order, reduce to cat 2, 7/7 - temps are elevated, below 55, 12/2 - reduction in signal after time offline, temp still slightly elevated, 1/24 - minor ORBP harmonics above 300x | Case In Progress | -44437
Coyote Ridge | Resolved | D6 |  | Sweep | Main Bearing | 2022-08-15 |  | 5 |  | Monitor | [6 empty] | 8/15 - Main bearing direct shows an increasing trend to the warning setpoint, temps look normal, monitor, 9/9 - occasional cyclical impacts, no fault harmonics, 9/26 - signal decreasing from the setpoint, 12/2 - MB has settled at normal operating signal |  | -44788
Coyote Ridge | Active | D6 | Oil Particle Counts Rising | Particle Counter | Particle Counter | 2024-02-19 |  | 6 | 2/19/24 - Oil Particle counts rising, possible 1st stage planetary issue. Continue to monitor | Monitor | [7 empty] | Case In Progress | -45341
Coyote Ridge | Resolved | D9 |  | Warning | 2nd Planetary Stage | 2021-09-05 |  | 2 |  | Monitor | [5 empty] | 2/15 - noisy harmonics above 2X GMF for 1+ month | 12/2 - high amplittude spikes of S2 SER PG GFR SR1 trend, S2 SER Planet fault sidebands still present, HSS harmonics present, | Case In Progress | -44444
Coyote Ridge | Resolved | D9 | SKF Main Bearing Issue | Sweep | Main Bearing | 2023-02-15 |  | 1 | CMS signatures have continued to progress, turbine should now be shutdown and DNR'd. | Repair Pending | 3084636 | Closed | Closed |  | 2023-07-12 |  |  | Defect Confirmed - Repair Complete | 147
Tatanka Ridge | Resolved | E01 | Main Bearing Issue | Warning | Main Bearing | 2021-04-26 |  | 6 | Borescope found adhesion damage, ORBP damage. Continue to monitor for progression, operate as normal. | CMSMBBORE | 2938892 | Closed | Closed |  |  | 3/22 - limited damage- in 1/24 borescope | 1/18/23 - well developed ORBP harmonics, recommending thrust derate, 2/2 - 1 spike in direct mode 0, 10/27/23 harmonics for mb issue are present but it hasn't progressed to the direct alarm threshold | Case In Progress | -44312
Coyote Ridge | Active | E01 | Main Bearing Accelerometer Open Circuit | Instrumentation | Main Bearing | 2023-08-25 |  | 3 | 9/25/23 - Main bearing sensor is currently reading an open circuit. Please investigate sensor wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | 3196615 | Closed | Closed |  |  |  |  | Case In Progress | -45163
Tatanka Ridge | Resolved | E02 |  | Change 1 | Helical High Speed Stage | 2021-11-16 |  | 5 | Monitor HSS BRGs | Monitor | [6 empty] | 3/2 - stage 3 direct shows dense peaks to about 4g, below warning setpoint. FFT peaks: 0.064g @ 2X, 0.029g @ 7.5X, 6/13 - stage 3 FFT indicates roller damage to HSS GS, 11/8 - no progression on trend in past year, Stage 3 FFT indicates HSIS RS IRBP damage and possible roller damage | Case In Progress | -44516
Tatanka Ridge | Active | E02 | S1 Planetary IRBP/ORBP Issue | Sweep | 1st Planetary Stage | 2024-07-24 | 2025-03-10 | 2 | 7/24/24 - CMS shows potential ORBP/IRBP S1 planetary bearing issue | Longterm Watchlist | 3390814 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45497
Jayhawk | Active | E02 | Potential Main Bearing IRBP issue | Sweep | Main Bearing | 2024-07-09 |  | 5 | 7/9/24 - CMS shows potential IRBP issue continue to monitor via CMS | Monitor | [7 empty] | Case In Progress | -45482
Jayhawk | Resolved | E03 | Potential MB IRBP Banding | Sweep | Main Bearing | 2023-03-14 |  | 5 | CMS shows banding on main bearing. | [6 empty] | 3/14 - ORBP harmonics starting mid-July 2022, limited progression |  | Case In Progress | -44999
Tatanka Ridge | Resolved | E03 |  | Warning | Main Bearing | 2021-03-20 |  | 5 |  | Monitor | [6 empty] | 3/2 - main bearing direct timeseries shows potential mild damage sustained Spring 2021, monitor for increases or FFT peaks, 11/8 - no progression | Case In Progress | -44275
Tatanka Ridge | Resolved | E03 | DE Gen Bearing Damage | Warning | Generator Inboard | 2021-07-23 |  | 5 | Elevated DE bearing vibration, inspect, add grease to reduce vibration | Monitor | 3092938 | Closed | Closed |  |  |  | 8/19 - low concern, 11/8 - clear ORBP damage (1.5g peak on FFT) with 10g impacts on timebase upgrade to Cat 2 | Case In Progress | -44400
Tatanka Ridge | Resolved | E03 | Generator Outboard | Alarm | Generator Outboard | 2024-06-18 |  | 3 | 9/24/24 - Bearings currently being replaced. 7/30/24 - requested 50% derate due to direct inscrease. 6/18/24 - CMS data shows generator outboard ORBP issue, sent out for inspection | CMSGENB | 3368573 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -45461
Jayhawk | Resolved | E03 |  | Keyphasor Issue | Keyphasor | 2022-02-08 |  |  | Check wiring next climb, replace monitor if necessary | CMSTRBLSHOOT | 2800313 |  | Closed |  | 2022-05-11 | Replace monitor if sensor troubleshoot doesn't work, 6/13 - CMS now showing shaft speed, unclear if action was taken, 9/9 - keyphasor came back online after SCR retro and likely reboots |  |  | 92
Jayhawk | Active | E03 | Potential Main bearing IRBP Issue | Sweep | Main Bearing | 2024-06-05 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -45448
Jayhawk | Resolved | E04 | Particle Counter Troubleshooting | Particle Counter | Particle Counter | 2023-07-07 |  | 3 | 9/7/23 - Awaiting total mass counter reset. 7/7/23 - Particle counter is showing large amounts of debris generation and change in flow rate over the past week with not correlation to CMS data. Recommend inspecting the fittings and connections of the inlet and outlet flows of the sensor and noting any abnormalities. | GBXPARTTS | 3153968 | Closed | Closed |  |  |  |  | Case In Progress | -45114
Tatanka Ridge | Resolved | E04 | EOW Gearbox Claim | Case Tracking | 1st Planetary Stage | 2021-12-14 |  | 1 | S1 PS, S2 PC BRG damage, monitor CMS and debris, 50% derate, rapid debris generation, 5/23 - shutdown by GE | Final Report Needed |  |  |  |  | 2023-07-13 |  | 1/18/23 - S1 PS BRG harmonics present | Defect Confirmed - Repair Complete | 576
Jayhawk | Resolved | E04 |  | Warning | 2nd Planetary Stage | 2022-02-02 |  | 5 |  | Monitor | [5 empty] | 2/10 - early S1 PS BRG harmoincs, monitor | 2/8 - low amplitude ring fault sidebands in stage 2, 5/24 - potential S2 PC BRG RS roller damage, some progression, monitor for increases in fault peaks in FFT, 6/13 - low level stage 2 planet mesh sidebands, 11/10 - No progression | Case In Progress | -44594
Jayhawk | Active | E04 | Potential Main bearing IRBP Issue | Sweep | Main Bearing | 2024-06-05 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -45448
Tatanka Ridge | Resolved | E05 | EOW Main Bearing Claim | Warning | Main Bearing | 2022-07-18 |  | 1 | 1/11/24 - estimated replacement is end of Q1-Q2 | Longterm Watchlist | 3135308 | Closed | Closed | Q3 2024 |  |  | 8/19 - low concern, 11/8 - no progression, 1/25 - EOW found severe OR spalling and micropitting, spectrum shows | Defect Confirmed - Repair Complete | -44760
Jayhawk | Resolved | E07 |  | Keyphasor Issue | Keyphasor | 2022-02-08 |  |  | Check wiring next climb, replace monitor if necessary | CMSTRBLSHOOT | 2800314 |  | Closed |  | 2022-06-28 | Replace monitor if sensor troubleshoot doesn't work, 9/9 - keyphasor came back online after feeder outage on 6/28 |  |  | 140
Jayhawk | Resolved | E08 |  | Instrumentation | CMS Monitor | 2022-02-08 |  |  | Wait until next report | [5 empty] | 2022-03-25 |  |  |  | 45
Jayhawk | Active | E08 | Potential early MB Issue | Sweep | Main Bearing | 2024-05-15 |  | 5 | 5/15/24 - CMS shows slight main bearing defect signature continue to monitor for progression | Monitor | [7 empty] | Case In Progress | -45427
Coyote Ridge | Resolved | E1 | SKF Main Bearing Issue | Sweep | Main Bearing | 2023-03-27 |  | 1 | (DNR) Failed main bearing | Repair Pending | 3103266 | Closed | Closed |  | 2023-06-16 |  |  | Defect Confirmed - Repair Complete | 81
Coyote Ridge | Resolved | E3 |  | Warning | Generator Inboard | 2021-09-21 |  | 5 |  | Monitor | [5 empty] | 2022-03-22 |  | False Positive - No Inspection | -44460
Coyote Ridge | Resolved | E3 | SKF Main Bearing Issue | Warning | Main Bearing | 2022-03-20 |  | 3 | 7/20/23 - MB CMS + Temp has increased in severity, turbine should be DNR'd until replacement. | Repair Pending | 3153099 | Closed | Closed |  | 2023-07-24 |  | 3/22 - likely damage to main bearing outer race, normal temps, 6/15 - ORBP harmonics are well-pronounced, temps are still normal, 12/2 - no trend progression, temps good | True Positive | 491
Jayhawk | Resolved | F07 |  | Instrumentation | CMS Monitor | 2022-02-08 |  |  | Wait until next report | [5 empty] | 2022-03-25 |  |  |  | 45
Jayhawk | Active | F08 | Potential Main bearing BS2X issue | Sweep | Main Bearing | 2024-08-06 |  | 2 | 8/06/24 - CMS shows potential main bearing bs2x issue. Request for borescope when progression is visble, currently intermittent. 9/18/24 - Request for CMSMBBORE sent. | Repair Pending | 3432752 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45510
Jayhawk | Resolved | F10 |  | Alarm | 1st Planetary Stage | 2022-02-07 |  | 5 |  | Monitor | [6 empty] | 2/8 - sudden increase in stage 1 vibration on 2/7, FFT consistently shows shaft harmonics ~0.015g, timebase shows impacts with a 58msec interval, 3/4 - Stage 1 SER Ring Fault signal shows peaks of increasing amplitude, stage 1 ring fault side bands are present throughout spectrum, 4/8 - cancelled WO 2813048, 5/24 - additional peak to alarm on 5/8, Envelope FFT indicates potential damage to S1 PC BRG GS raceways, 6/13 - stage 1 direct returned to normal levels, monitor for progression, 10/18 - no progression, 11/10 - no progression, lowering severity to Cat 2 | Case In Progress | -44599
Jayhawk | Resolved | F11 |  | Warning | Helical High Speed Stage | 2022-02-21 |  | 5 |  | Monitor | [6 empty] | 3/7 - stage 3 FFT shows 0.1g peak at HSS DnWind IRBP with harmonics, monitor for increases in timeseries, 4/8 - likely damage to HSS DnWind Rear inner race, harmonics for IRBP fault pervade spectrum, 5/24 - limited progression, continue to monitor, 6/13 - HSS GS Rear fault peak with harmonics carrying pinion fault sidebands, minor progression, 10/18 - no progression, 11/10 - continued decline in trend amplitude, IRBP damage still clear, indication of misalignment due to elevated 2x harmonic on S3 SER Gear fault | Case In Progress | -44613
Jayhawk | Resolved | F12 |  | Alarm | 1st Planetary Stage | 2021-12-24 |  | 5 |  | Monitor | [6 empty] | 4/8 - stage 1 direct peaked to warning setpoint in December, monitor for progression, 5/24 - FFT indicates damage to S1 PC BRG GS rollers, 6/13 - recent low amplitude peaks, low amplitude roller fault harmonics in the envelope, 10/18 - No progression, 11/10 - no progression | Case In Progress | -44554
Tatanka Ridge | Active | G01 | Generator Outboard IRBP | Alarm | Generator Outboard | 2023-12-18 |  | 3 | 8/28/24 - Grease added. 12/18/2023 - CMS indicates IRBP issue in generator outboard, reccomend inspection/grease check | CMSGENB | 3244412 | Closed | Closed |  |  |  |  | Case In Progress | -45278
Tatanka Ridge | Resolved | G02 | DE Gen Bearing Damage | Warning | Generator Inboard | 2022-09-09 |  | 5 |  | CMSGENB | 3016492 | Cancelled |  |  | 2022-10-21 | 10/6 - Alarm triggered after amplitude steadily increased from last shutdown. 50g peaks on direct signal timebase and 3g pk on FFT for 2nd harmonic of ORBP with 1,2,3&4 harmonics clear, 11/8 - trend has died down to normal levels since 10/21, Still clear ORBP peak and 2x harmonic, 1g signal on timebase,11/23 - decrease to Cat 2 |  | True Positive | 42
Tatanka Ridge | Active | G02 | Second Stage Planetary bearing | Alarm | 2nd Planetary Stage | 2021-11-29 |  | 2 | 7/24/24 - run off damage found, continue to monitor until spectrum progresses. 4/26/24 - CMS indicates progression in S2 for bearing defect, sent out for a gearbox borescope. 1/11/24 - CMS has not alerted for this turbine for any issues. It also isn't showing any damage or deviation in the spectrum data or the direct that could indicate there are any issues. However, the EOW borescope did show spalling damage. Estimated replacement: Q4 '24. 9/9/22 - Elevated DE bearing vibration, inspect, add grease to reduce vibration | CMSGBXBORE | 3342081 | Closed | Closed |  |  | 2022-06-13 | 12/3 - sudden increase in direct stage 2 vibrations, requesting immediate derate, borescope recommended 12/14 - maybe sensor issue, maybe a cracked race? No images yet, 1/18 - more events, extending to stage 1 &2, reopening borescope, 3/2 - direct stage 2 vibration has reduced to below the warning setpoint. 1.021g @ Stage 1 Carrier DnWind, borescope is still open. 3/23 - GE is planning on doing an uptower HSS Swap, unclear is borescope was performed | Defect Confirmed - Awaiting Repair | -44529
Tatanka Ridge | Resolved | G03 |  | Alarm | Helical High Speed Stage | 2021-12-13 |  | 5 | Monitor HSS BRGs | Monitor | [6 empty] | 12/27/21 - typical operation is just below the warning setpoint, spike above alarm on 12/13, 1/18 - continue to monitor, 2/10 - timebase floor = 5g, 0.15g peak at HSS DnWind cage frequency in the FFT, 3/2 - low concern, latch reset, 4/11 - 0.457g peak at 1X stage 3 GMF, followed by potential bearing fault harmonics, 6/13 - 2x sidebands likely sensor noise, 11/8 - no progression on trend, 5g peaks on timebase, | Case In Progress | -44543
Tatanka Ridge | Resolved | G03 |  | Warning | Generator Outboard | 2022-12-22 |  | 1 |  | Monitor | [6 empty] | 12/22/22 - Generator Outboard spiked up rapidly over 5hrs but immediately went back to regular operating levels, both IRBP and ORBP faults seen on spectrum |  | -44917
Jayhawk | Resolved | G07 |  | Keyphasor Issue | Keyphasor | 2022-02-08 |  |  | Check wiring next climb, replace monitor if necessary | CMSTRBLESHOOT | 2800315 |  | Closed |  | 2022-03-25 | Replace monitor if sensor troubleshoot doesn't work |  |  | 45
Jayhawk | Resolved | G10 |  | Warning | 2nd Planetary Stage | 2022-10-21 |  | 5 |  | Monitor | [6 empty] | 10/18 - potential early damage to Stage 2 bearings, 11/10 - trend has peaked over alarm signal since last check but overall trend is consistent with the past year, Mode 3 seems to be the worst, modulations on timebase to ~2g | Case In Progress | -44855
Jayhawk | Resolved | G16 |  | Alarm | 1st Planetary Stage | 2022-02-07 |  | 3 |  | Monitor | [6 empty] | 2/8 - ring fault harmonics present throughout FFT, Peaks to the alarm setpoint in the Direct timeseries, occasional impacts in the timebase, 3/7 - monitor for increases in the timeseries, 5/24 - peaks are reducing amplitude, now below warning setpoint, potential damage to S1 PC BRG GS rollers, low level fault peak with harmonics, 6/13 - no progression, 10/18 - no progression, 11/10 - no progression on timebase, now see roller damage indicated in the FFT | Case In Progress | -44599
Jayhawk | Active | G16 | 1st Planetary Stage Sun Pinion Damage | EOW | 1st Planetary Stage | 2023-07-27 |  | 6 | Continue to monitor for defect progression. 2/29/24 - Sending out for secondary borescope. 10/4/23 - Debris runover seen in in EOW inspection, signature seen in CMS data. Continuing to monitor. 12/18 - alert flagged, specturm has increased. Direct peaked at 52; EOW rejected | Longterm Watchlist | 3310504 | Closed | Closed | Q4 2024 |  |  |  | Case In Progress | -45134
Coyote Ridge | Resolved | G3 | Main Bearing BS2X | Sweep | Main Bearing | 2023-08-30 | 2024-06-12 | 2 | 3/21/24 - CMS indicates progression to defect damage, please perform full main bearing borescope. 9/27/23 - Evidence of golden grease, pitting seen on rollers and raceways. Estimated replacement 6/1/24. 8/30/23 - Recommend main bearing borescope within 2 weeks with focus on cage and rolling elements. Thrust Derated | Final Report Needed | 3320409 | Closed | Closed | 2024-05-15 |  |  |  | Defect Confirmed - Repair Complete | -45168
Tatanka Ridge | Active | H01 | S1 Planetary stage Carrier Bearing Issue | Sweep | 1st Planetary Stage | 2024-07-25 |  | 3 | 7/25/24 - CMS shows potential carrier bearing issue. Perform borescope within 3 months from now | Longterm Watchlist | 3391934 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45498
Tatanka Ridge | Resolved | H02 | S1 Gearbox Failure | Warning | 2nd Planetary Stage | 2021-12-10 |  | 1 | Tower is offline awaiting repair | Repair Pending |  |  |  |  | 2023-03-29 | 12/27 - peak to warning setpoint, monitor, 2/10 - 0.011g peak at Stage 2 Carrier DnWind ORBP frequency, 3/2 - resolving, 4/4 - reopening, borescope from October 21, found spalling on all 3 s1 planet gears, indents on other bearings, particle mesh in s1 and s2 mesh, replacement timeline is unclear, 6/13 - limited progression, 10/3 - stage 1 sun fault warning, 3/29/23 - replacement complete, configuration updated |  | True Positive | 474
Tatanka Ridge | Active | H02 | Second Stage Planetary Sensor issue | Instrumentation | 2nd Planetary Stage | 2024-01-10 |  | 5 | 1/10/24 - CMS shows electrical noise, work order made to troubleshoot | CMSTRBLSHOOT | 3252301 | Closed | Closed |  |  | 1/10/24 CMS indicates there is a sensor issue in stage 2 |  | Case In Progress | -45301
Tatanka Ridge | Resolved | H03 | S1 + S2 Planetary Damage | Warning | 1st Planetary Stage | 2021-12-11 |  | 3 | 3/6/24 - Warranty case updated. Borescope found inner race spalling, outer race and bearing pitting, and CMS shows progression in spectrum for S1 and S2. 4/17/23 - Replace for EOW claim, 50% derate on 4/17. | Longterm Watchlist | 3308853 | Closed | Closed | Q3 2024 |  | 1/18/23 - S2 Planet Fault GFED, EOW claim in process | 12/27 - peak to warning setpoint, monitor, 3/2 - resolving, 4/11 - Stage 1 FFT shows peaks at both planet bearing roller fault frequencies, stage 3 FFT indicates potential damage to HSS bearings, 6/13 - likely damage to HSS RS outer race, fault peaks and harmonics, 11/8 - EOW Inspection showed S1 PB damage, S1 SP, S2 RG and Planet damage, | Defect Confirmed - Repair Complete | -44541
Jayhawk | Resolved | H05 | S1 Planetary Accelerometer Issue | Instrumentation | 1st Planetary Stage | 2023-09-11 |  | 5 | 9/11/23 - S1 planetary sensor is currently reading an open circuit. Please investigate wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | 3188444 | Closed | Closed |  | 2023-10-05 |  |  | Defect Confirmed - Repair Complete | 24
Jayhawk | Active | H05 | Potential early MB Issue | Sweep | Main Bearing | 2024-05-15 |  | 5 | 5/15/24 - CMS shows slight main bearing defect signature continue to monitor for progression | Monitor | [7 empty] | Case In Progress | -45427
Tatanka Ridge | Active | I02 | Main Bearing Accelerometer Open Circuit | Warning | Main Bearing | 2023-08-31 |  | 5 | 8/31/23 - Main bearing sensor is reading an open circuit. Please investigate wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | 3182520 | Closed | Closed |  |  |  |  | Case In Progress | -45169
Tatanka Ridge | Resolved | I05 | S2 Planetary Damage | Warning | 1st Planetary Stage | 2022-11-23 |  | 1 | 7/17/23 - Gearbox replaced, awaiting repair report | Final Report Needed |  |  |  |  | 2023-07-01 | 12/5 - Major spike in S1 PG IRBP BFA trend in late Nov, S1 PC GS roller damage indicated on that FFT, S1 Direct FFT shows same roller damage indicator but direct trend not elevated, EOW Borescope found: S1 PB1 DW Raceway and Roller Spalling (101-172), S1 PB1 UW Spalling (085-099), S2 UWCB Indents (053-062), S2 DWCB Indents (040-051), RLS Indents (023-032) - claim submitted |  | True Positive | 220
Jayhawk | Resolved | I13 |  | Warning | 1st Planetary Stage | 2022-08-27 |  | 5 |  | Monitor | [6 empty] | 10/18 - trend has been nearing/over the warning limit for over a year, slight intensification in past 6 month, shows indication of early stage Stage 1 ring fault, 11/10 - no progression | Case In Progress | -44800
Jayhawk | Resolved | I13 |  | Warning | Main Bearing | 2022-10-18 |  | 3 |  | Monitor | [6 empty] | 10/18 - trend elevated in late Sept. and has remained at that level until present, FFT shows clear ORBP fault frequency, .5g impacts on timebase, 11/10 - no progression on trend, but ocassional impacts up to ~3g on timebase, probable roller damage seen on FFT | Case In Progress | -44852
Tatanka Ridge | Resolved | J01 | S2 PC BRG Damage | Warning | 2nd Planetary Stage | 2022-09-13 |  | 1 |  | Monitor | [6 empty] | 10/7 - Damage to Stage 2 Downwind Carrier Bearing, roller damage, probably from standstill damage, 11/8 - no progression, 1/25/23 - prior claim approved | Case In Progress | -44817
Tatanka Ridge | Active | J01 | Missing CMS data | Instrumentation | Other | 2024-04-26 |  | 5 | 4/25/24 - CMS data is missing, please conduct a CBM download. | CMSTRBLSHOOT | 3342082 | Closed | Closed |  |  |  |  | Case In Progress | -45408
Jayhawk | Resolved | J02 |  | Warning | 1st Planetary Stage | 2022-05-12 |  | 3 |  | Monitor | [6 empty] | 5/24 - peaks in the GFED signal above alarm setpoint, increase in direct signal amplitude, still below warning setpoint, envelope is dominated by 3X shaft harmonics on 5/12, frequent impacts in the timebase, 6/7 - severly worn brake pad and cat 5 transverse crack on a blade. CMS may indicate roller damage to HSIS RS, S1 PS Tooth, S1 PC BRG GS rollers, borescope when Direct warning or alarm is satisfied, 6/13 - stage 1 direct now hit warning setpoint, Stage 2 Planet Fault now evident on FFT, 11/10 - no progression in trend, FFT still shows S2 Planet Fault, 12/22 - NP | Case In Progress | -44693
Jayhawk | Resolved | J02 |  | Warning | Main Bearing | 2022-08-09 |  | 5 |  | Monitor | [6 empty] | 10/18 - increase in trend after coming back online in early August, no clear fault frequencies on FFT, 11/10 - trend has settled down to normal levels, possible Roller damage seen on FFT | Case In Progress | -44782
Jayhawk | Active | J02 | Particle Counts Rising | Particle Counter | Particle Counter | 2024-01-18 |  | 6 | 1/18/24 - Particle counts rising, setting remind to check back in 1 month. | Monitor | [7 empty] | Case In Progress | -45309
Jayhawk | Resolved | J03 | S1 Planetary Accelerometer Issue | Instrumentation | 1st Planetary Stage | 2023-05-01 |  | 5 | S1 Planetary sensor accelerometer is currently reading an open circuit. Please inspect wirings and connection, replace sensor if needed. | CMSTRBLSHOOT | 3120163 | Closed | Closed |  | 2023-09-11 |  |  | Defect Confirmed - Repair Complete | 133
Jayhawk | Resolved | J03 |  | Keyphasor Issue | Keyphasor | 2022-02-08 |  |  | Check wiring next climb, replace monitor if necessary | CMSTRBLESHOOT | 2800316 |  | Closed |  | 2022-02-16 | Replace monitor if sensor troubleshoot doesn't work |  |  | 8
Jayhawk | Active | J07 | Potential Rolling element issue | Sweep | Main Bearing | 2024-03-22 |  | 4 | 5/20/24 - Borescope shows normal wear, and nothing was found that that would necessitate a replacement. 5/15/24 - sent out for main beareing borescope. 3/22/24 - CMS indicates possible early signs of rolling element issue in Main bearing, continue to monitor CMS for signs of progression | Monitor | 3351409 | Closed | Closed |  |  |  |  | Case In Progress | -45373
Jayhawk | Active | J08 | Potential Rolling element issue | Sweep | Main Bearing | 2024-06-05 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -45448
Chapada I | Resolved | JOA09-09 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2024-02-01 |  | 3 | 9/24/24 - Turbine showing signs on planetary bearing signature since ~Feb 2024. On Essentia MCE list for 2025 | Longterm Watchlist | [7 empty] | Defect Confirmed - Awaiting Repair | -45323
Chapada I | Resolved | JOA09-13 | Main Bearing ORBP | Warning | Main Bearing | 2025-07-29 |  | 2 | 7/29/25 - Main bearing outer race issue, recommend borescoping main bearing within 1 month from 7/29/25. | CMSMBBORE | SR 00286
Chapada I | Resolved | JOA09-14 | Main Bearing Damage | Alarm | Main Bearing | 2025-01-22 |  | 3 | 8/22/25 - Main bearing damage as confirmed by 2024 borescope. Bearing appears to be reaching near shutdown levels.
Chapada I | Active | JOA09-08 | Planetary Sensor Open Circuit | Instrumentation | 1st Planetary Stage | 2026-06-25 |  | 5 | 3/25/25 - Planetary accelometer currently reading an open circuit, ensure sensor is plugged in. Check wirings and connections for any breakages. Replace sensor if needed. Acelerômetro do planetário está lendo como circuito aberto. Certifique-se que o sensor está conectado. Cheque os condutores e conexões em busca de alguma falha. Troque o sensor caso seja necessário. | CMSTRBLSHOOT | SS00683
Chapada II+III | Resolved | JOA01-12 | Generator Inboard Accelerometer Open Circuit | Instrumentation | Generator Inboard | 2025-09-16 |  | 4 | 9/16/25 - Generator Inboard accelerometer reading an open circuit, recommend inspecting wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | SR 00324
Chapada I | Resolved | JOA09-15 | Main Bearing ORBP | Warning | Main Bearing | 2024-10-11 |  |  | 10/11/24 - Defect + component is on MCE list | Repair Pending | [7 empty] | Defect Confirmed - Awaiting Repair | -45576
Chapada I | Resolved | JOA10-01 | HSIS Pinion Issue | Warning | Helical Intermediate Stage | 2025-03-10 |  | 6 | 3/10/25 - Confirmed crack on the HSIS pinion (07/30/2024), turbine is currently derated. Monitoring for progression.
Chapada II+III | Active | AUG04-14 | HSIS Accelerometer | Instrumentation | Helical Intermediate Stage | 2025-11-04 |  | 3 | 11/4/25 - HSIS accelerometer is reading erronous data, please inspect wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | SR 00569
Chapada II+III | Active | AUG05-01 | Koyo Main Bearing Outer Race Issue | Warning | Main Bearing | 2024-10-11 |  | 2 | 02/11/2025 - Recommend borescoping this main bearing within 2 month from 02/11/2025 with focus on outer race. | CMSMBBORE | SS00109 |  | TBD |  |  |  |  | Case In Progress | -45576
Chapada II+III | Resolved | AUG04-14 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-01-07 |  | 3 | 6/10 - Turbine is DNRd due to crack in planetary section. 1/21/25 - Also now seeing potential secondary damage to HSS DnWind outer race. 1/14/25 - August 2023 borescope showed wear to PBs, not much progression in signature since. Recommending followup borescope within 3 months from 1/14/25 to follow defect progression. | CMSGBXBORE | SS00088 | https://app.safetyculture.com/report/audit/audit_ce9ab2e76cb14553a04120f95f183a0d
Chapada II+III | Resolved | JOA01-06 | HSIS + HSS Accelerometer Short Circuits | Instrumentation | Helical High Speed Stage | 2025-08-22 |  | 3 | 8/22/25 - Both HSS and HSIS accelerometer reading short circuit, please investigate wirings and connections. Replace sensors if needed. | CMSTRBLSHOOT | SR 00299
Chapada II+III | Resolved | AUG04-16 | HSS Rotational | Alarm | Generator Inboard | 2026-01-06 |  | 3 | 1/6/26 - Potential generator misalignment, please perform generator alignment | CMSHSS | SR 00432
Chapada I | Active | JOA09-09 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-12-31 |  | 3 | 12/31/25 - Monitor not picking up a speed signal. Please inspect keyphasor and ensure it's plugged into KPH2. | CMSTRBLSHOOT | SS00102
Chapada I | Active | JOA09-15 | Potential HSIS Pinion Issue | Warning | Helical Intermediate Stage | 2025-11-04 |  | 2 | 11/4/25 - CMS indicates potential HSIS pinion issue, recommend visual inspection of gearing within two weeks from 11/4/25. | CMSGBXBORE | SR 00371
Chapada II+III | Resolved | JOA01-06 | Generator Inboard IRBP | Warning | Generator Inboard | 2024-11-11 |  |  | 11/24/25 - Continue to monitor for amplitude increase. |  | reach out to essentia | [6 empty] | Case In Progress | -45607
Chapada I | Resolved | JOA10-06 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-06-27 |  | 3 | 6/27/25 - CMS has detected a potential planetary stage bearing issue. Recommend borescoping gearbox with focus on planetary stage within 3 months from 6/27/25. | CMSGBXBORE | SR 00262
Chapada I | Resolved | JOA10-13 | Planet Bearing Parking Marks | Warning | 1st Planetary Stage | 2025-02-27 |  | 6 | 2/27/25 - Turbine showing planet bearing signature after coming out of a long term outage. Continue to monitor.
Chapada I | Active | JOA10-02 | HSS DnWind Rear ORBP | Warning | Helical High Speed Stage | 2024-10-11 |  | 6 | 10/11/24 - HSS Bearing issue, continue to monitor for progression. | Monitor | [7 empty] | Case In Progress | -45576
Chapada II+III | Active | AUG05-01 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-06-18 |  | 3 | 6/18/25 - Potential planetary bearing issue, recommend borescope with focus on the planetary stage within 1-3 months from 6/18/25. | CMSGBXBORE | SR 00247
Chapada I | Resolved | JOA10-16 | Planetary Bearing Isssue | Warning | 1st Planetary Stage | 10/225 |  | 3 | 11/14/25 - Tubrine is currently derated since 2024.
Chapada II+III | Active | AUG05-01 | Generator Outboard Sensor Open Circuit | Instrumentation | Generator Outboard | 21/07/2026 |  |  | O acelerômetro do gerador está indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. |  | SS00730
Chapada I | Active | JOA10-04 | Generator Outboard Open Circuit | Instrumentation | Generator Outboard | 2025-11-04 |  | 3 | 11/4/25 - Non-drive end generator accelerometer is currently reading an open, please inspect wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | SR 00372
Chapada I | Active | JOA10-13 | Communication fault on the module | Instrumentation | CMS Monitor | 2026-06-25 |  |  | Foi identificado que o monitor de CMS não está comunicando adequadamente. Solicitamos que seja desplugado e plugado novamente a fim de verificar se houve o retorno da comunicação com o monitor. |  | SS00686
Chapada II+III | Resolved | JOA04-14 | HSS Rotational | Warning | Generator Inboard | 2025-02-12 |  | 3 | 2/12/25 - Potential generator misalignment, please perform generator alignment |  | SS00115
Chapada II+III | Resolved | JOA04-14 | Generator Inboard Accelerometer Open Circuit | Instrumentation | Generator Inboard | 2025-02-27 |  | 5
Chapada II+III | Resolved | JOA04-14 | HSIS Accelerometer Open Circuit | Instrumentation | Helical Intermediate Stage | 2025-08-22 |  | 3 | 8/22/25 - HSIS Accelerometer reading an open circuit, recommend inspecting wiring and connections. Replace sensor if needed. | CMSTRBLSHOOT | SR 00300
Chapada II+III | Active | AUG05-02 | Stage 2 Parellel Accelerometer Issue | Instrumentation | Helical Intermediate Stage | 2026-07-21 |  |  | Os acelerômetros do estágio intermediário estão indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00731
Chapada II+III | Active | AUG05-03 | HSS Pinion Signature | Warning | Helical High Speed Stage | 2026-07-08 |  | 4 | Solicitamos que seja realizada inspeção visual na gearbox da AUG05-03 com foco no pinhão do HSS. Não é necessário uma boroscopia. | CMSGBXBORE | SS00707 |  | TBD
Chapada II+III | Active | AUG05-04 | Keyphasor Issue | Instrumentation | Keyphasor | 2024-11-11 |  |  |  |  | SS00067 | [6 empty] | Case In Progress
Chapada II+III | Resolved | JOA07-09 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2024-11-11 |  | 3 | 3/25/25 - Turbine showing uptick in energy in the HSS section of the gearbox. Recommend derating turbine to 50% and performing secondary borescope. 12/9/24 - Recommend full gearbox borescope with focus on HSS stage and planetary stage within 3 months from 12/9/24. Recomendar boroscópio de caixa de engrenagens completa com foco no estágio HSS e estágio planetário dentro de 3 meses a partir de 09/12/24. | CMSGBXBORE | SS00069 | [6 empty] | Case In Progress | -45607
Chapada II+III | Resolved | JOA07-09 | HSS DnWind ORBP | Warning | Helical High Speed Stage | 2024-11-11 |  | 3 | 12/9/24 - Recommend full gearbox borescope with focus on HSS stage and planetary stage within 3 months from 12/9/24. Recomendar boroscópio de caixa de engrenagens completa com foco no estágio HSS e estágio planetário dentro de 3 meses a partir de 09/12/24. 3/18/25 - Borescope found heavy damages to planetary bearings, recommend replacement within 6-9 months from 3/18/25. | CMSGBXBORE | SS00069 | [6 empty] | Case In Progress | -45607
Chapada II+III | Resolved | AUG05-14 | Planetary Gearing Issue | Warning | 1st Planetary Stage | 2025-06-27 |  | 1 | 6/27/25 - Recommend full gearbox borescope within 72 hours from 6/27/25 with focus on the planetary stage. Also recommend derating turbine to 50% until an inspection can be performed. | CMSGBXBORE | SR 00261
Chapada I | Active | JOA10-14 | Generator Outboard Sensor Open Circuit | Instrumentation | Generator Outboard | 2024-12-19 |  | 5 | 12/19/24 - NDE Sensor currently reading an open circuit, please inspect wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | SS00074
Chapada I | Active | JOA10-14 | Generator Outboard Sensor Open Circuit | Instrumentation | Generator Outboard | 2026-06-25 |  |  | O acelerômetro do gerador está indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. |  | SS00684
Chapada II+III | Resolved | JOA01-15 | Potential HSS Pinion Issue | Alarm | Helical High Speed Stage | 2025-07-22 |  | 1 | 7/22/25 - Recommend visual inspection of HSS pinion teeth within 72 hours from 7/22/25. Also recommend derating turbine to 50% until inspection can be completed. | CMSHSS
Chapada II+III | Active | AUG05-06 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-12-30 |  | 2 | 12/30/25 - Potential planetary bearing signature present, recommend full gearbox borescope with focus on planetary stage within 3 months from 12/30/25 | CMSGBXBORE | SR 00429
Chapada I | Resolved | JOA09-08 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2024-10-11 |  | 2 | 11/16/24 - Gearbox failed, DNR. 10/11/24 - Long standing planetary bearing issue | Repair Pending |  |  |  |  | 2025-03-18 |  |  | Defect Confirmed - Repair Complete | 158
Chapada II+III | Active | AUG05-10 | Main Bearing ORBP | Warning | Main Bearing | 2026-02-16 |  | 3 | 2/16/26 - CMS indicates potential damage to the main bearing's outer raceways. Recommend main bearing borescope with focus on roller elements within 3 months from 2/16/26. | CMSMBBORE | SR 00459
Chapada II+III | Resolved | AUG03-08 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-06-02 |  | 2 | 5/12/26 - Damage confirmed via november 2025 borescope 6/2/25 - CMS indicates potential damage to the gearbox's planetary stage. Recommend full gearbox borescope within 2 weeks from 6/2/25 with focus on the planetary stage. | CMSGBXBORE
Chapada II+III | Active | AUG05-13 | Planetary Stage + Main Bearing Accelerometer Issue | Instrumentation | 1st Planetary Stage | 2026-07-21 |  | 4 | Foram identificados problemas de conexão com os acelerômetros do Main Bearing e do estágio planetário da gearbox da AUG05-13. Investigue a fiação dos sensores e suas conexões. Substitua o sensor se necessário. | CMSTRBLSHOOT | SR 00732
Chapada I | Active | JOA11-06 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-07-29 |  | 3 | 7/29/25 - Potential planetary bearing issue, recommend gearbox borescope within the next 3 months from 7/29/25. | CMSGBXBORE | SR 00284
Chapada I | Active | JOA11-06 | Stage 2 - Parallel accelerometer short circuit | Instrumentation | Helical Intermediate Stage | 2026-06-25 |  |  | O acelerômetro do estágio paralelo está indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. |  | SS00685
Chapada II+III | Active | AUG05-15 | Possibly Incorrect Kinematics | Warning | 1st Planetary Stage | 2024-11-11 |  | 6 | 11/11/24 - Turbine possibly has the incorrect kinematics, need to verify. | Monitor | [7 empty] | Case In Progress | -45607
Chapada I | Active | JOA11-09 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2025-03-10 |  | 3 | 3/10/25 - CMS monitor is netcom, please ensure CMS monitor is powered and ethernet is plugged into Port A. | CMSTRBLSHOOT | SR00146
Chapada II+III | Active | AUG05-15 | Potential Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-12-01 |  | 3 | 12/1/25 - Potential planetary bearing issue, recommend borescope with focus on the planetary stage within 1-3 months from 12/1/25. | CMSGBXBORE | SR 00416
Chapada I | Active | JOA11-11 | HSIS Accelerometer Short Circuit | Instrumentation | Helical Intermediate Stage | 2024-12-31 |  | 4 | 12/31/24 - HSIS sensor is currently reading a short circuit. Please inspect wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | SS00103
Chapada I | Active | JOA11-11 | Stage 2 Parallel Accelerometer Short Circuit | Instrumentation | Helical Intermediate Stage | 2026-06-25 |  |  | O acelerômetro do estágio paralelo está indicando um curto-circuito; recomenda-se inspecionar a fiação, conexões e fixação. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00687
Chapada I | Active | JOA11-12 | Generator Outboard Open Circuit | Instrumentation | Generator Outboard | 2024-12-31 |  | 4 | 12/31/24 - NDE Gen CMS sensor is currently reading a open circuit. Please inspect wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | SS00104
Chapada I | Active | JOA11-13 | Generator Outboard Accelerometer Issue | Instrumentation | Generator Outboard | 2025-03-10 |  | 5 | 3/10/25 - Generator outboard accelerometer is picking up electrical noise. Please ensure sensor and generator is properly grounded. | CMSTRBLSHOOT | SR00147
Chapada I | Active | JOA11-13 | HSS DnWind Rear IRBP + HSIS Pinion Issue | Warning | Helical Intermediate Stage | [5 empty] | SS00116
Chapada I | Resolved | JOA12-06 | Possible Planetary Stage Damages | Warning | 1st Planetary Stage | 2025-09-16 |  | 3 | 9/23/25 - Shut down due to potential catastrophic failure. 9/16/25 - Possible planetary stage damage or wear, recommend full gearbox borescope with focus on planetary stage within 1 month from 9/16/25 | CMSGBXBORE | SS00333
Chapada II+III | Active | JOA01-01 | LSIS Gear Crack | Warning | Helical Intermediate Stage | 2026-08-03 |  |  | Solicitamos uma inspeção visual, a partir da janela de inspeção do HSS, da engrenagem do LSIS, procurando por danos ou trincas nos dentes desta engrenagem. | CMSGBXBORE | SS00760
Chapada I | Resolved | JOA12-11 | HSS Rotational | Warning | Helical High Speed Stage | 2025-11-04 |  | 2 | 11/4/25 - Please perform generator alignment and check HSS coupler for any signs of damage. Also check high speed stage vibration sensor mounting and circuit for looseness and open/shorted wiring. Please create an inspection report in HUVR, including all photos and videos taken during inspection | CMSHSS | SR 00373
Chapada II+III | Active | JOA01-06 | HSS Stage Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2026-05-26 |  | 5 |  | CMSTRBLSHOOT | 03154
Chapada II+III | Active | JOA01-08 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2025-10-15 |  | 3 | 10/15/25 - CMS monitor is netcom, please ensure CMS monitor is powered and ethernet is plugged into Port A. |  | SR 00342
Chapada II+III | Active | JOA01-09 | HSS DnWind + HSIS Bearing Issue | Warning | Helical Intermediate Stage | 2024-11-11 |  | 3 | 12/9/24 - Turbine was borescoped in Jan 2024, heavy standstill marking on HSS pinion and bearing. Not much progression since, continue to monitor. 9/1/24 - Turbine showing unusually high energy in the HSIS stage, with a clear HSS dnwind signature. Recommend borescope with focus on the HSIS and HSS bearings if inspection hasn't been completed recently. | CMSGBXBORE | SS00151 | [6 empty] | Defect Confirmed - Awaiting Repair | -45607
Chapada II+III | Active | JOA01-11 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2026-05-26 |  | 3 | 5/26/26 - Potential planetary bearing issue, recommend borescopem inspection on first planetary stage within 3 months from 5/26/26. | CMSGBXBORE | SR 00619
Chapada I | Resolved | JOA12-12 | Main Bearing Open Circuit | Instrumentation | Main Bearing | 2025-05-22 |  | 4 | 5/22/25 - Main Bearing Accelerometer Open circuit, recommend inspecting wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | SR 00211
Chapada II+III | Resolved | AUG05-04 | Generator Outboard Increasing Energy | Warning | Generator Outboard | 2025-01-14 |  | 4 | 1/14/25 - Recommend adding grease to both generator bearings, take photos of current grease quality. | CMSTRBLSHOOT | SS00085
Chapada II+III | Active | JOA01-13 | Planetary Stage Accelerometer issue | Instrumentation | 1st Planetary Stage | 2025-10-15 |  | 3 | 10/15/25 - Turbine is showing possible planetary accelerometer issue, please inspect wiring and connections. Replace sensor if needed. | CMSTRBLSHOOT | SR 00349
Chapada II+III | Active | JOA01-14 | Potential Ring Gear Damage | Warning | 1st Planetary Stage | 2025-10-15 |  | 2 | 10/15/25 - Turbine is showing signs of ring gear wear, recommend full gearbox borescope with focus on planetary stage within 3 months from 10/15/25 |  | SR 00343
Chapada I | Resolved | JOA12-12 | HSS DnWInd ORBP + Planetary Bearing | Warning | 1st Planetary Stage | 2024-12-11 |  | 3 | 12/11/25 - Turbine is showing signs on planetary bearing spalling and damage to the HSS Dnwind Bearings, recommend full gearbox borescope inspection within 3 months from 12/11/24. | CMSGBXBORE | SS00070 | [6 empty] | Case In Progress | -45637
Chapada I | Active | JOA11-16 | Generator Outboard Sensor Issue | Instrumentation | Generator Outboard | 2024-12-31 |  | 4 | 12/31/24 - NDE Gen CMS sensor is currently showing a potential sensor issue. Please inspect wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | SS00105
Chapada I | Resolved | JOA12-14 | HSS Rotational | Warning | Helical High Speed Stage | 2025-11-04 |  | 2 | 11/4/25 - Please perform generator alignment and check HSS coupler for any signs of damage. Also check high speed stage vibration sensor mounting and circuit for looseness and open/shorted wiring. Please create an inspection report in HUVR, including all photos and videos taken during inspection | CMSHSS | SR 00374
Chapada I | Resolved | JOA12-16 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2026-02-03 |  |  | 2/3/26 - Planetary bearing crack
Chapada I | Active | JOA11-16 | HSIS Pinion Signature | Warning | Helical Intermediate Stage | 2025-11-14 |  | 3 | 11/14/25 - Requesting visual inspection of the HSIS stage due to abnormal spiking after downtown.
Chapada I | Active | JOA11-16 | Main bearing accelerometer short circuit | Instrumentation | Main Bearing | 2026-06-25 |  |  | Os acelerômetros do main bearing e do gerador estão indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00688
Chapada I | Active | JOA12-01 | HSS Pinion Signature | Warning | Helical High Speed Stage | 2024-12-11 |  | 6 | 12/11/24 - Turbine showing signs of parking marks on HSS and HSIS pinions, continue to monitor. | [8 empty] | Defect Confirmed - Awaiting Repair | -45637
Chapada I | Resolved | JOA15-01 | Planetary Stage Damage | Alarm | 1st Planetary Stage | 2024-12-11 |  | 6 | 12/11/24 - Turbine showing signs of significant planetary stage damages, turbine stopped on 11/21/24 | Repair Pending | [7 empty] | Defect Confirmed - Awaiting Repair | -45637
Chapada I | Active | JOA12-02 | HSS DnWind Bearing Parking Marks | Warning | Helical High Speed Stage | 2024-12-31 |  | 6 |  | Monitor
Chapada I | Active | JOA12-04 | LSIS Gear Crack | Warning | Helical High Speed Stage | 2025-01-01 |  | 2 | 1/1/25 - LSIS gear crack, continue to monitor.
Chapada I | Resolved | JOA15-06 | HSS UpWind IRBP | Warning | Helical High Speed Stage | 2025-08-18 |  | 3 | 8/18/25 - HSS UpWind IRBP signature progressing, recommend borescope inspection within the next 6 months.
Chapada I | Resolved | JOA15-07 | Potential Planetary Bearing Issue | Warning | 1st Planetary Stage | 2024-12-11 |  | 3 | 3/7/25 - Turbine experienced a planetary gearing failure and is now currently down. 12/11/24 - Turbine is showing signs on planetary bearing spalling recommend full gearbox borescope inspection within 3 months from 12/11/24. | CMSGBXBORE | SS00071 | [6 empty] | Case In Progress | -45637
Chapada I | Resolved | JOA15-08 | Planetary Gearing Issue | Warning | 1st Planetary Stage | 2025-10-21 |  | 2 | 10/21/25 - Turbine currently derated for potential planetary gearing issue
Chapada I | Active | JOA12-05 | HSS DnWind Rear ORBP | Warning | Helical High Speed Stage | 2025-09-16 |  | 5 | 9/16/25 - HSS DnWind Rear ORBP, not borescopeable. Recommend HSS assembly replacement within 6 months from 9/16/25.
Chapada II+III | Active | JOA03-02 | Main Bearing ORBP | Warning | Main Bearing | 2025-06-18 |  | 3 | 6/18/25 - Potential main bearing ORBP issue, recommend borescope with focus on the outer races within 3 months from 6/18/25. | CMSMBBORE | SR 00248
Chapada II+III | Resolved | AUG05-13 | Potential Planetary Gearing Failure | Alarm | 1st Planetary Stage | 2024-11-11 |  | 1 | 11/11/24 - Recommend performing a full gearbox borescope with focus on the planetary stage at next possible opportunity. Please shut down turbine until borescope can be completed. Recomendamos a realização de um boroscópio de caixa de engrenagens completo com foco no estágio planetário na próxima oportunidade possível. Desligue a turbina até que o boroscópio possa ser concluído. | CMSGBXBORE | SS00049 | [6 empty] | Case In Progress | -45607
Chapada II+III | Active | JOA03-04 | Main Bearing ORBP | Warning | Main Bearing | 2025-02-12 |  | 3 | 2/12/25 - Recommend borescope of the main bearing with focus on outer raceways within 3 months from 2/12/25 | CMSMBBORE | SS00114
Chapada I | Resolved | JOA15-11 | Main Bearing Open Circuit | Instrumentation | Main Bearing | 2024-12-31 |  | 4 | 12/31/24 - Main Bearing CMS sensor is currently reading a open circuit. Please inspect wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | SS00106
Chapada II+III | Active | JOA03-08 | Main Bearing ORBP | Warning | Main Bearing | 2026-01-06 |  | 2 | 1/6/26 - CMS is showing signs on a main bearing ORBP issue, recommend borescope and grease purge within 3 months from 1/6/26. | CMSMBBORE | SR 00433
Chapada II+III | Resolved | JOA05-01 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2024-11-11 |  | 2 | 11/11/24 - Turbine has had a long term planetary bearing issue that appears to have progressed into damaging the planetary gearing as well. Recommend gearbox replacement by end of 2024. | Repair Pending | [7 empty] | Defect Confirmed - Awaiting Repair | -45607
Chapada II+III | Resolved | JOA05-01 | HSS UpWind ORBP | Warning | Helical High Speed Stage | 2024-11-11 |  | 4 | 12/9/24 - Recommend borescoping turbine with focus on HSS bearings within 3 months from 12/9 |  | SS00068 | [6 empty] | Case In Progress | -45607
Chapada II+III | Active | JOA03-10 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-09-16 |  | 3 | 9/16/25 - Potential Planetary Bearing Issue, recommend full gearbox borescope with focus on plnetary stage within 3 months from 9/16/25. | CMSGBXBORE | SR 00325
Chapada II+III | Active | JOA04-02 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2024-11-11 |  | 3 | 6/13/25 - Turbine DNRd. 12/9/24 - July 24 borescope found spalling on PBs, recommend replacement by end of 2025. | Longterm Watchlist | [7 empty] | Defect Confirmed - Awaiting Repair | -45607
Chapada II+III | Resolved | JOA05-11 | Potential Main Bearing ORBP+IRBP | Warning | Main Bearing | 2025-06-30 |  | 3 | 6/30/25 - CMS indicates potential damage to the main bearing's outer raceways, recommend borescope with focus on the outer races within 3 months from 6/18/25. | CMSMBBORE | SR 00265
Chapada II+III | Active | JOA04-02 | HSS Accelerometer Short Circuit | Instrumentation | Helical High Speed Stage | 2025-05-22 |  | 4 | 5/22/25 - High speed stage accelerometer is currently reading a short circuit, please investigate wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT
Chapada II+III | Resolved | AUG03-11 | HSS DnWind Rear IRBP | Warning | Helical High Speed Stage | 2024-11-05 |  | 2 | 8/31/24 -Recommend HSS replacement within the next 6 months. | Repair Pending | SS000157 | [6 empty] | Defect Confirmed - Awaiting Repair | -45601
Chapada I | Active | JOA12-05 | HSS DnWind Rear ORBP | Warning | Helical High Speed Stage | 2026-07-02 |  | 5 | Boroscope requested to evaluate the condition of the HSS bearings and planet bearings. | CMSGBXBORE | SS00703
Chapada II+III | Resolved | AUG03-11 | HSS DnWind IRBP + HSIS Bearing Issue | Alarm | Helical High Speed Stage | 2024-10-11 | 2025-04-01 | 3 | 3/20/25 - Limitação da turbina em 50%. Requisição para o time de campo para realizar uma boroscopia completa na Gearbox. 10/11/24 - Turbine appears to have an HSS bearing issue, on uptower replacement list |  | SS000157 | [6 empty] | Defect Confirmed - Awaiting Repair | -45576
Tatanka Ridge | Resolved | K00 |  | Instrumentation | CMS Monitor | 2022-03-02 |  |  | wait | [5 empty] | 2022-03-23 | Monitor regained communications without troubleshoot |  |  | 21
Tatanka Ridge | Active | K03 | Main Bearing Sensor Issue | Instrumentation | Main Bearing | 2023-06-09 |  | 5 | 6/9/23 - Check main bearing sensor harness for open circuit | CMSTRBLSHOOT | 3141244 | Closed | Closed |  |  |  |  | Case In Progress | -45086
Tatanka Ridge | Resolved | K04 | S1 PS BRG Damage | Sweep | 1st Planetary Stage | 2023-04-04 |  | 1 | 5/11/23 - Borescope found secondary debris damage and possible planetary bearing damage. Gearbox replacement likely needed Q2-Q3 2024, CMS will continue to monitor vibration and particle counts. WEC requested 50% derate. | Longterm Watchlist | 3116859 | Closed | Closed | Q2-3 2024 |  | 4/4 - noticed on MB spectrum, started mid February 2023, planned PC install |  | Defect Confirmed - Repair Complete | -45020
Tatanka Ridge | Resolved | L01 | S2 Planetary Damage - EOW | Warning | 2nd Planetary Stage | 2021-11-25 |  | 1 | Replace for EOW claim, 50% power derate on 3/14, shutdown by GE 5/18 | Repair Pending |  |  |  |  | 2023-07-25 | 1/18/23 - EOW inspection found damage S1 and S2 planetary damage to both bearings and gears, 3/3 - increasing DEI Intermediate, lowered alarm to 0.4 for derate needs, 3/14 - increased DEI intermediate, derate | 2/10 - stage 2 FFT shows peaks at 3x and 6x shaft speed, may indicate bearing damage, 0.01 g planet fault sidebands in stage 2, 3/2 - resolving, 4/11 - reopening case for EOW serial defect tracking. Limited evidence of damage to stage 1 planet bearings. FFT shows occasional peaks at 38.344X shaft speed that does not align with known bearing or gear fault frequencies. 11/8- S1 PC RS shown in S2 FFT, trend looks fine | True Positive | 607
Tatanka Ridge | Resolved | L02 |  | Instrumentation | CMS Monitor | 2022-03-02 |  |  | wait | [5 empty] | 2022-03-23 | resolving, monitor offline due to failed PMT |  |  | 21
Tatanka Ridge | Resolved | L03 |  | Warning | Generator Inboard | 2022-01-25 |  | 5 |  | Monitor | [5 empty] | 2/10 - very early damage to DE gen bearing, 1g impacts in timebase, 0.15g peak at ORBP, 3/2 - isolated peak to the alarm setpoint on 1/25, low concern, 11/8 - time base shows modulation up to 5g, potential ORBP damage |  | Case In Progress | -44586
Tatanka Ridge | Active | L06 | Generator Outboard ORBP | Sweep | Generator Outboard | 2023-10-17 |  | 3 | 10/17/23 - Please perform an auditory and visual inspection of the generator bearings: - record audio of both bearings, take note if anything sounds off - check quantity and quality of grease in the traps - check slip ring assembly - check gen brush assembly - check vibration sensor mounting and circuit for looseness and open/shorted wiring. Add grease to both bearings Please create an inspection report in HUVR, including all photos and videos taken during inspection Contact abarndt@invenergy.com for support | CMSGENB | 3208045 | Closed | Closed |  |  |  |  | Case In Progress | -45216
Tatanka Ridge | Resolved | L08 |  | Alarm | Generator Outboard | 2022-09-13 |  | 2 |  | Monitor | [5 empty] | 10/10/22 |  | Sudden Failure | -44817
Tatanka Ridge | Resolved | L08 |  | Instrumentation | Main Bearing | 2021-11-16 |  |  | Open Sensor Wiring | CMSTRBLSHOOT | 2645599 |  | Closed |  | 2022-01-03 |  |  |  | 48
Tatanka Ridge | Resolved | L08 |  | Alarm | Main Bearing | 2021-08-13 |  | 3 |  | Monitor | [5 empty] | 2022-02-10 |  | False Positive - Sensor Issue | -44421
Tatanka Ridge | Active | L08 | CMS Troubleshoot | Instrumentation | CMS Monitor | 2024-08-06 |  | 5 | 8/6 - CMS shows instrumentation issue. | CMSTRBLSHOOT | 3398230 | Closed | Closed |  |  |  |  | Case In Progress
Tatanka Ridge | Resolved | L10 | S1 PS BRG Damage | Warning | 1st Planetary Stage | 2021-07-24 |  | 3 | Early S1 PS BRG, detected in MB signal | Monitor | [5 empty] | 10/29 - continue to monitor, 11/16 - may have already sustained damage, 3/2 - repeat warning on 2/20/22, 3/23 - monitor for progression, 6/13 - potential S2 PC BRG outer race, 11/8 - Indication of S1 GS PC roller damage |  | True Positive | -44401
Tatanka Ridge | Resolved | L11 | S1 PS BRG Damage - EOW | Warning | 2nd Planetary Stage | 2021-12-10 |  | 1 | 2/9/24 - Turbine down for EOW gearbox replacement | Repair Pending | 2687851 |  |  | Q4 2024 |  | 12/27 - peak to warning setpoint, monitor, 2/10 - 0.015g peak at Stage 2 Carrier DnWind ORBP frequency, 3/2 - resolving, 4/11 reopening case for EOW/serial defect tracking, 6/13 - modulation in stage 2 timebase, 11/8 - S2 Ring Fault Developing, 1/18/23 - EOW found S2 PS BRG indents and early spalls, S1 PS BRG raceway spalling, |  | Defect Confirmed - Repair Complete | -44540
Tatanka Ridge | Resolved | P03 |  | Warning | Helical High Speed Stage | 2022-01-07 |  | 3 |  | Monitor | [5 empty] | 2/10 - 0.2g sidebands between 2X and 3X GMF, monitor, 3/23 - 0.1g peaks at 6X and 12X stage 2 shaft speed, 6/13 - potential S2 PC BRG GS roller and outer race damage, 11/8 - less clear harmonics now, trend shows no progression |  | Case In Progress | -44568
Tatanka Ridge | Active | P04 | Potential Main bearing ORBP |  |  | 2025-02-05 |  | 5 | 2/5/2025 - Continue to monitor shows potential main bearing issue however was shut down for a prolong period of time. | Monitor | [7 empty] | Case In Progress
Tatanka Ridge | Resolved | P06 |  | Alarm | Generator Inboard | 2022-12-21 |  | 3 |  | Monitor | [5 empty] | 12/22 - very big spike on trend in Gen DE, has gone back down to regular levels, 18x freq very high |  |  | -44916
Tatanka Ridge | Active | P06 | S1 PC BRG OR damage | Sweep | 1st Planetary Stage | 2023-04-19 | 2025-04-01 | 4 | 6/18/24 - Turbine shut down until repair. 4/19/23 -CMS shows fault harmonics indicating damage to S1 PC BRG ORBP | CMSGBXBORE | 3116820 | Closed | Closed |  |  |  |  | Case In Progress | -45035
Tatanka Ridge | Resolved | P07 |  | Alarm | Generator Outboard | 2022-03-16 |  | 3 |  | Generator Replacement | 2890105 | Cancelled | Cancelled |  |  | 2022-06-18 |  | True Positive | -44636
Tatanka Ridge | Resolved | P07 |  | Instrumentation | Generator Outboard | 2022-08-19 |  |  | Wait for gen replacement to be complete | [5 empty] | 2022-09-01 |  |  |  | 13
Tatanka Ridge | Resolved | P07 | 2nd Stage Planetary Gearing Issue | Alarm | 2nd Planetary Stage | 2024-04-15 | 2024-10-06 | 2 | 4/15/24 - CMS indicates potential damage to second planetary stage gearings, sent out for full borescope with focus on 2nd stage. Currently under 50% derate | CMSGBXBORE | 3333897 | Closed | Ready to Schedule |  |  |  |  | Defect Confirmed - Repair Complete | -45397
Tatanka Ridge | Resolved | P08 |  | Instrumentation | Main Bearing | 2022-03-02 |  |  | open sensor wiring | CMSTRBLSHOOT | 2811136 |  | Cancelled |  | 2022-06-13 | Sensor issue no longer active, sensor is correctly reading vibration |  |  | 103
Tatanka Ridge | Resolved | S06 | NTN Main Bearing Outer Race Damage | Warning | Main Bearing | 2023-03-19 | 2024-12-07 | 2 | 11/19/24 - repair complete. 7/6/23 - Main bearing showing moderate pitting damage on rolling elements and inner and outer races. Recommend replacement 6-9 months from 7/6/23. | Final Report Needed | 3134562 | Closed | Closed | Q4 2024 |  | 4/5 - new roller damage since 3/1 |  | Defect Confirmed - Repair Complete | -45004
Gordon Butte | Resolved | TC-2 | Possible Generator Misalignment | Warning | Generator Outboard | 2023-02-13 |  | 2 |  | CMSGENB | 3081401 | Closed | Closed |  | 2023-05-21 | Peak at 1X HSS shaft speed, 3/7 - continue to monitor gen bearings for increases, 5/9 - gen outboard direct remains below 10g no apparent impacts in the timebase, 6/8 - monitor for increases, 8/29 - potential coupler misalignment, 10/14 - no progression, 11/3 - no progression, more evidence of potential misalignment, 12/13 - no progression |  | Defect Confirmed - Repair Complete | 97
Gordon Butte | Resolved | TC-3 |  | Instrumentation | CMS Monitor | 2022-05-17 |  |  | Lost Comms with monitor | CMSTRBLSHOOT | 2931881 | Cancelled | Cancelled |  | 2022-06-08 |  |  |  | 22
Gordon Butte | Resolved | TC-3 |  | Instrumentation | CMS Monitor | 2021-08-05 |  |  |  | CMSTRBLSHOOT | 2475054 |  | Closed |  | 2022-03-09 |  |  |  | 216
Gordon Butte | Resolved | TC-3 | HSIS Pinion Issue | Alarm | Helical Intermediate Stage | 2022-11-20 |  | 1 |  | Pending Replacement | 3051120 | Closed | Closed |  |  | 11/23 - signal suddenly peaked on 11/20 after no prior indication, S2 Pinion Fault Sidebands present and S2 GMF 1x,2x,3x harmonics, S3 Gear Fault&sidebands seen on S2 Direct High res, 12/13 - trend has settled down but still elevated signal near the Alarm amplitude, Progression of S2 Pinion fault sidebands and 3x GMF, still waiting on Borescope |  | True Positive | -44885
Gordon Butte | Resolved | TC-3 |  | Warning | Helical Intermediate Stage | 2021-09-07 |  | 5 |  | Monitor | [7 empty] | Case In Progress | -44446
Gordon Butte | Resolved | TC-3 |  | Warning | Helical Intermediate Stage | 2022-09-23 |  | 6 |  | Monitor | [8 empty] | -44827
Gordon Butte | Resolved | TC-3 |  | Alarm | Helical High Speed Stage | 2022-11-20 |  | 1 | [10 empty] | -44885
Gordon Butte | Resolved | TC-4 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2022-06-08 |  | 2 |  | CMSTRBLSHOOT | 2943378 | Closed | Closed |  |  |  |  | True Positive | -44720
Gordon Butte | Active | TC-5 | Main Bearing Damage | Warning | Main Bearing | 2022-05-20 |  | 2 |  | Monitor | 3069034 | Closed | Closed |  |  | 9/20 - peaks in the ORBP BFA signal, temps are low, 10/14 - no progression, 11/3 - No vibrations or temp progression, 1/17/23 - Some progression is signature seen over a year of data. Could potentially be parking marks, but just as likely a real defect. Escalating for borescope. |  | Case In Progress | -44701
Gordon Butte | Resolved | TC-5 |  | Instrumentation | CMS Monitor | 2022-08-05 |  |  |  | CMSTRBLSHOOT | Wait |  |  |  | 2022-09-20 | 8/29 - turbine offline for gen failure, wait to troubleshoot CMS monitor until tower is back online |  |  | 46
Gordon Butte | Resolved | TC-5 |  | Instrumentation | CMS Monitor | 2021-08-05 |  |  |  | CMSTRBLSHOOT | 2475055 |  | Closed |  | 2022-03-02 | comms restored on 3/2, closing work order though no work was noted in the WO |  |  | 209
Gordon Butte | Resolved | TC-5 |  | Instrumentation | Main Bearing | 2022-03-07 |  |  | check main bearing sensor for open wiring | CMSTRBLSHOOT | 2813121 |  | Closed |  | 2022-03-18 | 3/30 - sensor troubleshoot did not resolve issue, replacing sensor |  |  | 11
Gordon Butte | Resolved | TC-5 |  | Instrumentation | Main Bearing | 2022-03-16 |  |  | Check for open wiring, else replacce sensor | NA |  |  | Closed |  | 2022-03-17 | we love the judith gap team |  |  | 1
Gordon Butte | Resolved | TC-5 |  | Alarm | Main Bearing | 2022-03-08 |  | 1 |  | Latch Reset | [5 empty] | 2022-04-06 |  | False Positive - Sensor Issue | -44628
Gordon Butte | Active | TC-6 | HSS DnWind Rear IRBP | Alarm | Helical High Speed Stage | 2022-03-12 |  | 1 |  | Repair Pending | [5 empty] | 3/18 - alarm and warning events following no damage found in borescope and a latch reset, continue to monitor, 4/6 - no data past 3/26, FFT indicates damage to the rollers of the HSS DnWind bearing, timebase shows impacts from bearing fault, latch reset, 6/8 - LSIS GS roller fault peaks with harmonics, monitor for progression, 8/29 - additional LSIS warning event, LSIS GS roller fault as well, Stage 3 shows progression and 5g cyclical impacts in the timebase, massive pinion faults in the high resolution spectrum, 9/20 - LSIS GS roller damage appears to have progressed, 10/14 - 5g impacts still in timebase, no progression in trend, pinion faults amplitude intensifying, LSIS GS roller no progression, 11/3 - Stage 3 SER pinion fault no progression, no progression on LSIS GS, 12/13 - HSIS RS IRBP has peaked above the warning level and near alarm, S2 Direct signal is also slowly progressing, S3 HSS GS Roller damage trend progressing |  | Case In Progress | -44632
Gordon Butte | Resolved | TC-6 |  | Warning | Helical Intermediate Stage | 2021-09-27 |  | 2 |  | CMSGBXBORE | 2736989 | Closed | Closed |  |  | 2022-02-25 |  | False Positive - Sensor Issue | -44466
Gordon Butte | Resolved | TC-7 |  | Instrumentation | Helical Intermediate Stage | 2021-07-29 |  |  | Replace sensor 3 | CMSTRBLSHOOT | 2475007 |  | Closed |  | 2022-03-23 | Gearbox sensor 2 is not ok, likely requires sensor replacement, 1/25/22 - Jesse and Mike switched gearbox 2 & 3 sensors to confirm bad sensor, sensor 3 needs replacement, no sensors in stock, ordering for replacement |  |  | 237
Gordon Butte | Resolved | TC-9 |  | Instrumentation | CMS Monitor | 2021-08-05 |  |  |  | CMSTRBLSHOOT | 2475052 |  | Closed |  | 2022-05-05 | 1/25 - monitor was rebooted still lost comms, order new monitor for replacement, 5/5 - monitor replaced, configured, sychronized, and updated |  |  | 273
Gordon Butte | Resolved | TC-9 |  | Instrumentation | CMS Monitor | 2022-06-08 |  |  | Update Firmware, resolve configmismatch | [5 empty] | 2022-09-20 | 6/8 - updated firmware, lost comms with monitor. Check config when monitor is back online |  |  | 104
Blooming Grove | Active | WTG-002 | Timken Main Bearing Issue | Sweep | Main Bearing | 2024-03-26 |  | 2 | Main bearing failed DNR applied. 08/15/24 - Sent out for re-borescope due to CMS defect signature progression. 3/28/24 - Borescope found metal shavings in the grease and light denting in the races of the bearing, recommend close monitoring. 3/26/24 - CMS indicates progression to MB timken rolling elements issue 4/18/23 - Turbine is preemptively thrust derated, continue to monitor. 5/14/24 - CMS shows slight progression to main bearing defect signature | Longterm Watchlist | 3323535 | Closed | Closed | Q1 2025 |  |  |  | Defect Confirmed - Awaiting Repair | -45377
Blooming Grove | Resolved | WTG-003 |  | EOW | 1st Planetary Stage | 2022-08-23 |  | 1 |  | Monitor | [5 empty] | 12/21 - EOW found S1 PS BRG micropitting, claim rejected, limited CMS indicators |  |  | -44796
Blooming Grove | Resolved | WTG-003 | Timken Main Bearing Issue | Sweep | Main Bearing | 2023-04-11 |  | 3 | 4/14/23 - Borescope indicated some cage wear, CMS will continue to monitor for signature progression. Thrust derated | Final Report Needed | 3111647 | Closed | Closed |  |  |  |  | Defect Confirmed - Repair Complete | -45027
Blooming Grove | Active | WTG-003 | Stage 1 Planetary beaing ORBP/IRBP | Alarm | 1st Planetary Stage | 2025-02-19 |  | 3 | 1/24/25 - CMS shows indication of stage 1 ORBP/IRBP | Longterm Watchlist | 3499040 |  | Closed |  |  |  |  | Case In Progress
Blooming Grove | Resolved | WTG-006 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [5 empty] | 10/14 - EOW found brinelling and spalling on rollers and inner race, outer race micropitting, seal spacer spinning in bore, 12/21 - claim rejected |  |  | -44848
Blooming Grove | Resolved | WTG-006 |  | Warning | 2nd Planetary Stage | 2021-06-14 |  | 5 | 11/8 - Frequency spectrum has peaks around 0.06g, indicate bearing fault, 12/20 - FFT peaks around 0.02g, 1/17 -borescope at first opportunity, 6/14 - likely damage to S2 PS BRG inner race, potential mesh damage as well, limited progression. Stage 1 FFT indicates damage to S1 PC BRG rollers. Stage 3 shows clear misalignment, 10/13 - EOW found leaking carrier seal, claim submitted | Final Report Needed | [5 empty] | 11/8 - Frequency spectrum has peaks around 0.06g, indicate bearing fault, 12/20 - FFT peaks around 0.02g, 1/17 -borescope at first opportunity, 6/14 - likely damage to S2 PS BRG inner race, potential mesh damage as well, limited progression. Stage 1 FFT indicates damage to S1 PC BRG rollers. Stage 3 shows clear misalignment, 10/13 - EOW found leaking carrier seal, claim submitted |  | Case In Progress | -44361
Blooming Grove | Resolved | WTG-007 |  | Warning | Helical High Speed Stage | 2022-01-19 |  | 5 |  | Monitor |  |  |  |  | 2022-10-13 | 3/1 - peak to warning setpoint on 1/19, 6/14 - limited progression, likely misalignment, 10/13 - no damage in EOW, resolving |  | False Positive - No Inspection | 267
Blooming Grove | Resolved | WTG-009 |  | Warning | Generator Inboard | 2022-03-13 |  | 5 |  | Monitor |  |  |  |  | 2022-10-14 | 6/14 - low concern, 10/14 - no claim, resolving |  | False Positive - No Inspection | 215
Blooming Grove | Resolved | WTG-010 |  | Warning | 2nd Planetary Stage | 2022-01-19 |  | 1 |  | Monitor | [5 empty] | 3/1 - some stage 1 ring fault sidebands, less than 0.04g, 6/14 - likely stage 2 bearing damage, potentially S2 PC BRG raceways, 10/13 - EOW found S1 PS BRG end scoring and abrasions, S2 PS BRG spall and banding, 12/21 - claim rejected |  | Case In Progress | -44580
Blooming Grove | Resolved | WTG-010 |  | Warning | Main Bearing | 2021-11-01 |  | 5 |  | Monitor |  |  |  |  | 2022-10-14 | 3/1 - small peaks to warning setpoint since October, varying peaks in FFT, less than 0.008g, 6/14 - likely outer race damage to main bearing, 10/13 - no claim at EOW, missing inspection port cover, resolving |  | False Positive - No Inspection | 347
Blooming Grove | Resolved | WTG-010 | CMS Monitor Missing | Instrumentation | CMS Monitor | 2023-05-01 |  | 5 | Please order new CMS monitor and install it in this turbine. | CMSTRBLSHOOT | 3119421 | Closed | Closed |  | 2023-07-25 |  |  | Defect Confirmed - Repair Complete | 85
Blooming Grove | Resolved | WTG-010 | Timken Main Bearing Issue | GE Alert | Main Bearing | 2022-11-23 |  | 1 |  | Final Report Needed | [5 empty] | 11/28 - GE alert to derate to 50%, adding CMS spectrum to case, 12/19 - GE Alert to shutdown, claim updated, claim accepted |  | Case In Progress | -44888
Blooming Grove | Resolved | WTG-011 | Main Bearing BS2X issue | Sweep | Main Bearing | 2024-04-29 |  | 4 | msa exchanged. 5/3/24 - DLC delamination from the rollers and some secondary damage such as indents on the raceways. Turbine added to the list to replace with ongoing work at blooming grove. 5/2/24 - Sent out for main bearing borescope, CMS shows progresssion. 4/29/2024 - CMS shows an increase in noise floor and early potential BS2X signature, continue to monitor via CMS. | Longterm Watchlist | 3345504 | Closed | Closed | Q2-3 2024 |  |  |  | Defect Confirmed - Repair Complete | -45411
Blooming Grove | Resolved | WTG-012 |  | Warning | 1st Planetary Stage | 2021-12-14 |  | 5 |  | Monitor | [5 empty] | 12/14 - potential ring fault in stage 2, 12/20 - stage 2 has been between 3-5g in timeseries, occasional peaks above 5g, ring fault sidebands at 1x and 3x GMF ~0.02g, 6/14 - peak at 13.094x with harmonics indicate stage 2 bearing damage |  | Case In Progress | -44544
Blooming Grove | Active | WTG-012 | Potential S1 Planetary/Carrier Bearing Issue | Sweep | 1st Planetary Stage | 2024-08-07 |  | 3 | 10/29/24 - Potential planetary gearing defect, requested new borescope and derated tower to 50%. 8/16. Borescope found secondary damage. Continue to monitor for progresssion. 8/7 - CMS indicates potential S1 Planetary/carrier bearing issue | Longterm Watchlist | 3452968 | Closed | Closed | Q1 2025 |  |  |  | Defect Confirmed - Awaiting Repair | -45511
Blooming Grove | Resolved | WTG-015 |  | Warning | 2nd Planetary Stage | 2021-09-07 |  | 1 | Gearbox was replaced | Final Report Needed | [5 empty] | 12/21 - claim accepted pending replacement | 11/8 - sidebands at GMF varying in amplitude, 11/19 - gearbox replacement request sent to GE {{{1/17 - Borescope completed 12/21, planet bearing spalling has progressed, expected failure Spring 2022}}}, 5/26 - no obvious signs of progression, low amplitude peak in the trend may indicate recent minor progression, considering low amplitude profile of known damage, 6/14 - jump in stage 2 direct hit warning setpoint on 6/13, | True Positive | -44446
Blooming Grove | Resolved | WTG-016 |  | Alarm | Helical High Speed Stage | 2021-06-14 |  | 5 |  | Monitor | 2635789 | Closed | Closed |  |  | 12/21 - EOW found S2 PC BRGS GS spall, claim rejected, monitor | 11/8 - Frequency spectrum indicates damage to stage 3 HSS upwind bearing, CMSHSS Check, 12/20 - work completed under WO 2644708 on 11/11, no damage found, Signal begins to show 0.5-0.8g sidebands throughout FFT, concerned about Pinion and gear teeth could be vibe, 3/1 - 1.779g peak at 86X stage 3 shaft speed - cause unclear (2X GMF = 76X), 6/14 - potential stage 2 bearing damage, | Case In Progress | -44361
Blooming Grove | Active | WTG-018 | Potential Main bearing ball spin 2x issue | Sweep | Main Bearing | 2024-09-11 |  | 4 | 9/11/24 - CMS indicates potential BS2X issue continue to monitor for progression | Monitor | [7 empty] | Case In Progress | -45546
Blooming Grove | Resolved | WTG-019 | Keyphasor Issue | Instrumentation | Keyphasor | 2021-12-20 |  | 3 | ​PEM was replaced with previous tower's, encoder remained. Please inspect encoder using attached keyphasor guide. | CMSTRBLSHOOT | 2680538 | Closed | closed |  | 2023-08-07 | Gap Voltage = 4.12V, likely transducer failure, requires replacement |  | True Positive | 595
Blooming Grove | Resolved | WTG-019 | Keyphasor Issue | Instrumentation | Keyphasor | 2023-08-02 |  | 3 | CMS monitor not receiving speed signal. Please investigate keyphasor circuit using attached guide. Contact abarndt@invenergy.com for support. | CMSTRBLSHOOT | 3168306 | Closed | Closed |  | 2023-08-07 |  |  | Defect Confirmed - Repair Complete | 5
Blooming Grove | Resolved | WTG-020 |  | Warning | 2nd Planetary Stage | 2021-07-29 |  | 5 |  | Monitor | [5 empty] | 10/4 - low concern, |  | False Positive - No Inspection | -44406
Blooming Grove | Resolved | WTG-024 |  | Warning | Main Bearing | 2022-09-20 |  | 5 |  | Monitor | [5 empty] | 10/14/22 |  | False Positive - No Inspection | -44824
Blooming Grove | Resolved | WTG-024 | ZF S2 Planetary Stage Carrier Bearing | GE Alert | 1st Planetary Stage | 2021-11-29 |  | 1 | Gearbox failure | Final Report Needed |  |  |  |  | 2023-08-07 | 5/26 - Invenergy identified catastrophic damage to S1 PS BRG inner races, with indents throughout stage 1 and 2. GE sent alert on 11/29. CMS does not indicate significant progression, 6/14 - potential damage to S2 PC BRG outer race, no indication of impending failure, 12/2 - additional S2 warning events, borescope determined its ok to run until EOW replacement, 3/9/23 - Gearbox Failed |  | True Positive | 616
Blooming Grove | Active | WTG-024 | Potential Main Bearing Issue | Sweep | Main Bearing | 2023-11-21 |  | 2 | 12/06/23 - performed main bearing borescope and purge, during the inspection there were no findings of damage, could possibly be parking marks. 11/21/23 - Please perform a full main bearing borescope and upload the report to HUVR. - Take a grease sample from in between the rollers - Check vibration and temperature sensors are tightly mounted https://invenergy.sharepoint.com/sites/ODR/Procedures/Procedure_Fleet_Main_Bearing_Inspection_current.pdf | Monitor | 3228001 | Closed | Closed |  |  |  |  | False Positive | -45251
Blooming Grove | Resolved | WTG-025 |  | Warning | Helical High Speed Stage | 2022-06-14 |  | 5 |  | Monitor | [5 empty] | 10/14/22 |  | False Positive - No Inspection | -44726
Blooming Grove | Active | WTG-027 | Gearbox sensor 1 | Alarm | CMS Monitor | 2024-11-13 |  | 5 | 11/13/24 - CMS shows gearbox sensor 1 issue. | CMSTRBLSHOOT | 3464035 |  | Ready to Schedule |  |  |  |  | Case In Progress
Blooming Grove | Resolved | WTG-028 |  | Warning | Main Bearing | 2021-10-13 |  | 5 |  | Monitor | 2795998 | Closed | Closed |  |  | 2022-10-14 | 10/19 - recent peaks near alarm, impacts in timebase, temps look normal from TADS, monitor, 11/8 - timebase and freq spec amplitudes are low, potential early damage to main bearing, 12/20 - timeseries shows dramatic increase from normal operating levels around 1g, increased to 10g alarm setpoint since July, WO to check sensor mounting, | False Positive - No Inspection | -44482
Blooming Grove | Resolved | WTG-028 |  | EOW | 1st Planetary Stage | 2022-09-15 |  | 1 |  | Monitor | [5 empty] | 12/21 - EOW found S1 PS BRG RS spall, claim rejected, occasional PS BRG roller fault harmonics |  |  | -44819
Blooming Grove | Resolved | WTG-029 |  | Warning | 1st Planetary Stage | 2021-03-02 |  | 5 |  | Monitor | [5 empty] | 2022-10-14 |  | False Positive - No Inspection | -44257
Blooming Grove | Active | WTG-030 | Potential Main bearing BS2X issue | Sweep | Main Bearing | 2024-06-05 | 2025-04-02 | 5 | 6/5/24 - CMS shows potential main bearing bs2x issue, however turbine was down for a while due to gearbox repair so it probably is just parking marks. Continue to monitor for progression. | Monitor | [7 empty] | Case In Progress | -45448
Blooming Grove | Resolved | WTG-030 | S1 PS BRG IRBP issue | Sweep | 1st Planetary Stage | 2024-03-22 | 2024-06-07 | 2 | 5/30/24 - repair complete. 4/30/24 - currently DNR'd. 4/29/24 - Turbine shut down due to particle accumulation and CMS shows direct peaked at around 89g. 4/02/24 - Borescope found banding (normal wear and tear), particle mesh on S2 planet gear and S1 planet gear 3 (indentation), continue to monitor using CMS and particle counter. 3/22/24 - CMS indicates potential damage to S1 Planetary stage inner race | Longterm Watchlist | 3321244 | Closed | Closed | 2024-05-31 |  |  |  | Defect Confirmed - Repair Complete | -45373
Blooming Grove | Resolved | WTG-031 |  | Warning | 2nd Planetary Stage | 2021-09-24 |  | 1 | Gearbox was replaced | Final Report Needed | [5 empty] | 11/8 - vibration peaks hit alarm setpoint in October 11/24 - indent damage found in stage 1 planet bearing, warranty claim to be filed, 6/14 - Stage 2 high res FFT shows bearing fault sidebands, envelope indicates damage to S2 PC BRG ORBP, 10/13 - EOW claim accepted |  | Defect Confirmed - Awaiting Repair | -44463
Blooming Grove | Resolved | WTG-032 |  | EOW | 1st Planetary Stage | 2022-09-20 |  | 1 |  | Monitor | [5 empty] | 12/21 - EOW found S1 PS BRG RS spall, S2 Ring dent, claim rejected, some ring fault sidebands in S2 |  |  | -44824
Blooming Grove | Resolved | WTG-033 |  | Warning | Helical High Speed Stage | 2021-04-14 |  | 1 |  | Monitor | [5 empty] | 3/1 - 1.605g peak at 2X GMF, 12/2 - recent spike in S3 direct, 12/21 - EOW found sun drift, GE requested additional information, |  | Case In Progress | -44300
Blooming Grove | Active | WTG-034 | 1st Planetary Stage Bearing Issue | Alarm | 1st Planetary Stage | 2024-01-05 | 2025-04-04 | 2 | 2/29/24- Borescope shows indentation on S2, and potential spalling. Borescope likely missed more damage, will continue to monitor and re-borescope in a couple of months. 1/5/24 - Debris alert, and CMS indicates possible damage to the 1st planetary stage bearing, sent out for inspection/borescope | Longterm Watchlist | 3310459 | Closed | Closed |  |  |  |  | Defect Confirmed - Awaiting Repair | -45296
Blooming Grove | Resolved | WTG-036 |  | Alarm | Helical High Speed Stage | 2021-07-23 |  | 1 |  | Pending Replacement | [5 empty] | 11/8 - skeptical of GFED alarms, 1X peak = 0.966g, 2X peak = 1.369g, CMSHSS Check Recommended once GMF's carry more sidebands, 3/1 - 1g peak at 1X GMF, 5/27 - likely misalignment, 6/14 - limited progression, 9/29 - carrier damage found at EOW, 12/21 - claim accepted |  | Case In Progress | -44400
Blooming Grove | Resolved | WTG-036 | HSS Hydraulic Brake Issue | Warning | Other | 2023-04-14 |  | 2 | Please inspect HSS brake disc pads for any signs of rubbing or dragging. If no signs of issues with brake are found, please inspect HSS pinion for signs of tooth breakage. | CMSHSS | 3113023 | Closed | Closed |  | 2023-04-16 |  |  | Defect Confirmed - Repair Complete | 2
Blooming Grove | Resolved | WTG-037 | ZF S2 Planetary Stage Carrier Bearing | GE Alert | 1st Planetary Stage | 2021-11-18 |  | 1 | Gearbox failure | Final Report Needed | [5 empty] | 5/26 - GE Alert on 11/18, borescope found damage. Limited indicators in CMS, 6/14 - extremely small indications for S1 PS BRG rollers, 10/13 - EOW found gearbox damage, claim accepted, 12/21 - Additional S2 planet warnings, |  | True Positive | -44518
Blooming Grove | Resolved | WTG-039 |  | EOW | 1st Planetary Stage | 2022-09-15 |  | 1 |  | Monitor | [5 empty] | 12/21 - EOW found indents and banding throughout S1 PS BRGs, claim rejected |  |  | -44819
Blooming Grove | Resolved | WTG-041 |  | EOW | 1st Planetary Stage | 2022-09-20 |  | 1 |  | Monitor | [5 empty] | 12/21 - EOW found micropitting, standstills, and a spall on S1 PS BRGs, claim rejected |  |  | -44824
Blooming Grove | Resolved | WTG-041 |  | Warning | Main Bearing | 2022-02-17 |  | 2 |  | Monitor | [5 empty] | 3/1 - direct timeseries shows increases to the warning setpoint, 1g impact in the timebase, temps look normal compared to neighbors, monitor, 6/14 - signal now below warning setpoint after outage, |  | Case In Progress | -44609
Blooming Grove | Resolved | WTG-042 |  | Alarm | 1st Planetary Stage | 2021-09-20 |  | 5 |  | Longterm Watchlist | [7 empty] | False Negative | -44459
Blooming Grove | Resolved | WTG-042 |  | GE Alert | 1st Planetary Stage | 2021-09-21 |  | 1 |  | Repair Pending | 2938854 | Closed | Closed |  |  | 5/27 - GE Alert on 9/21, borescope found catastrophic spalling on stage 1 planet bearing. Recent increase in Stage 1 SER Sun Fault may indicate progressing damage to stage 1 bearings. Borescope, 6/14 - waiting for borescope results in HUVR, WO notes say damage is progressing, ok to run, 10/14 - EOW claim accepted, |  | True Positive | -44460
Blooming Grove | Resolved | WTG-045 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2021-10-06 |  | 2 | Troubleshoot monitor connection | CMSTRBLSHOOT | 2613915 | Closed | Closed |  | 2022-12-15 | CMS monitor is now showing up in Adapt.wind |  | True Positive | 435
Blooming Grove | Resolved | WTG-052 |  | EOW | 1st Planetary Stage | 2022-09-06 |  | 1 |  | Monitor | [6 empty] | 12/21 - EOW found S1 PC BRG RS edge chipping, S1 PS BRGs |  | -44810
Blooming Grove | Resolved | WTG-052 | Main Bearing ORBP issue | Sweep | Main Bearing | 2024-04-17 | 2024-08-03 | 2 | msa exchanged. 4/25/24 - borescope showed several sections of debris damage as well as the "golden grease" with metallic flakes, we suspect that there is likely more damage than shown in the borescope with this evidence and the CMS data. 4/17/24 - CMS indicates potential Main Bearing ORBP issue, work order sent out for CMSMBBORE inspection. | Longterm Watchlist | 3335294 | Closed | closed | Q3 2024 |  |  |  | Defect Confirmed - Repair Complete | -45399
Blooming Grove | Active | WTG-053 | S1 Planetary Carrier Issue | Sweep | 1st Planetary Stage | 2023-04-21 | 2025-04-01 | 3 | 1/3/24 - EAM notes stated that nothing catastrophic was found but there was some spalling on stage 1 and 2 bearing and gears, asked tech to upload borescope to HUVR. Continue to monitor until progression. 4/21/23 - Recommend full gearbox borescope with focus on the first planetary stage. | Monitor | 3115482 | Closed | Closed |  |  | 1/3/23 - comments from EAM state that nothing catastrophic was found but there was some spalling on stage 1 and 2 bearing and gears. |  | Case In Progress | -45037
Blooming Grove | Active | WTG-053 | Gearbox sensor 1 and Keyphasor issue | Instrumentation | CMS Monitor | 2024-09-11 |  | 5 | 9/11/24 - CMS monitor shows -22v for gearbox 1 sensor bias voltage and an invalid speed for keyphasor. Please begin troubleshooting CMS sensors | CMSTRBLSHOOT | 3426094 | Closed | Ready to Schedule |  |  |  |  | Case In Progress
Blooming Grove | Resolved | WTG-054 |  | Warning | Main Bearing | 2021-11-06 |  | 5 |  | Monitor | [5 empty] | 2022-10-14 |  | False Positive - No Inspection | -44506
Blooming Grove | Resolved | WTG-056 |  | Warning | 2nd Planetary Stage | 2021-09-20 |  | 5 |  | Monitor | [5 empty] | 2022-10-14 |  | False Positive - No Inspection | -44459
Blooming Grove | Active | WTG-056 | Potential Main bearing BS2X issue | Sweep | Main Bearing | 2024-06-05 | 2025-04-03 | 5 | 6/5/24 - CMS shows potential main bearing bs2x issue, however turbine was down for a while, which could indicate parking marks. Continue to monitor for progression. | Monitor | [7 empty] | Case In Progress | -45448
Blooming Grove | Resolved | WTG-057 | Main Bearing BS2X Signature NTN | Sweep | Main Bearing | 2024-04-24 | 2024-08-01 | 2 | msa exchanged. 4/6/4 - Borescope may have missed main damage but due to experiance with NTN main bearings its reccomended replacement is early Q3-Q4, at the latest for repair. 4/24/24 - CMS indicates damage to main bearing rolling elements, Please perform full main bearing borescope/inspection, grease sample, check vibration and temperature sensors are tightly mounted. | Longterm Watchlist | 3341540 | Closed | Closed | Q3 2024 |  |  |  | Defect Confirmed - Repair Complete | -45406
Blooming Grove | Resolved | WTG-058 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found pitting and indents on raceways and rollers, 12/21 - claim rejected | False Negative | -44848
Blooming Grove | Resolved | WTG-059 |  | Alarm | 1st Planetary Stage | 2021-11-06 |  | 5 |  | CMSGBXBORE | 2635969 | Closed | Closed |  |  |  |  | False Positive - Sensor Issue | -44506
Blooming Grove | Resolved | WTG-061 |  | Warning | 1st Planetary Stage | 2021-11-06 |  | 5 |  | Monitor | [5 empty] | 2022-10-14 |  | False Positive - No Inspection | -44506
Blooming Grove | Active | WTG-062 | Potential MB ORBP issue | Sweep | Main Bearing | 2024-10-07 |  | 5 | 11/19/24 - CMS Main bearing borescope requested. 10/7 - CMS early indications of potential MB issue. | CMSMBBORE |  |  | Ready to Schedule |  |  |  |  | Case In Progress | -45572
Blooming Grove | Active | WTG-062 | Main bearing ORBP/IRBP Issue | Alarm | Main Bearing | 2024-11-19 |  | 2 | 11/19/24 - CMS indicates potential Main bearing ORBP/IRBP issue. | CMSMBBORE | 3466484 |  | Ready to Schedule |  |  |  |  | Case In Progress | -45615
Blooming Grove | Resolved | WTG-065 |  | EOW | 1st Planetary Stage | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found S1 PS BRG micropitting and indents, S1 PC BRG RS edge chipping, 12/21 - claim rejected, S1 PS BRG fault harmonics present | False Negative | -44848
Blooming Grove | Resolved | WTG-067 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found inner race brinelling, micropitting, roller spalling, outerrace spalling and micropitting, 12/21 - claim rejected |  | -44848
Blooming Grove | Resolved | WTG-069 | HSS Hydraulic Brake Issue | Alarm | Other | 2023-02-20 |  | 2 | Please inspect HSS brake disc pads for any signs of rubbing or dragging. If no signs of issues with brake are found, please inspect HSS pinion for signs of tooth breakage. | CMSHSS | 3085501 | Closed | Closed |  | 2023-02-20 |  |  | Defect Confirmed - Repair Complete | 0
Blooming Grove | Resolved | WTG-069 |  | Instrumentation | CMS Monitor | 2022-03-01 |  |  | Replace monitor | CMSTRBLSHOOT | 2809857 |  | Closed |  | 2022-03-16 | Replace monitor |  |  | 15
Blooming Grove | Active | WTG-069 | ZF S2 Planetary Stage Carrier Bearing | EOW | 2nd Planetary Stage | 2022-10-14 | 2025-04-06 | 1 | 10/14 - EOW found S2 PS BRG indents and S2 Sun indents, 12/21 - claim accepted, monitor S2 Planet trend | Longterm Watchlist |  |  |  | Q1 2025 |  | 10/14 - EOW found S2 PS BRG indents and S2 Sun indents, 12/21 - claim accepted, monitor S2 Planet trend |  | Defect Confirmed - Awaiting Repair | -44848
Blooming Grove | Resolved | WTG-070 |  | Warning | Generator Inboard | 2021-08-27 |  | 6 |  | Monitor | [6 empty] | since 6/15/21, modulation in timebase, staying below warning levels | Case In Progress | -44435
Blooming Grove | Resolved | WTG-071 |  | Warning | 1st Planetary Stage | 2021-09-17 |  | 2 |  | Monitor | [6 empty] | 10/19 - continue to monitor, 12/20 - peak to warning setpoint on 11/29, no indicators in FFT of gear mesh damage, 2/7 - signs of damage to stage 1 carrier DnWind rollers, 6/15 - limited progression, low amplitude peaks in trend have reduced, 10/14 - EOW found leaking dust seal | Case In Progress | -44456
Blooming Grove | Resolved | WTG-072 |  | Warning | 1st Planetary Stage | 2022-01-01 |  | 5 |  | Monitor | [5 empty] | 2022-10-14 |  | False Positive - No Inspection | -44562
Blooming Grove | Resolved | WTG-072 |  | Warning | Main Bearing | 2021-10-20 |  | 1 |  | Monitor | [6 empty] | 11/8 - Impacts in timebase are worrisome, continue to monitor, 12/20 alarm level peaks August - October, FFT does not indicate specific damage. Timeseries amplitude has decreased since the fall, damage may already be sustained. PM Borescope candidate, 10/14 - EOW found spalling on rollers and raceway, 12/21 - claim rejected | Case In Progress | -44489
Blooming Grove | Resolved | WTG-073 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found inner race indents, roller spalling, outer race micropitting, hardened grease, 12/21 - claim rejected | False Negative | -44848
Blooming Grove | Active | WTG-073 | EOW, S2 Sungear shift downwind | EOW | 2nd Planetary Stage | 2022-10-14 | 2025-04-07 | 1 | 10/14/22 - EOW found S2 Sun gear shift downwind and HSS seal leak, 12/21/22 - claim accepted | Longterm Watchlist | 2372542 |  |  | Q1 2025 |  | 10/14/22 - EOW found S2 Sun gear shift downwind and HSS seal leak, 12/21/22 - claim accepted |  | Case In Progress | -44848
Blooming Grove | Resolved | WTG-076 |  | Warning | Main Bearing | 2022-04-12 |  | 1 |  | Monitor | [6 empty] | 4/12 - peak to warning setpoint, FFT shows clear peak at ORBP fault with harmonics and sidebands, 6/15 - ORBP fault harmonics only present occasionally, continue to monitor, 10/14 - EOW found roller spalling on outer race micropitting, hardened grease, 12/21 - claim rejected | True Positive | -44663
Blooming Grove | Resolved | WTG-078 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found roller spalling, raceway spall and micropitting, separated grease, 12/21 - claim rejected |  | -44848
Blooming Grove | Resolved | WTG-079 |  | EOW | 2nd Planetary Stage | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found S2 sun shifted dw, 12/21 - claim rejected, | False Negative | -44848
Blooming Grove | Resolved | WTG-079 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found foller spalling, broken off cage piece, outer race micropitting and spalling, blackened separated grease, 12/21 - claim rejected |  | -44848
Blooming Grove | Resolved | WTG-082 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found spalling on rollers and raceways, split grease, 12/21 - claim rejected | False Negative | -44848
Blooming Grove | Resolved | WTG-083 |  | EOW | 1st Planetary Stage | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found S1 PS BRG RS pitting and indents, S2 Sun pitting, 12/21 - claim rejected | False Negative | -44848
Blooming Grove | Resolved | WTG-083 |  | Warning | Main Bearing | 2022-02-04 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found roller spalling, raceways damage, split grease, 12/2 - additional warning event, 12/21 - claim rejected | True Positive | -44596
Blooming Grove | Active | WTG-083 | Potential Main Bearing Outer race Issue | Case Tracking | Main Bearing | 2022-07-27 | 2025-04-08 | 4 | 1/24/23 - EOW found roller and inner race damage. 7/27 - Thrust derate, CMS will continue to monitor for signature progression. | Longterm Watchlist |  |  |  | Q4 2024 |  | 1/24/23 - EOW found roller and inner race damage. Current CMS signature has progressed, going to followup in a month. 12/18 - alert flagged, specturm slightly increase and temp is currently at 36 C. |  | Defect Confirmed - Awaiting Repair | -44769
Blooming Grove | Resolved | WTG-084 |  | Warning | 2nd Planetary Stage | 2021-06-21 |  | 5 |  | Monitor | [5 empty] | 2022-12-21 |  | False Positive - No Inspection | -44368
Blooming Grove | Resolved | WTG-084 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found roller spalling, smearing througout, split grease12/21 - claim rejected | False Negative | -44848
Blooming Grove | Resolved | WTG-085 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found roller spalling and raceway damag, 12/21 - claim rejected | False Negative | -44848
Blooming Grove | Resolved | WTG-086 |  | Instrumentation | CMS Monitor | 2021-07-07 |  |  |  |  | 2474394 |  |  |  |  | Waiting on warranty claim to replace monitor, completed 10/28 |  |  | -44384
Blooming Grove | Resolved | WTG-086 |  | EOW | 1st Planetary Stage | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found S1 PC BRG RS spinning in bore, bubbling at outerrace and housing interface, 12/21 - claim rejected, | False Negative | -44848
Blooming Grove | Resolved | WTG-086 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found roller spalling and abrasive wear, split grease, 12/21 - claim rejected | False Negative | -44848
Blooming Grove | Resolved | WTG-087 |  | Warning | 1st Planetary Stage | 2021-12-15 |  | 5 |  | Monitor | [5 empty] | 2022-10-14 |  | False Positive - No Inspection | -44545
Blooming Grove | Resolved | WTG-087 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found spalling rollers, outer race micropitting, burnt and split grease, 12/21 - claim rejected |  | -44848
Blooming Grove | Resolved | WTG-088 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found excessive micropitting throughout, 12/21 - claim rejected | False Negative | -44848
Blooming Grove | Active | WTG-088 | ZF Flash 2nd Stage Carrier Bearing Issue | Warning | 2nd Planetary Stage | 2023-03-09 |  | 2 | 1/2/24 - Particle counts and CMS data increases drastically, turbine to be shut down until repair. 7/17/23 - Signature started Nov 2022, July 2023 borescope confirmed moderate damage to 2nd stage carrier bearings. Estimated replacement needed Q2-3 2024 | Final Report Needed | 3095270 | Closed | Closed | Q2-3 2024 |  |  |  | Defect Confirmed - Awaiting Repair | -44994
Blooming Grove | Active | WTG-088 | Gearbox 1 sensor issue/Keyphasor Issue | Instrumentation | CMS Monitor | 2024-09-04 |  | 5 | Please conduct CMS troubleshoot for incorrect gearbox 1 voltage values and keyphasor issue. | CMSTRBLSHOOT | 3414313 | Closed | Closed |  |  |  |  | Case In Progress
Blooming Grove | Resolved | WTG-089 |  | EOW | Main Bearing | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found roller spalling and inner race indents, 12/21 - claim rejected | False Negative | -44848
Blooming Grove | Resolved | WTG-089 | Potential Main Bearing BS2X, and Inner Race damage | Sweep | Main Bearing | 2024-03-22 | 2024-05-22 | 2 | 5/7/24 - turbine repaired and back online. 3/29/24 - Borescope found metal material in grease, and severe spalling, light spalling, and denting trhoughout the bearing. Both rollers found missing metal roughly 1/4'' deep on the roller. Based on CMS data and experiance with NTNs, will continue to operate derated for a few weeks. 3/22/24 - CMS indicates potential rolling element, and inner race damage. Main Bearing borescope requested. | Longterm Watchlist | 3321258 | Closed | Closed | 2024-05-16 |  |  |  | Defect Confirmed - Repair Complete | -45373
Blooming Grove | Active | WTG-089 | potential S2 Issue | Sweep | 2nd Planetary Stage | 2024-04-29 |  | 4 | 4/29/24 - CMS shows flagged for a potential S2 issue, however there is nothing in the oil particle data. Continue to monitor via CMS. | Monitor | [7 empty] | Case In Progress | -45411
Blooming Grove | Resolved | WTG-090 |  | Warning | 1st Planetary Stage | 2021-09-24 |  | 1 |  | Monitor | [6 empty] | Monitor for now, 6/15 - potential damage to S1 and S2 carriers GS, 10/14 - S1 PC BRG RS spinning in bore, bubbling between outer race and housing interface, 12/21 - claim rejected | Case In Progress | -44463
Blooming Grove | Resolved | WTG-090 | Main Bearing BS2X/Inner race issue | Sweep | Main Bearing | 2024-03-22 | 2024-08-09 | 2 | 6/15/24 - repaired 4/26/24 - Borescope found very progressed damage, should be replaced within the upcoming MCE work. 50% Derate implemented. 3/22/24 - CMS spectrum indicates potential damage to BS2X and Inner Race, please perform full main bearing borescope. | Final Report Needed | 3321198 | Closed | Closed | Q3 2024 |  |  |  | Defect Confirmed - Repair Complete | -45373
Blooming Grove | Resolved | WTG-092 |  | Alarm | Main Bearing | 2022-11-27 |  | 1 |  | Monitor | [6 empty] | 12/2 - limited indicators of damage, no damage found at EOW, |  | -44892
Blooming Grove | Resolved | WTG-093 |  | EOW | 1st Planetary Stage | 2022-10-14 |  | 1 |  | Monitor | [6 empty] | 10/14 - EOW found S1 PC BRG RS spinning in bore, bubbling at outerrace and housing interface, 12/21 - claim rejected, |  | -44848
Blooming Grove | Resolved | WTG-094 | 1st Planetary Stage Bearing Issue | Sweep | 1st Planetary Stage | 2023-07-25 | 2024-09-05 | 2 | repaired. 5/28/24 - Recommend 50% power derate due to particle count spike. 9/20/23 - Borescope found damage on S1 PBs, particle damage seen throughout the gearbox. Continue to monitor via CMS and particle data. Estimated repair date Q4 2024 - Q1 2025. 7/25/23 - Recommend full gearbox borescope with focus on 1st planetary stage within 1 month from 7/25/23. | Longterm Watchlist | 3160998 | Closed | Closed | Q1 2025 | 2024-09-02 |  |  | Defect Confirmed - Repair Complete | 405
Chapada II+III | Active | JOA04-02 | Main Bearing Accelerometer Open Circuit | Instrumentation | Main Bearing | 2025-12-01 |  | 3 | 12/1/25 - Main bearing acclerometer is currently reading an open circuit, please inspect wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | SR 00417
Chapada II+III | Active | JOA04-06 | HSIS Pinion Issue | Warning | Helical Intermediate Stage | 2024-11-11 |  | 2 | 12/9/24 - Aug 2024 found tooth breakage, recommend immediate replacement and derating turbine to 50%. 9/1/24 - Possible HSIS pinion issue, recommend inspection of the HSIS pinion for any signs of tooth breakage. Replacement likely needed at next opportunity. | Repair Pending | [7 empty] | Defect Confirmed - Awaiting Repair | -45607
Chapada II+III | Active | JOA04-07 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2026-04-20 |  | 3 | 4/20/26 - Potential planetary bearing issue, recommend borescope with focus on planetary stage within 3 months from 4/20/26. | CMSGBXBORE | SR 00525
Chapada II+III | Active | JOA04-08 | Generator Outboard Accelerometer Open Circuit | Instrumentation | Generator Outboard | 2025-02-27 |  | 5
Asa Branca | Active | ASB07-15 | Planetary Stage Accelerometer Open Circuit | Instrumentation | 1st Planetary Stage | 2025-11-10 |  | 4 | 11/10/25 - Planetary stage accelerometer is currently reading an open circuit, please inspect wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | SR 00397
Chapada I | Resolved | JOA16-02 | Potential Planetary Bearing Issue | Warning | 1st Planetary Stage | 2024-12-11 |  | 3 | 12/17/24 - Borescope found severe damage to planet bearings and rolling elements.Recommend gearbox replacement within 6 months. 12/11/24 - Turbine is showing signs on planetary bearing spalling recommend full gearbox borescope inspection within 3 months from 12/11/24. | Longterm Watchlist | [7 empty] | Defect Confirmed - Awaiting Repair | -45637
Chapada I | Active | JOA12-12 | Main Bearing Open Circuit | Instrumentation | Main Bearing | 2026-05-21 |  | 4 | 5/22/25 - Main Bearing Accelerometer Open circuit, recommend inspecting wirings and connections. Replace sensor if needed. | CMSTRBLSHOOT | SS00704
Asa Branca | Active | ASB07-16 | High Speed Stage Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2024-11-07 |  | 4 | 11/7/24 - O acelerômetro do estágio de alta está lendo como circuito aberto. Por favor investigar os enrolamentos e as conexões. Trocar o sersor se for necessário. | CMSTRBLSHOOT | SS00046
Chapada I | Active | JOA12-13 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2025-05-29 |  | 3 | 5/29/25 - CMS Monitor is netcom, please ensure monitor is power and communications is plugged into Port A | CMSTRBLSHOOT | SR 00222
AUG05-16
Chapada I | Active | JOA13-04 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-05-29 |  | 3 | 5/29/25 - Recommend full gearbox borescope with focus on planetary stage within 1-3 months from 5/29/25. | CMSGBXBORE | SR 00223
Asa Branca | Active | ASB07-16 | High Speed Stage Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2026-07-27 |  |  | Solicitamos uma inspeção nos sensores do HSS. |  | SS00746
Asa Branca | Resolved | ASB08-11 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2025-05-29 |  | 3 | 5/29/25 - CMS Monitor is netcom, please ensure monitor is power and communications is plugged into Port A | CMSTRBLSHOOT | SR 00220
Chapada I | Resolved | JOA16-09 | Planetary Gearing Failure | Warning | 1st Planetary Stage | 2024-10-17 |  | 1 | 12/31/24 - Turbine appears failed on 11/30. DNR
Chapada II+III | Active | JOA04-13 | HSIS + Main Bearing Accelerometer Open Circuit | Instrumentation | Main Bearing | 2025-07-29 |  | 4 | 7/29/25 - Main bearing and HSIS accelerometers are both reading open circuits, please investigate wirings and connections. Replace sensors if needed. | CMSTRBLSHOOT | SR 00283
Chapada II+III | Active | JOA05-04 | HSS DnWind Rear ORBP | Warning | Helical High Speed Stage | 2024-11-11 |  | 3 | 11/11/24 - Recommend replacement of HSS DnWind Rear bearing within 6 months from 11/11/24 | Longterm Watchlist | [7 empty] | Defect Confirmed - Awaiting Repair | -45607
Chapada II+III | Resolved | AUG05-13 | Planetary Stage + Main Bearing Accelerometer Issue | Instrumentation | 1st Planetary Stage |  |  | 4 | 5/14/25 - Main Bearing + Planetary stage accelerometer issues. Please investigate sensor wirings and connections, replace sensors if needed. | CMSTRBLSHOOT | SR 00207
Chapada I | Resolved | JOA13-14 | HSS + HSIS Sensor Issue | Instrumentation | Helical Intermediate Stage | 2025-12-20 |  |  | 12/16/25 - Both stage sensors are reading electrical noise. Please inspect wirings and connections, replace sensor if needed. |  | SR00430
Chapada I | Active | JOA13-08 | HSS DnWind Rear ORBP | Warning | Helical High Speed Stage |  |  |  | 11/4/25 - Continue to monitor for progression.
Asa Branca | Resolved | ASB08-15 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2025-05-29 |  | 3 | 5/29/25 - CMS Monitor is netcom, please ensure monitor is power and communications is plugged into Port A | CMSTRBLSHOOT | SR 00221
Chapada I | Active | JOA15-05 | Incorrect Kinematics
Chapada I | Active | JOA15-06 | HSS Rotational | Warning | Generator Inboard | 2025-11-14 |  | 1 | 11/14/25 - Turbine is showing large signs of imbalance, recommending the weights on the generator fan be moved and gen alignment performed.
Chapada I | Active | JOA15-12 | Main Bearing Open Circuit | Instrumentation | Main Bearing | 2025-08-05 |  | 3 | 8/5/25 - Main bearing accelerometer open circuit, recommend inspecting wiring and connections. Replace sensor if needed. | CMSTRBLSHOOT | SR 00287
Chapada I | Active | JOA15-14 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-11-04 |  | 3 | 11/4/25 - Turbine is showing signs on planetary bearing spalling recommend full gearbox borescope inspection within 3 months from 11/4/25. | CMSGBXBORE | SR 00375
Chapada I | Active | JOA16-04 | Incorrect Kinematics |  |  | 2025-03-07
Chapada I | Active | JOA16-07 | HSS DnWind Rear ORBP | Alarm | Helical High Speed Stage | 2024-12-11 |  |  | 12/11/24 - | [8 empty] | Case In Progress | -45637
Chapada I | Active | JOA16-09 | HSIS Accelerometer Issue | Instrumentation | Helical Intermediate Stage | 2025-09-23 |  | 3 | 9/23/25 - Potential HSIS accelerometer issue, please inspect wirings and connection |  | SS00334
Chapada I | Active | JOA16-10 | Generator Outboard ORBP | Warning | Generator Outboard | 2025-09-23 |  | 6 | 9/23/25 - Continue to monitor.
Chapada I | Active | JOA16-10 | Generator Outboard Open Circuit | Instrumentation
Asa Branca | Resolved | ASB04-18 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2026-05-07 |  |  | CMS Monitor is netcom, please ensure monitor is power and communications is plugged into Port A | CMSTRBLSHOOT | SS00556
Asa Branca | Resolved | ASB07-05 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2026-05-07 |  |  | CMS Monitor is netcom, please ensure monitor is power and communications is plugged into Port A | CMSTRBLSHOOT | SS00557
Asa Branca | Resolved | ASB08-12 | CMS Monitor Netcom | Instrumentation | CMS Monitor | 2026-05-08 |  |  | CMS Monitor is netcom, please ensure monitor is power and communications is plugged into Port A | CMSTRBLSHOOT | SS00563
Chapada I | Active | JOA16-11 | Keyphasor Issue | Instrumentation | Keyphasor | 2025-10-22 |  | 2 | 10/22/2025 - Monitor not picking up a speed signal. Please inspect keyphasor and ensure it's plugged into KPH2. | CMSTRBLSHOOT | SR 00350
Chapada I | Active | JOA16-13 | HSS Rotational | Alarm | Generator Inboard | 2025-12-16
Chapada II+III | Active | JOA05-05 | HSIS Accelerometer Open Circuit | Instrumentation | Helical Intermediate Stage | 2025-01-07 |  | 4 | 1/7/25 - HSIS accelerometer reading an open circuit, please investigate wirings and connecions. Replace sensor if needed. | CMSTRBLSHOOT | SS00107
|  | AUG04-11 | HSS DnWind Cage Wear | Warning | Helical High Speed Stage | 2026-07-08 |  |  | HSS DnWind cage wear identified. | Monitor
Chapada II+III | Active | JOA05-08 | Generator Inboard Accelerometer Issue | Instrumentation | Generator Inboard | 2025-02-04 |  | 5 | 2/4/25 - Please inspect sensor wirings and connections. Replace sensor isolator, ensure generator is properly grounded. | CMSTRBLSHOOT | SS00108
Chapada II+III | Active | JOA05-08 | HSIS DnWind ORBP | Warning | Helical Intermediate Stage | 2025-02-04 |  | 3 | 2/4/25 - Recommend gearbox borescope with focus on the HSIS section of the gearbox within 3 months from 2/4/25. | CMSGBXBORE | SS00110
Asa Branca | Active | ASB08-01 | Main Bearing ORBP | Warning | Main Bearing | 2025-09-16 |  | 3 | 9/16/25 - Main bearing ORBP, recommend main bearing borescope within 3 months from 9/16/25 | CMSMBBORE | SR 00326
Caetés | Active | EBR01-01 | HSS Rotational | Alarm | Generator Outboard | 2026-08-28 |  | 3 | Please perform generator alignment and check HSS coupler for any signs of damage. | CMSTRBLSHOOT | SS00868
Caetés | Active | EBR01-02 | HSS Rotational | Alarm | Generator Outboard | 2026-08-28 |  | 3 | Please perform generator alignment and check HSS coupler for any signs of damage. | CMSTRBLSHOOT | SS00869
Caetés | Active | EBR01-07 | 1st Planetary Stage Accelerometer Issue | Instrumentation | 1st Planetary Stage | 2026-08-28 |  | 3 | Os acelerômetros do estágio planetário estão indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00870
Caetés | Active | EBR02-03 | Main Bearing ORBP | Alarm | Main Bearing | 2026-08-28 |  | 3 | Dados de CMS apresentam indícios de um problema de ORBP no Main Bearing. Recomenda-se realizar uma boroscopia e uma purga de graxa. | CMSMBBORE | SS00877
Caetés | Active | EBR02-12 | Main Bearing ORBP | Alarm | Main Bearing | 2026-08-28 |  | 3 | Dados de CMS apresentam indícios de danos de pista interna e externa do Main Bearing. Recomenda-se realizar uma boroscopia e uma purga de graxa. | CMSMBBORE | SS00878
Caetés | Active | EBR02-14 | Main Bearing ORBP | Alarm | Main Bearing | 2026-08-28 |  | 3 | Dados de CMS apresentam indícios de danos de pista externa do Main Bearing. Recomenda-se realizar uma boroscopia e uma purga de graxa. | CMSMBBORE | SS00879
Caetés | Active | EBR03-03 | Generator Outboard sensor issue | Instrumentation | Generator Outboard | 2026-08-28 |  | 3 | O acelerômetro do gerador está indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00880
Chapada II+III | Active | JOA05-13 | HSIS DnWind Rear IRBP | Warning | Helical Intermediate Stage | 2025-10-15 |  | 3
Chapada II+III | Active | JOA05-14 | HSIS UpWind Bearing Issue | Warning | Helical Intermediate Stage | 2025-08-14 |  | 3 | 8/14/25 - CMS indicates damage to HSIS section bearings, recommend borescope within 3 months from 8/14/25. | CMSGBXBORE | SR 00293
Chapada II+III | Active | JOA07-01 | Planetary Stage Sensor Issue | Instrumentation | 1st Planetary Stage | 2014-12-09 |  | 3 | 1/9/25 - Planetary stage sensor is giving bad readings, recommend replacment of sensor. | CMSTRBLSHOOT | SS00152 | https://app.safetyculture.com/report/audit/audit_533bc20f94064ad9ac1e79237936525a
Asa Branca | Active | ASB08-05 | 1st Planetary Stage Accelerometer Issue | Instrumentation | 1st Planetary Stage | 2024-11-07 |  | 4 | 11/7/24 - O acelerômetro do primeiro estágio planetário está em curto-circuito. Por favor, investigue os enrolamentos e conexões. Troque o seridor, se necessário. | CMSTRBLSHOOT | SS00047
Asa Branca | Active | ASB08-06 | HSIS Accelerometer Open Circuit | Instrumentation | Helical Intermediate Stage | 2025-07-15 |  | 3 | 7/15/25 - HSIS accelerometer is currently reading an open circuit, please inspect wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | SR 00275
Asa Branca | Active | ASB08-08 | Main Bearing Accelerometer Issue | Instrumentation | Main Bearing | 2025-05-29 |  | 4 | 5/29/25 - Main bearing accelerometer is showing signs of an open circuit. Recommend check wiring and connections, replace sensor if needed. | CMSTRBLSHOOT | SR 00217
Asa Branca | Active | ASB08-10 | High Speed Stage Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2026-07-27 |  |  | Solicitamos uma inspeção nos sensores do HSS. |  | SS00747
Chapada II+III | Active | JOA07-15 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2025-02-12 |  | 3 | 2/12/25 - JOA7-015 - Recommend full gearbox borescope within 3 months from 2/12/25. | CMSGBXBORE | SS00113
Alto Sertão 2 | Active | PIL-18 | Stage 2 Parellel Accelerometer Issue | Instrumentation | Helical Intermediate Stage | 2026-08-04 |  |  | Os acelerômetros do estágio intermediário estão indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. |  | SS00765
Alto Sertão 2 | Active | SEP-08 | Communication fault on the module | Instrumentation | CMS Monitor | 2026-06-08 |  |  | Foi identificado que o monitor de CMS não está comunicando adequadamente. Solicitamos que seja desplugado e plugado novamente a fim de verificar se houve o retorno da comunicação com o monitor.
Chapada II+III | Active | AUG04-12 | HSIS Sensor Issue | Instrumentation | Helical Intermediate Stage | 2026-08-18 |  | 4 | 10/11/24 - Possible HSIS sensor issue, please investigate wirings and connections, replace sensor if needed. | CMSTRBLSHOOT | SS00835 |  | TBD
Chapada II+III | Active | AUG04-15 | Main Bearing ORBP | Warning | Main Bearing | 2026-08-18 |  | 4 | Solicitamos que seja realizada uma boroscopia no main bearing da turbina AUG04-15, com foco em seu anel externo. Após a execução da inspeção, realize a relubrificação do rolamento. | CMSTRBLSHOOT | SS00836 |  | TBD
Chapada II+III | Active | JOA01-02 | Generator Inboard Issue | Warning | Generator Inboard | 2026-08-18 |  | 4 | Solicitamos que seja realizada a relubrificação do rolamento frontal do gerador. | CMSTRBLSHOOT | SS00837 |  | TBD
Chapada II+III | Active | JOA01-05 | Generator Outboard Issue | Warning | Generator Outboard | 2026-08-18 |  | 4 | Monitor. | CMSTRBLSHOOT |  |  | TBD
Chapada II+III | Active | JOA01-07 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2026-08-18 |  | 4 | Solicitamos uma boroscopia da gearbox da turbina JOA01-07, como foco no estágio planetário e seus rolamentos. | CMSTRBLSHOOT | SS838 |  | TBD
Chapada II+III | Active | JOA01-13 | Generator Inboard Accelerometer Issue | Instrumentation | Generator Inboard | 2026-08-18 |  | 3 | O acelerômetro do gerador está indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS839
Chapada II+III | Active | JOA03-09 | Generator Inboard Accelerometer Issue | Instrumentation | Generator Inboard | 2026-08-18 |  | 3 | O acelerômetro do gerador está indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS840
Chapada II+III | Active | JOA04-10 | Planetary Bearing Issue | Warning | 1st Planetary Stage | 2026-08-18 |  | 3 | Solicitamos uma boroscopia da gearbox da turbina JOA04-10, como foco no estágio planetário e seus rolamentos. | CMSTRBLSHOOT | SS841
Chapada II+III | Active | JOA05-01 | Main Bearing issue | Warning | Main Bearing | 2026-08-18 |  | 4 | Monitor. | [7 empty] | Case In Progress | -45607
Caetés | Active | EBR03-04 | LSIS issue | Alarm | Helical Intermediate Stage | 2026-08-28 |  | 3 | Dados de CMS apresentam indícios de danos na engrenagem do segundo estágio. Recomenda-se realizar uma boroscopia com foco no segundo estágio. | CMSTRBLSHOOT | SS00881
Caetés | Active | EBR03-07 | HSIS pinion issue | Alarm | Helical Intermediate Stage | 2026-08-28 |  | 3 | Boroscopia evidencia danos no HSS e no estágio planetário. | Monitor
Caetés | Active | EBR03-08 | Main Bearing ORBP | Alarm | Main Bearing | 2026-08-28 |  | 3 | Dados de CMS apresentam indícios de danos de pista externa do Main Bearing. Recomenda-se realizar uma boroscopia e uma purga de graxa. | CMSMBBORE | SS00882
Caetés | Active | EBR03-14 | Planetary Bearing Issue | Alarm | 1st Planetary Stage | 2026-08-28 |  | 3 | Dados de CMS apresentam indícios de danos nos rolamentos dos planetas do estágio planetário da gearbox. Recomenda-se realizar uma boroscopia com foco no estágio planetário. | CMSTRBLSHOOT | SS00883
Caetés | Active | EBR03-15 | Main Bearing ORBP | Alarm | Main Bearing | 2026-08-28 |  | 3 | Dados de CMS apresentam indícios de danos de pista externa do Main Bearing. Recomenda-se realizar uma boroscopia e uma purga de graxa. | CMSMBBORE | SS00884
Caetés | Active | EBR04-03 | Planetary Bearing Issue | Alarm | 1st Planetary Stage | 2026-08-28 |  | 3 | Dados de CMS apresentam indícios de danos nos rolamentos dos planetas do estágio planetário da gearbox. Recomenda-se realizar uma boroscopia com foco no estágio planetário. | CMSTRBLSHOOT | SS00885
Caetés | Active | EBR04-08 | HSS Rotational | Alarm | Generator Outboard | 2026-08-28 |  | 3 | Please perform generator alignment and check HSS coupler for any signs of damage. | CMSTRBLSHOOT | SS00886
Caetés | Active | EBR05-09 | Main Bearing Accelerometer Issue | Instrumentation | Main Bearing | 2026-07-20 |  | 3 | Os acelerômetros do main bearing estão indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00719
Caetés | Active | EBR05-12 | Stage 2 Parellel Accelerometer Issue | Instrumentation | Helical Intermediate Stage | 2026-07-20 |  | 3 | Os acelerômetros do estágio intermediário estão indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00720
Caetés | Active | EBR05-17 | Stage 3 Parellel Accelerometer Issue | Instrumentation | Helical High Speed Stage | 2026-07-20 |  | 3 | Os acelerômetros do estágio de saída (HSS) estão indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00721
Caetés | Active | EBR06-11 | Stage 1 Planetary Accelerometer Issue | Instrumentation | 1st Planetary Stage | 2026-07-20 |  | 3 | Os acelerômetros do estágio planetário estão indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00722
Caetés | Active | EBR07-09 | Stage 2 Parellel Accelerometer Issue | Instrumentation | Helical Intermediate Stage | 2026-07-20 |  | 3 | Os acelerômetros do estágio intermediário estão indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00723
Caetés | Active | EBR07-10 | Main Bearing Accelerometer Issue | Instrumentation | Main Bearing | 2026-07-20 |  | 3 | Os acelerômetros do main bearing estão indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00724
Caetés | Active | EBR07-14 | Stage 2 Parellel Accelerometer Issue | Instrumentation | Helical Intermediate Stage | 2026-07-20 |  | 3 | Os acelerômetros do estágio intermediário estão indicando um curto-circuito; recomenda-se inspecionar a fiação e as conexões. Substitua o sensor, se necessário. | CMSTRBLSHOOT | SS00725
Caetés | Active | EBR05-04 | Main Bearing Accelerometer Issue | Alarm | Main Bearing | 2026-08-28 |  | 3 | Dados de CMS indicam que os acelerômetros do main bearing estão indicando uma leitura incorreta. | CMSTRBLSHOOT | SS00887
Caetés | Active | EBR05-08 | Intermediate Stage Issue | Alarm | Helical Intermediate Stage | 2026-08-28 |  | 3 | Dados de CMS apresentam indícios de danos no estágio intermediário da gearbox. Recomenda-se realizar uma boroscopia com foco no segundo estágio. | CMSTRBLSHOOT | SS00888
Caetés | Active | EBR05-10 | HSS DnWind Rear Bearing Issue | Alarm | Helical High Speed Stage | 2026-08-28 |  | 3 | Dados de CMS apresentam indícios de danos no rolamento down wind rear da gearbox. Recomenda-se realizar uma inspeção no filtro de óleo da gearbox para verificar existência de limalhas. | CMSTRBLSHOOT | SS00889
Caetés | Active | EBR06-09 | Planetary stage bearing issue | Alarm | 1st Planetary Stage | 2026-08-28 |  | 3 | Dados de CMS apresentam indícios de danos nos rolamentos dos planetas do estágio planetário da gearbox. Recomenda-se realizar uma boroscopia com foco no estágio planetário. | CMSTRBLSHOOT | SS00890
Caetés | Active | EBR07-02 | Planetary Accelerometer issue | Alarm | 1st Planetary Stage | 2026-08-28 |  | 3 | Dados de CMS indicam que os acelerômetros do estágio planetário estão indicando uma leitura incorreta. | CMSTRBLSHOOT | SS00891
Caetés | Active | EBR07-07 | Main Bearing IRBP | Alarm | Main Bearing | 2026-08-28 |  | 3 | Dados de CMS apresentam indícios de danos de pista interna do Main Bearing. Recomenda-se realizar uma boroscopia e uma purga de graxa. | CMSTRBLSHOOT | SS00892
Formulas:
Detection Time: = Events[[#This Row],[Date Resolved]]-Events[[#This Row],[Event Date]]

## Sites
Site | X | XXX | Owner | Operation Status | Master Access? | Platform | WTG Count | CMS Monitoring | State | Region | Site Lead | AE | Gearbox | Asset Manager (01/16/23) | Notes
Beech Ridge II | 91 |  | Southern | Out of Warranty | Yes | 2.x | 20 | Yes | WV | East |  | Sam | William | Annie
Bethel | 116 | BTH | Southern | Out of Warranty - Left rFSA, CMS TBD | Yes | 2.x | 120 | Yes | TX | Texas 2 | Erick Avila | Sam | Alex | Annie
Bishop Hill III | 66 | BH3 | WEC | Out of Warranty | Yes | 2.x | 53 | Yes | IL | Midwest | Michael Belcher | Milene | William | Tommy
Blooming Grove | 68 | BLG | WEC | Out of Warranty | Yes | 2.x | 94 | Yes | IL | Midwest | Grant Lengfelder | Milene | William | Tommy
Chicksaw |  |  | MEC |  |  | Siemens+GE | 58 | Yes |  |  |  | Sam | Alex | Abbey
Coyote Ridge | 138 | CYR | WEC | Out of Warranty | NO | 2.x | 39 | Yes | SD | Northern Plains |  | Milene | Alex | Teresa | get approval from WEC, RCS case, SCADA implement thrust derate
Desert Sky | 10.165.14.200 |  | Invenergy | Out of Warranty |  | 1.X |  | No | TX |  |  | Justin |  | Frances
Deuel Harvest | 69 | DUL | Southern | Out of Warranty | Yes | 2.x | 109 | Yes | SD | Northern Plains | Cody Kraus | Sam | William | Annie Wyman
Diversion |  |  | AEP | In Warranty |  | Sierra |  | Yes |  |  |  | Sam | Alex
Goldthwaite | 94 |  | Invenergy | rFSA | NO | 1.x-100, 2.5 | 86 | No | TX | Texas 2 |  | Max | William
Gordon Butte | 49 |  | GB Wind | Out of Warranty | YES | SLE, 2.x | 9 | Yes | MT | West |  | Sam | William | Jack?
Jayhawk | 146 | JAY | WEC | Out of Warranty | Yes | 2.82-127 | 70 | Yes | KS | Central Plains | Dave Anderson | Milene | Alex | Tommy?
Marsh Hill | 105 |  | Invenergy | rFSA | Yes | 1.x-100 | 10 | No | NY | East |  | Max | Alex
Maverick | 134 | MAV | AEP | Out of Warranty | Yes | 2.x | 103 | Yes | OK | Oklahoma | Barry Wasson | Ashley | William | Sally
Miami | 102 |  | Invenergy | rFSA | Yes | 1.x-100 | 156 | No | TX | Central Plains |  | Max | William
Number 3 (GE) |  | N3 | Invenergy | Vestas - FSA, COD ? | ?? |  | 5 | Yes | NY | East |  | Chloe | Alex | Maggie | 5 GE safe harbor, rest are Vestas FSA
Number 3 (Vestas) | [6 empty] | 26 | No |  |  |  | Chloe | Alex
Orangeville | 93 |  | Invenergy | rFSA | NO | 1.x-100 | 58 | No | NY | East |  | Max | William
Plymouth | 72 |  | MidAmerican | Out of Warranty | NO | 2.x | 73 | Yes | IA | Northern Plains | Todd Westerdahl | Sam | Alex | Abbey | ONYX Pilot, Keyphasor issue | Southern | 249
Red Barn | WIMONREDBCM01 |  | WEC | In Warranty | ?? |  | 28 | Yes | WI | Midwest | Greg Peterson | Milene | William |  | Connect to WEC Customer Server from 10,10.10.11, then to CMS server | WEC | 593 | CMS 1
Rock Creek |  |  | Pacificorp |  |  |  |  | Yes |  |  |  | Sam | Alex | Abbey
Santa Rita East | 123 | SRE | Invenergy | Out of Warranty | Yes | 2.x | 120 | Yes | TX | Texas 2 | Josh Wilson | Max | William | Cody Boebel |  | GB | 9
Sapphire Sky |  |  | WEC | Vestas - FSA, COD 12/1/22 | ?? | V150-4.2 + V136-3.6 | 64 | Yes | IL | Midwest |  | Milene | William | Tommy | Vestas | AEP | 651
Spring Canyon Exp. |  |  | Clearway | Out of Warranty |  |  |  | No | [5 empty] | Kevin Burdeck | Onyx Monitoring | MidAm | 73
Sundance | 70 | SND | AEP | Out of Warranty | Yes | 2.x | 72 | Yes | OK | Oklahoma | Jeremy Ross | Ashley | William | Sally | Need AEP permissions for derates + parameter changes
Tatanka Ridge | 63 | TTR | WEC | Out of Warranty | NO | 2.x | 56 | Yes | SD | Northern Plains |  | Milene | Alex | Teresa |  | INV | 129
Trent Mesa | 10.167.14.200
Thunderhead | 108 | THD | WEC | Out of Warranty | Yes | 2.x-127 | 108 | Yes | NE | Northern Plains | Nicholas Heithoff | Milene | Alex | Teresa |  |  | 1704
Tophat |  |  |  | Vestas - FSA, COD ? | ?? |  | 67? | No | [6 empty] | Vestas
Traverse 1 | 135 | TV1 | AEP | Out of Warranty | Yes | 2.x | 142 | Yes | OK | Oklahoma |  | Remo | William | Sally
Traverse 2 | 136 | TV2 | AEP | Out of Warranty | Yes | 2.x | 142 | Yes | OK | Oklahoma | Jeremy Cartwright | Remo | William | Sally
Traverse 3 | 137 | TV3 | AEP | Out of Warranty | Yes | 2.x | 72 | Yes | OK | Oklahoma |  | Remo | William | Sally
Trent Mesa |  |  | Invenergy | Out of Warranty |  |  |  | No | TX |  |  | Justin |  | Frances
Upstream | 122 | UPS | WEC | Out of Warranty | Yes | 2.5-116 | 82 | Yes | NE | Northern Plains | Dan Tillis | Milene | Alex | Teresa | Vibrations for T20 show up for T57 bc 57 was removed
IP Structure: | 10.X.14.200 |  |  | Case Studies
Hostname Structure | XXX-SGESCMS1.INVSCADA.LOCAL | [12 empty] | Priority | Description
[14 empty] | 1 | Immediate Action Needed
Data Validation Tables | [13 empty] | 2 | Action Needed Soon
[14 empty] | 3 | Action within 2 months
Event | Location | Priority | Case Outcome | Action | [9 empty] | 4 | Action within 6 months | 1569
Alarm | 1st Planetary Stage | 2 | Defect Confirmed - Awaiting Repair | CMSMB | [9 empty] | 5 | Next Climb
GE Alert | 2nd Planetary Stage | 3 | Defect Confirmed - Turbine Failed | CMSMBBORE | [9 empty] | 6 | Monitor
Sweep | CMS Monitor |  | Miss - Defect Not Caught | Repair Pending
Instrumentation | Generator Inboard | 5 | Defect Confirmed - Repair Complete | CMSGENB
EOW | Generator Outboard |  | False Positive | CMSTRBLSHOOT
Change 1 | Helical High Speed Stage | 4 | Case In Progress | CMSHSS
Particle Counter | Helical Intermediate Stage |  |  | Monitor
Case Tracking | Keyphasor |  |  | Longterm Watchlist
Warning | Main Bearing | 1 |  | CMSGBXBORE
| Other |  |  | GBXPARTTS
| Particle Counter |  |  | Final Report Needed

## Part Numbers
Component Name | Alternate Name(s) | GE PN | EAM PN | EAM Historic PN
Keyphasor (2.x) PEM | Pulse Extender, Tachometer | 109W2582P001 | NT00-0272A | 946300007193
Keyphasor (1.5) | Pulse Extender, Tachometer, Generator | 108W6630P001
60M100 Monitor | Bently Nevada PLC | 104W9823P002 | NALC-0016A | 946300007055
Accelerometer | CMS Sensor, Transducer | 108W9046P001 | ND00-1062A | 946300007056
Sensor Cable, Straight Connector | Wiring connector | 104W9931P010 | ND00-1852A
Sensor Cable, Right Angle Connector | Wiring connector | 104W9931P011 | ND00-2078A
CMS Module Adapter Plate | Adapts 60M100 to 3701 | 444W2207P001 | NALC-0024A
CMS Kit, 60M100, CMS, Din Rail Mount with plate |  | 104W9823D002 | WTG0-0649A | 946300007182
55.1
94.7

## Fault Frequencies
Component | Make | Ratio/Model | Subcomponent | Order | Input RPM | Hz
Main Bearing | All | 240/750 | IRBP | 16.5 |  | 0
Main Bearing | All | 240/750 | ORBP | 13.25 |  | 0
Main Bearing | NTN | 240/750 | ORBP | 12.75 |  | 0
Main Bearing | SKF | 240/750 | Ball Spin | 4.875 | 13.29 | 1.0798
Main Bearing | SKF | 240/750 | ORBP | 13 | 13.29 | 2.8795
Main Bearing | Timken | 240/750 | Ball Spin | 10.384 |  | 0
Main Bearing | Timken | 240/750 | IRBP | 15.862 |  | 0
Main Bearing | Timken | 240/750 | ORBP | 13.138 |  | 0
Gearbox | Nanjing | FDM2C | S1 PC BRG ORBP | 33.5 |  | 0
Gearbox | Nanjing | FDM2C | S1 PC BRG RS | 31 |  | 0
Gearbox | Nanjing | FDM2F | S2 PC BRG | 19.25 |  | 0
Gearbox | ZF | EH811A | S1 PS BRG IRBP | 26.5 |  | 0
Gearbox | ZF | EH811A | S1 PS BRG ORBP | 22.5 |  | 0
Gearbox | ZF | EH811A | S2 PC BRG ORBP | 28.5 |  | 0
Gearbox | Winergy | 111.9/PZAB 3505 |  |  |  | 0
Gearbox | Winergy |  |  |  |  | 0
| Winergy |  |  |  |  | 0
| Winergy |  |  |  |  | 0
| Winergy |  |  |  |  | 0
| Winergy |  |  |  |  | 0
[7 empty] | 0.43333 | 2
|  |  | 2.492 | 149.52 | 11.2506
|  |  | 2.4252 | 145.512 | 11.1932
|  | IR | 15.862 | 206.206 | 3.4368
|  | OR | 13.128 | 170.664 | 2.8444
|  | Cage | 0.547 | 7.111 | 0.11852
|  | Roller | 5.192 | 67.496 | 1.1249 | 2.2499

## Miss Tracker
Turbine: | Description of Incident: | How Found?: | CMS Failure: | Corrective Actions:
Bethel 82 | Turbine was found on to have experienced a thermal event, possibly in part caused by a failure of the main bearing that wasn't detected by CMS. | Site found turbine after the thermal event had occurred. | Turbine had a long overdue WO to fix the main bearing circuit, CMS likely could have caught indcident before catastrophic failure had occurred | • Possibly send sites an email of long overdue EAM WOs on a consistent basis Come up with a standard of when case is overdue
Sundance 49 | Customer relayed that they were seeing issues with the turbine via CMS and temp data. Turbine was then DNRd and inspected, severe outer race damage was found. | Customer notification | Turbine could've been caught weeks earlier if we had access to CMS spectrum data. With just measurement trend data, we could've caught it much earlier as well. | Working on getting CMS data into internal databases to run calculations off of and have alerting outside of the CMS server in place.
Bethel 96

## Site Specific Credentials
XXX-SGESCMS1.INVSCADA.LOCAL
Site | Column1 | XXX
Maverick | 134 | MAV
Sundance | 70 | SND
Santa Rita East | 123 | SRE
Traverse 1 | 135 | TV1
Traverse 2 | 136 | TV2 | [5 empty] | 218.3333
Traverse 3 | 137 | TV3 | [5 empty] | 19213.3333
Gordon Butte | 49 | see snip | [5 empty] | 36461.6667
Miami | 102
Marsh Hill | 105
Orangeville | 93
Goldthwaite | 94
Beech Ridge II | 91
Deuel Harvest | 69 | DUL
Bethel | 116
Bishop Hill III | 66
Blooming Grove | 68
Coyote Ridge | --
Tatanka Ridge | --
Upstream | 122
Jayhawk | 146 | JAY
Thunderhead | 127 | THD
i+pZ,'Fq8jdW
Uppercase Z F W
Red Barn: | WIRED\Abarndt | Password1234!
Maverick | 134 | MAV | AEP | None - warranty until 6/2023 | 2.x | 103
Sundance | 70 | SND | AEP | None - warranty until 4/2023 | 2.x | 72
Santa Rita East | 123 | SRE | AEP | None | 2.x | 120
Traverse 1 | 135 | TV1 | AEP | None - warranty until 6/2024 | 2.x | 88
Traverse 2 | 136 | TV2 | AEP | None - warranty until 6/2024 | 2.x | 142
Traverse 3 | 137 | TV3 | AEP | None - warranty until 6/2024 | 2.x | 72
Gordon Butte | 49 |  | GB Wind | None | SLE, 2.x | 9
Miami | 102 |  | Invenergy | rFSA | 1.x-100
Marsh Hill | 105 |  | Invenergy | rFSA | 1.x-100
Orangeville | 93 |  | Invenergy | rFSA | 1.x-100
Goldthwaite | 94 |  | Invenergy | rFSA | 1.x-100, 2.5
Number 3 |  |  | Invenergy | COD 7/1/22
Plymouth | ONYX |  | MidAmerican | COD 2/1/22 |  | 73
Beech Ridge II | 91 |  | Southern | None - warranty until 3/2022 | 2.x | 20
Deuel Harvest | 69 | DUL | Southern | None - warranty until 11/2022 | 2.x | 109
Bethel | 116 | BTH | Southern | rFSA - no reports until further notice | 2.x | 120
Bishop Hill III | 66 | BH3 | WEC | None | 2.x | 53
Blooming Grove | 68 | BLG | WEC | None - warranty until 11/2022 | 2.x | 108
Coyote Ridge | -- |  | WEC | None | 2.x | 39
Sapphire Sky | Vestas |  | WEC | Vestas - FSA, COD 12/1/22
Tatanka Ridge | -- |  | WEC | None - warranty until 12/2023 | 2.x | 56
Upstream | 122 | UPS | WEC | None | 2.x | 81
Jayhawk | 146 | JAY | WEC | None - warranty until 2023? | 2.82-127 | 70
Thunderhead | 127 | THD | WEC | COD 6/1/22 | 2.x-127 | 108
Red Barn |  |  | WPS | COD 12/31/22
[6 empty] | 1443 | 1428570

## EDUP Query
Site | WTG | SystemNumber | Main Bearing | Gearbox
Buffalo Mountain | 1 | 19371 |  | Hansen
Buffalo Mountain | 2 | 19372 |  | Hansen
Buffalo Mountain | 3 | 19373 |  | Hansen
Buffalo Mountain | 4 | 19374 |  | L&S (Bosh)
Buffalo Mountain | 5 | 19375 |  | Moventas
Buffalo Mountain | 6 | 19376 |  | Winergy
Buffalo Mountain | 7 | 19377 |  | Moventas
Buffalo Mountain | 8 | 19378 |  | Moventas
Buffalo Mountain | 9 | 19379 |  | hansen
Buffalo Mountain | 10 | 19380 |  | Moventas
Buffalo Mountain | 11 | 19381 |  | Moventas
Buffalo Mountain | 12 | 19382 |  | Hansen
Buffalo Mountain | 13 | 19383 |  | ZF
Buffalo Mountain | 14 | 19384 |  | Hansen
Buffalo Mountain | 15 | 19385 |  | Moventas
Tymien | 1 | 21248 |  | Winergy
Tymien | 2 | 21249 |  | Winergy
Tymien | 3 | 21250 |  | Hansen
Tymien | 4 | 21251 |  | Hansen
Tymien | 5 | 21252 |  | Hansen
Tymien | 6 | 21253 |  | Hansen
Tymien | 7 | 21254 |  | Hansen
Tymien | 8 | 21255 |  | Hansen
Tymien | 9 | 21256 |  | Winergy
Tymien | 10 | 21257 |  | Moventas
Tymien | 11 | 21258 |  | Hansen
Tymien | 12 | 21259 |  | Moventas
Tymien | 13 | 21260 |  | Moventas
Tymien | 14 | 21261 |  | ZF
Tymien | 15 | 21262 |  | Winergy
Tymien | 16 | 21263 |  | Moventas
Tymien | 17 | 21264 |  | Hansen
Tymien | 18 | 21265 |  | Moventas
Tymien | 19 | 21266 |  | Hansen
Tymien | 20 | 21267 |  | Winergy
Tymien | 21 | 21268 |  | Hansen
Tymien | 22 | 21269 |  | Hansen
Tymien | 23 | 21270 |  | Winergy
Tymien | 24 | 21271 |  | Moventas
Tymien | 25 | 21272 |  | Hansen
Number Three | 106 | 104782 | VESTAS | ZF
Number Three | 107 | 104783 | VESTAS | ZF
Number Three | 108 | 104784 | VESTAS | ZF
Number Three | 109 | 104785 | VESTAS | ZF
Number Three | 110 | 104786 | VESTAS | ZF
Number Three | 111 | 104787 | VESTAS | ZF
Number Three | 112 | 104788 | VESTAS | ZF
Number Three | 113 | 104789 | VESTAS | ZF
Number Three | 114 | 104790 | VESTAS | ZF
Number Three | 115 | 104791 | VESTAS | ZF
Number Three | 116 | 104792 | VESTAS | ZF
Number Three | 117 | 104793 | VESTAS | ZF
Number Three | 118 | 104794 | VESTAS | ZF
Number Three | 119 | 104795 | VESTAS | ZF
Number Three | 120 | 104796 | VESTAS | ZF
Number Three | 121 | 104797 | VESTAS | ZF
Number Three | 122 | 104798 | VESTAS | ZF
Number Three | 123 | 104799 | VESTAS | ZF
Number Three | 124 | 104800 | VESTAS | ZF
Number Three | 125 | 104801 | VESTAS | ZF
Number Three | 126 | 104802 | VESTAS | ZF
Number Three | 127 | 104803 | VESTAS | ZF
Campo Palomas | 1 | 211006 |  | Winergy
Campo Palomas | 2 | 211007 |  | Winergy
Campo Palomas | 3 | 211008 |  | Winergy
Campo Palomas | 4 | 211009 | SKF | Winergy
Campo Palomas | 5 | 211010 |  | Winergy
Campo Palomas | 6 | 211011 |  | Winergy
Campo Palomas | 7 | 211012 |  | Winergy
Campo Palomas | 8 | 211013 |  | Winergy
Campo Palomas | 9 | 211014 |  | Winergy
Campo Palomas | 10 | 211015 |  | Winergy
Campo Palomas | 11 | 211016 |  | Winergy
Campo Palomas | 12 | 211017 |  | Winergy
Campo Palomas | 13 | 211018 |  | Winergy
Campo Palomas | 14 | 211019 |  | Winergy
Campo Palomas | 15 | 211020 |  | Winergy
Campo Palomas | 16 | 211021 |  | Winergy
Campo Palomas | 17 | 211022 |  | Winergy
Campo Palomas | 18 | 211023 |  | Winergy
Campo Palomas | 19 | 211024 |  | Winergy
Campo Palomas | 20 | 211025 |  | Winergy
Campo Palomas | 21 | 211026 |  | Winergy
Campo Palomas | 22 | 211027 |  | Winergy
Campo Palomas | 23 | 211028 |  | Winergy
Campo Palomas | 24 | 211029 |  | Winergy
Campo Palomas | 25 | 211030 |  | Winergy
Campo Palomas | 26 | 211031 |  | Winergy
Campo Palomas | 27 | 211032 |  | Winergy
Campo Palomas | 28 | 211033 |  | Winergy
Campo Palomas | 29 | 211034 |  | Winergy
Campo Palomas | 30 | 211035 |  | Winergy
Campo Palomas | 31 | 211036 |  | Winergy
Campo Palomas | 32 | 211037 |  | Winergy
Campo Palomas | 33 | 211038 |  | Winergy
Campo Palomas | 34 | 211039 |  | Winergy
Campo Palomas | 35 | 211040 |  | Winergy
Flat Ridge III | 37A | 234449 | FAG | Winergy
Flat Ridge III | 1 | 234478 |  | Winergy
Flat Ridge III | 2 | 234479 | FAG | Winergy
Flat Ridge III | 4 | 234480 | Koyo | ZF
Flat Ridge III | 5 | 234481 |  | Winergy
Flat Ridge III | 7 | 234482 | FAG | Winergy
Flat Ridge III | 8 | 234483 | Koyo | Winergy
Flat Ridge III | 9 | 234484 |  | Winergy
Flat Ridge III | 10 | 234485 | Koyo | Winergy
Flat Ridge III | 11 | 234486 |  | Winergy
Flat Ridge III | 12 | 234487 | Koyo | Winergy
Flat Ridge III | 19 | 234488 |  | ZF
Flat Ridge III | 20 | 234489 | FAG | ZF
Flat Ridge III | 21 | 234490 |  | Winergy
Flat Ridge III | 23 | 234491 | FAG | Winergy
Flat Ridge III | 24 | 234492 | FAG | Winergy
Flat Ridge III | 31 | 234493 | FAG | Winergy
Flat Ridge III | 32 | 234494 | FAG | Winergy
Flat Ridge III | 33 | 234495 | FAG | Winergy
Flat Ridge III | 34 | 234496 | FAG | Winergy
Flat Ridge III | 35 | 234497 | Koyo | ZF
Flat Ridge III | 36 | 234498 | Koyo | ZF
Flat Ridge III | 79A | 234500 |  | ZF
Flat Ridge III | 39 | 234501 |  | Winergy
Flat Ridge III | 40 | 234502 | FAG | Winergy
Flat Ridge III | 41 | 234503 |  | Winergy
Flat Ridge III | 43 | 234504 | SKF | ZF
Flat Ridge III | 44 | 236209 | SKF | ZF
Flat Ridge III | 45 | 236210 | SKF | ZF
Flat Ridge III | 46 | 236211 | SKF | ZF
Flat Ridge III | 47 | 236212 | SKF | Winergy
Flat Ridge III | 48 | 236213 | SKF | ZF
Flat Ridge III | 49 | 236214 | SKF | ZF
Flat Ridge III | 51 | 236215 | SKF | ZF
Flat Ridge III | 52 | 236216 | SKF | ZF
Flat Ridge III | 74 | 236217 | SKF | ZF
Flat Ridge III | 75 | 236218 |  | ZF
Flat Ridge III | 76 | 236219 |  | ZF
Flat Ridge III | 77 | 236220 |  | ZF
Flat Ridge III | 78 | 236221 |  | ZF
Flat Ridge III | 502XX | 236222 |  | ZF
Flat Ridge III | 88 | 236223 | Koyo | ZF
Flat Ridge III | 89 | 236224 | FAG | Winergy
Flat Ridge III | 90 | 236225 | FAG | Winergy
Flat Ridge III | 3 | 236226 | SKF | ZF
Flat Ridge III | 6 | 236227 | Koyo | ZF
Flat Ridge III | 12A | 236228 | FAG | Winergy
Flat Ridge III | 16 | 236229 | FAG | Winergy
Flat Ridge III | 17 | 236230 | FAG | Winergy
Flat Ridge III | 18 | 236231 | FAG | Winergy
Flat Ridge III | 13A | 236232 |  | ZF
Flat Ridge III | 25 | 236233 | Koyo | Winergy
Flat Ridge III | 26 | 236234 | Koyo | ZF
Flat Ridge III | 13B | 236235 |  | ZF
Flat Ridge III | 15A | 236236 | Koyo | Winergy
Flat Ridge III | 50 | 236237 | Koyo | Winergy
Flat Ridge III | 53 | 236238 | SKF | ZF
Flat Ridge III | 54 | 236239 |  | ZF
Flat Ridge III | 55 | 236240 | Koyo | Winergy
Flat Ridge III | 56 | 236241 |  | Winergy
Flat Ridge III | 80A | 236242 |  | Winergy
Flat Ridge III | 91 | 236243 |  | Winergy
Chickasaw | 1 | 3100100 | Timken | Nanjing
Chickasaw | 2 | 3100101 | Timken | Nanjing
Chickasaw | 3 | 3100102 | Timken | Nanjing
Chickasaw | 4 | 3100103 | Timken | Nanjing
Chickasaw | 5 | 3100104 | Timken | Nanjing
Chickasaw | 6 | 3100105 | Timken | Nanjing
Chickasaw | 9 | 3100106 | Timken | Nanjing
Chickasaw | 10 | 3100107 | Timken | Nanjing
Chickasaw | 11 | 3100108 | Timken | Nanjing
Chickasaw | 12 | 3100109 | Timken | Nanjing
Chickasaw | 13 | 3100110 | Timken | Nanjing
Chickasaw | 14 | 3100111 | Timken | Nanjing
Chickasaw | 15 | 3100112 | Timken | Nanjing
Chickasaw | 16 | 3100113 | Timken | Nanjing
Chickasaw | 17 | 3100114 | Timken | Nanjing
Chickasaw | 18 | 3100115 | Timken | Nanjing
Chickasaw | 19 | 3100116 | Timken | Nanjing
Chickasaw | 21 | 3100117 | Timken | Nanjing
Chickasaw | 22 | 3100118 | Timken | Nanjing
Chickasaw | 23 | 3100119 | Timken | Nanjing
Chickasaw | 24 | 3100120 | Timken | Nanjing
Chickasaw | 25 | 3100121 | Timken | Nanjing
Chickasaw | 27 | 3100122 | Timken | Nanjing
Chickasaw | 29 | 3100123 | Timken | Nanjing
Chickasaw | 31 | 3100124 | Timken | Nanjing
Chickasaw | 33 | 3100125 | Timken | Nanjing
Chickasaw | 34 | 3100126 | Timken | Nanjing
Chickasaw | 35 | 3100127 | Timken | Nanjing
Chickasaw | 36 | 3100128 | Timken | Nanjing
Chickasaw | 37 | 3100129 | Timken | Nanjing
Chickasaw | 38 | 3100130 | Timken | Nanjing
Chickasaw | 39 | 3100131 | Timken | Nanjing
Chickasaw | 41 | 3100132 | Timken | Nanjing
Chickasaw | 42 | 3100133 | Timken | Nanjing
Chickasaw | 43 | 3100134 | Timken | Nanjing
Chickasaw | 44 | 3100135 | Timken | Nanjing
Chickasaw | 45 | 3100136 | Timken | Nanjing
Chickasaw | 46 | 3100137 | Timken | Nanjing
Chickasaw | 47 | 3100138 | Timken | Nanjing
Chickasaw | 48 | 3100139 | Timken | Nanjing
Chickasaw | 49 | 3100140 | Timken | Nanjing
Chickasaw | 50 | 3100141 | Timken | Nanjing
Chickasaw | 51 | 3100142 | Timken | Nanjing
Chickasaw | 52 | 3100143 | Timken | Nanjing
Chickasaw | 53 | 3100144 | Timken | Nanjing
Chickasaw | 55 | 3100145 | Timken | Nanjing
Chickasaw | 56 | 3100146 | Timken | Nanjing
Chickasaw | 58 | 3100147 | Timken | Nanjing
Chickasaw | 59 | 3100148 | Timken | Nanjing
Chickasaw | 60 | 3100149 | Timken | Nanjing
Chickasaw | 61 | 3100150 | Timken | Nanjing
Chickasaw | 63 | 3100151 | Timken | Nanjing
Chickasaw | 66 | 3100152 | Timken | Nanjing
Chickasaw | 67 | 3100153 | Timken | Nanjing
Chickasaw | 68 | 3100154 | Timken | Nanjing
Chickasaw | 82 | 3100155 | Timken | Nanjing
Chickasaw | 83 | 3100156 | Timken | Nanjing
Chickasaw | 86 | 3100157 | Timken | Nanjing
Ustka | U2/16 | 15080033 |  | Winergy
Darlowo IIIa | P18 | 15080034 |  | Winergy
Ustka | U1/03 | 15080035 |  | Winergy
Ustka | U1/04 | 15080036 | FAG | Winergy
Ustka | U2/26 | 15080037 | FAG | Winergy
Darlowo IIIa | P19 | 15080038 | FAG | Winergy
Ustka | U1/08 | 15080039
Ustka | U2/02 | 15080040 |  | Winergy
Darlowo IIIa | P5 | 15080041 |  | Winergy
Darlowo IIIa | P14 | 15080042 |  | Winergy
Ustka | U1/02 | 15080043 |  | Winergy
Darlowo IIIa | P16 | 15080044 |  | Winergy
Ustka | U1/09 | 15080045 |  | Winergy
Darlowo IIIa | P10 | 15080046 |  | Winergy
Darlowo IIIa | P2 | 15080047 |  | Winergy
Darlowo IIIa | P3 | 15080048 |  | Winergy
Ustka | U1/01 | 15080049 |  | Winergy
Ustka | U2/27 | 15080050 |  | Winergy
Darlowo IIIa | P9 | 15080051 |  | Winergy
Ustka | U2/19 | 15080052
Darlowo IIIa | P12 | 15080053 |  | Winergy
Darlowo IIIa | P4 | 15080054 |  | Winergy
Darlowo IIIa | P7 | 15080055 | FAG | Winergy
Ustka | U2/20 | 15080056 |  | Winergy
Darlowo IIIa | P6 | 15080057 | FAG | Winergy
Darlowo IIIa | P22 | 15080058 | FAG | Winergy
Ustka | U2/01 | 15080059 |  | Winergy
Ustka | U2/17 | 15080060 |  | Winergy
Darlowo IIIa | P20 | 15080061 |  | Winergy
Darlowo IIIa | P17 | 15080062 |  | Winergy
High Sheldon | A-1 | 15080870 | Timken | Winergy
High Sheldon | A-2 | 15080871 | SKF | Winergy
High Sheldon | A-3 | 15080872 | SKF | Winergy
High Sheldon | B-1 | 15080873 | SKF | Winergy
High Sheldon | B-2 | 15080874 | SKF | Winergy
High Sheldon | B-3 | 15080875 | SKF | Winergy
High Sheldon | C-1 | 15080876 | SKF | Winergy
High Sheldon | C-2 | 15080877 | SKF | Winergy
High Sheldon | C-3 | 15080878 | SKF | Moventas
High Sheldon | D-1 | 15080879 | FAG | Winergy
High Sheldon | D-2 | 15080880 | FAG | Winergy
High Sheldon | D-3 | 15080881 | SKF | Winergy
High Sheldon | D-4 | 15080882 | SKF | Winergy
High Sheldon | D-5 | 15080883 | SKF | Winergy
High Sheldon | E-1 | 15080884 | Replacement Pending | Winergy
High Sheldon | E-2 | 15080885 | FAG | Winergy
High Sheldon | E-3 | 15080886 |  | Winergy
High Sheldon | E-4 | 15080887 | Timken | Winergy
High Sheldon | E-5 | 15080888 | FAG | Winergy
High Sheldon | E-6 | 15080889 | FAG | Winergy
High Sheldon | E-7 | 15080890 | FAG | Winergy
High Sheldon | E-8 | 15080891 | SKF | Winergy
High Sheldon | E-9 | 15080892 | SKF | Winergy
High Sheldon | E-10 | 15080893 | FAG | Winergy
High Sheldon | F-1 | 15080894 | FAG | Winergy
High Sheldon | F-2 | 15080895 | FAG | Winergy
High Sheldon | F-3 | 15080896 | FAG | Winergy
High Sheldon | F-4 | 15080897 | FAG | Winergy
High Sheldon | F-5 | 15080898 | Timken | Winergy
High Sheldon | F-6 | 15080899 | FAG | Winergy
High Sheldon | F-7 | 15080900 | SKF | Winergy
High Sheldon | F-8 | 15080901 | FAG | Winergy
High Sheldon | G-1 | 15080902 | Koyo | ZF
High Sheldon | G-2 | 15080903 | SKF | Moventas
High Sheldon | G-3 | 15080904 | SKF | Nanjing
High Sheldon | G-4 | 15080905 | FAG | Winergy
High Sheldon | G-5 | 15080906 | FAG | Winergy
High Sheldon | G-6 | 15080907 | FAG | Winergy
High Sheldon | G-7 | 15080908 | FAG | Winergy
High Sheldon | H-1 | 15080909 | SKF | Winergy
High Sheldon | H-2 | 15080910 | SKF | Nanjing
High Sheldon | H-3 | 15080911 | SKF | Winergy
High Sheldon | H-4 | 15080912 | FAG | Winergy
High Sheldon | H-5 | 15080913 | SKF | Winergy
High Sheldon | H-6 | 15080914 | FAG | Nanjing
High Sheldon | H-7 | 15080915 | Timken | GETS
High Sheldon | H-8 | 15080916 | SKF | Winergy
High Sheldon | H-9 | 15080917 | SKF | Winergy
High Sheldon | I-1 | 15080918 | SKF | Nanjing
High Sheldon | I-2 | 15080919 | FAG | Nanjing
High Sheldon | I-3 | 15080920 | SKF | Winergy
High Sheldon | I-4 | 15080921 | SKF | Nanjing
High Sheldon | I-5 | 15080922 | NTN | Nanjing
High Sheldon | I-6 | 15080923 | NTN | Winergy
High Sheldon | I-7 | 15080924 | SKF | Nanjing
High Sheldon | I-8 | 15080925 | NTN | Nanjing
High Sheldon | I-9 | 15080926 | SKF | Winergy
High Sheldon | I-10 | 15080927 | SKF | GETS
High Sheldon | J-1 | 15080928 | SKF | Winergy
High Sheldon | J-2 | 15080929 | SKF | Winergy
High Sheldon | J-3 | 15080930 | SKF | Winergy
High Sheldon | J-4 | 15080931 | SKF | Nanjing
High Sheldon | J-5 | 15080932 | SKF | GETS
High Sheldon | J-6 | 15080933 | NTN | Winergy
High Sheldon | J-7 | 15080934 | SKF | GETS
High Sheldon | J-8 | 15080935 | SKF | Winergy
High Sheldon | J-9 | 15080936 | SKF | Winergy
High Sheldon | J-10 | 15080937 | Koyo | Winergy
High Sheldon | K-1 | 15080938 | SKF | Winergy
High Sheldon | K-2 | 15080939 | SKF | GETS
High Sheldon | K-3 | 15080940 | NTN | GETS
High Sheldon | K-4 | 15080941 | SKF | Winergy
High Sheldon | L-1 | 15080942 | NTN | Moventas
High Sheldon | L-2 | 15080943 | FAG | Winergy
High Sheldon | L-3 | 15080944 | SKF | Winergy
Vantage | 29 | 15081711 | NTN | Winergy
Vantage | 30 | 15081712 | NTN | Winergy
Vantage | 31 | 15081713 | NTN | Winergy
Vantage | 33 | 15081714 | NTN | Winergy
Vantage | 34 | 15081715 | NTN | Winergy
Vantage | 35 | 15081716 | NTN | Winergy
Vantage | 36 | 15081717 | NTN | Winergy
Vantage | 37 | 15081718 | NTN | Winergy
Vantage | 38 | 15081719 | NTN | Winergy
Vantage | 39 | 15081720 | NTN | Winergy
Vantage | 40 | 15081721 | NTN | Moventas
Vantage | 41 | 15081722 | NTN | Winergy
Vantage | 42 | 15081723 | SKF | Winergy
Vantage | 43 | 15081724 | NTN | Winergy
Vantage | 44 | 15081725 | NTN | Winergy
Vantage | 45 | 15081726 | NTN | Winergy
Vantage | 46 | 15081727 | Timken | Winergy
Vantage | 47 | 15081728 | SKF | Nanjing
Vantage | 48 | 15081729 | NTN | Winergy
Vantage | 49 | 15081730 | SKF | Winergy
Vantage | 50 | 15081731 | SKF | Winergy
Vantage | 51 | 15081732 | SKF | Winergy
Vantage | 52 | 15081733 | SKF | Winergy
Vantage | 53 | 15081734 | SKF | Winergy
Vantage | 54 | 15081735 | SKF | Winergy
Vantage | 55 | 15081736 | NTN | Winergy
Vantage | 56 | 15081737 | SKF | Nanjing
Vantage | 57 | 15081738 | SKF | GETS
Vantage | 58 | 15081739 | SKF | Winergy
Vantage | 59 | 15081740 | Koyo | Winergy
Vantage | 60 | 15081741 | NTN | Winergy
Vantage | 61 | 15081742 | SKF | Winergy
Vantage | 62 | 15081743 | NTN | Nanjing
Vantage | 1 | 15090290 | NTN | Winergy
Vantage | 2 | 15090291 | NTN | Winergy
Vantage | 3 | 15090292 | Koyo | Winergy
Vantage | 4 | 15090293 | NTN | Winergy
Vantage | 5 | 15090294 | NTN | Winergy
Vantage | 6 | 15090295 | NTN | Winergy
Vantage | 7 | 15090296 | Koyo
Vantage | 8 | 15090297 | NTN | Winergy
Vantage | 9 | 15090298 | Koyo | Winergy
Vantage | 10 | 15090299 | NTN | Winergy
Vantage | 11 | 15090300 | Koyo | Winergy
Vantage | 12 | 15090301 | Koyo | Winergy
Vantage | 13 | 15090302 | Koyo | Winergy
Vantage | 14 | 15090303 | NTN | Winergy
Vantage | 15 | 15090304 | NTN | Rexroth
Vantage | 16 | 15090305 | NTN | Winergy
Vantage | 17 | 15090306 | NTN | Winergy
Vantage | 18 | 15090307 | NTN | Winergy
Vantage | 19 | 15090308 | NTN | Winergy
Vantage | 20 | 15090309 | NTN | Winergy
Vantage | 21 | 15090310 | NTN | Winergy
Vantage | 22 | 15090311 | NTN | Winergy
Vantage | 23 | 15090312 | NTN | Winergy
Vantage | 24 | 15090313 | NTN | Winergy
Vantage | 26 | 15090314 | NTN | Winergy
Vantage | 27 | 15090315 | NTN | Winergy
Vantage | 28 | 15090316 | NTN | Winergy
Fowler Ridge II | A-001 | 15090492 | SKF | Moventas
Fowler Ridge II | A-002 | 15090493 | NTN | Moventas
Fowler Ridge II | A-003 | 15090494 | SKF | Moventas
Fowler Ridge II | A-004 | 15090495 | NTN | Winergy
Fowler Ridge II | A-005 | 15090496 | NTN | Winergy
Fowler Ridge II | A-006 | 15090497 | Koyo | Moventas
Fowler Ridge II | A-007 | 15090498 | Koyo | Winergy
Fowler Ridge II | A-008 | 15090499 | NTN | Winergy
Fowler Ridge II | A-009 | 15090500 | NTN | Rexroth
Fowler Ridge II | A-010 | 15090501 | Koyo | Winergy
Fowler Ridge II | A-011 | 15090502 | NTN | Winergy
Fowler Ridge II | A-012 | 15090503 | NTN | Winergy
Fowler Ridge II | A-013 | 15090504 | NTN | Winergy
Fowler Ridge II | A-014 | 15090505 | NTN | Rexroth
Fowler Ridge II | A-015 | 15090506 | SKF | Winergy
Fowler Ridge II | B-016 | 15090507 | SKF | Moventas
Fowler Ridge II | B-017 | 15090508 |  | Winergy
Fowler Ridge II | B-018 | 15090509 | NTN | Winergy
Fowler Ridge II | B-019 | 15090510 | SKF | Moventas
Fowler Ridge II | B-020 | 15090511 | NTN | Winergy
Fowler Ridge II | B-021 | 15090512 | SKF | Moventas
Fowler Ridge II | B-022 | 15090513 | SKF | Moventas
Fowler Ridge II | B-023 | 15090514 | SKF | Moventas
Fowler Ridge II | B-024 | 15090515 | SKF | Winergy
Fowler Ridge II | B-025 | 15090516 | SKF | Winergy
Fowler Ridge II | B-026 | 15090517 | SKF | Nanjing
Fowler Ridge II | B-027 | 15090518 | SKF | Moventas
Fowler Ridge II | B-028 | 15090519 | Koyo | GETS
Fowler Ridge II | B-029 | 15090520 | SKF | Winergy
Fowler Ridge II | B-030 | 15090521 | SKF | Winergy
Fowler Ridge II | C-031 | 15090522 | NTN | Winergy
Fowler Ridge II | C-032 | 15090523 | SKF | Nanjing
Fowler Ridge II | C-033 | 15090524 | NTN | Rexroth
Fowler Ridge II | C-034 | 15090525 | Koyo | GETS
Fowler Ridge II | C-035 | 15090526 | SKF | GETS
Fowler Ridge II | C-036 | 15090527 | SKF | GETS
Fowler Ridge II | C-037 | 15090528 | SKF | Winergy
Fowler Ridge II | C-038 | 15090529 | SKF | Moventas
Fowler Ridge II | C-039 | 15090530 | SKF | Rexroth
Fowler Ridge II | C-040 | 15090531 | SKF | Rexroth
Fowler Ridge II | C-041 | 15090532 | SKF | Rexroth
Fowler Ridge II | C-042 | 15090533 | SKF | Rexroth
Fowler Ridge II | C-043 | 15090534 | SKF | Winergy
Fowler Ridge II | C-044 | 15090535 | SKF | Moventas
Fowler Ridge II | C-045 | 15090536 | SKF | Moventas
Fowler Ridge II | D-046 | 15090537 | SKF | Winergy
Fowler Ridge II | D-047 | 15090538 | SKF | Moventas
Fowler Ridge II | D-048 | 15090539 | SKF | Moventas
Fowler Ridge II | D-049 | 15090540 | SKF | Rexroth
Fowler Ridge II | D-050 | 15090541 | SKF | Winergy
Fowler Ridge II | D-051 | 15090542 | SKF | Winergy
Fowler Ridge II | D-052 | 15090543 | SKF | Winergy
Fowler Ridge II | D-053 | 15090544 | SKF | Winergy
Fowler Ridge II | D-054 | 15090545 | SKF | Moventas
Fowler Ridge II | D-055 | 15090546 | SKF | Moventas
Fowler Ridge II | D-056 | 15090547 | SKF | Moventas
Fowler Ridge II | D-057 | 15090548 | SKF | Rexroth
Fowler Ridge II | D-058 | 15090549 | SKF | Rexroth
Fowler Ridge II | D-059 | 15090550 | SKF | Nanjing
Fowler Ridge II | D-060 | 15090551 | SKF | Winergy
Fowler Ridge II | D-061 | 15090552 |  | Moventas
Fowler Ridge II | E-062 | 15090553 | NTN | Winergy
Fowler Ridge II | E-063 | 15090554 | NTN | Winergy
Fowler Ridge II | E-064 | 15090555 | SKF | Rexroth
Fowler Ridge II | E-065 | 15090556 | NTN | Nanjing
Fowler Ridge II | E-066 | 15090557 | SKF | GETS
Fowler Ridge II | E-067 | 15090558 | NTN | Winergy
Fowler Ridge II | E-068 | 15090559 | SKF | Nanjing
Fowler Ridge II | E-069 | 15090560 | NTN | Nanjing
Fowler Ridge II | E-070 | 15090561 | SKF | Moventas
Fowler Ridge II | E-071 | 15090562 | SKF | Winergy
Fowler Ridge II | F-072 | 15090563 | SKF | Moventas
Fowler Ridge II | F-073 | 15090564 | FAG | Winergy
Fowler Ridge II | F-074 | 15090565 | FAG | Winergy
Fowler Ridge II | F-075 | 15090566 | SKF | Winergy
Fowler Ridge II | F-076 | 15090567 | SKF | Moventas
Fowler Ridge II | F-077 | 15090568 | SKF | Winergy
Fowler Ridge II | F-078 | 15090569 | FAG | Winergy
Fowler Ridge II | F-079 | 15090570 | SKF | Moventas
Fowler Ridge II | F-080 | 15090571 | FAG | Winergy
Fowler Ridge II | F-081 | 15090572 | FAG | Winergy
Fowler Ridge II | F-082 | 15090573 | FAG | Winergy
Fowler Ridge II | F-083 | 15090574 | FAG | Winergy
Fowler Ridge II | F-084 | 15090575 | SKF | Moventas
Fowler Ridge II | F-085 | 15090576 | SKF | Winergy
Fowler Ridge II | F-086 | 15090577 | SKF | Winergy
Fowler Ridge II | F-087 | 15090578 | SKF | Winergy
Fowler Ridge II | G-088 | 15090579 | SKF | Winergy
Fowler Ridge II | G-089 | 15090580 | SKF | Moventas
Fowler Ridge II | G-090 | 15090581 | SKF | Winergy
Fowler Ridge II | G-091 | 15090582 | SKF | Winergy
Fowler Ridge II | G-092 | 15090583 | NTN | Winergy
Fowler Ridge II | G-093 | 15090584 | SKF | Nanjing
Fowler Ridge II | G-094 | 15090585 | SKF | Winergy
Fowler Ridge II | G-095 | 15090586 | SKF | Nanjing
Fowler Ridge II | G-096 | 15090587 | SKF | Winergy
Fowler Ridge II | G-097 | 15090588 | FAG | Winergy
Fowler Ridge II | G-098 | 15090589 | SKF | Winergy
Fowler Ridge II | G-099 | 15090590 | FAG | Winergy
Fowler Ridge II | G-100 | 15090591 | SKF | Winergy
Fowler Ridge II | G-101 | 15090592 | FAG | Moventas
Fowler Ridge II | G-102 | 15090593 | FAG | Winergy
Fowler Ridge II | H-103 | 15090594 | SKF | Rexroth
Fowler Ridge II | H-104 | 15090595 | SKF | GETS
Fowler Ridge II | H-105 | 15090596 | SKF | Winergy
Fowler Ridge II | H-106 | 15090597 | SKF | Winergy
Fowler Ridge II | H-107 | 15090598 | Koyo | Nanjing
Fowler Ridge II | H-108 | 15090599 | SKF | Winergy
Fowler Ridge II | H-109 | 15090600 | NTN | Winergy
Fowler Ridge II | H-110 | 15090601 | NTN | Winergy
Fowler Ridge II | H-111 | 15090602 | SKF | GETS
Fowler Ridge II | H-112 | 15090603 | SKF | Winergy
Fowler Ridge II | H-113 | 15090604 | SKF | Rexroth
Fowler Ridge II | H-114 | 15090605 | SKF | Rexroth
Fowler Ridge II | H-115 | 15090606 | SKF | Nanjing
Fowler Ridge II | H-116 | 15090607 | SKF | Moventas
Fowler Ridge II | H-117 | 15090608 | NTN | Winergy
Fowler Ridge II | H-118 | 15090609 | SKF | Nanjing
Fowler Ridge II | I-119 | 15090610 | SKF | Moventas
Fowler Ridge II | I-120 | 15090611 | NTN | Winergy
Fowler Ridge II | I-121 | 15090612 | SKF | Winergy
Fowler Ridge II | I-122 | 15090613 | SKF | Winergy
Fowler Ridge II | I-123 | 15090614 | SKF | Winergy
Fowler Ridge II | I-124 | 15090615 | NTN | Winergy
Fowler Ridge II | I-125 | 15090616 | SKF | GETS
Fowler Ridge II | I-126 | 15090617 | SKF | GETS
Fowler Ridge II | I-127 | 15090618 | SKF | Winergy
Fowler Ridge II | I-128 | 15090619 | SKF | Winergy
Fowler Ridge II | I-129 | 15090620 | SKF | GETS
Fowler Ridge II | I-130 | 15090621 | SKF | GETS
Fowler Ridge II | I-131 | 15090622 | SKF | GETS
Fowler Ridge II | I-132 | 15090623 | SKF | GETS
Fowler Ridge II | I-133 | 15090624 | SKF | Winergy
Beech Ridge | G-1 | 15090711 | SKF | Winergy
Beech Ridge | G-2 | 15090712 | SKF | Winergy
Beech Ridge | G-3 | 15090713 | SKF | Nanjing
Beech Ridge | G-4 | 15090714 | SKF | Winergy
Beech Ridge | G-5 | 15090715 | SKF | Nanjing
Beech Ridge | G-6 | 15090716 | SKF | Winergy
Beech Ridge | G-7 | 15090717 | SKF | Winergy
Beech Ridge | G-8 | 15090718 | SKF | GETS
Beech Ridge | G-9 | 15090719 | SKF | Winergy
Beech Ridge | G-10 | 15090720 | SKF | GETS
Beech Ridge | G-11 | 15090721 | SKF | Winergy
Beech Ridge | G-12 | 15090722 | SKF | Winergy
Beech Ridge | G-15 | 15090723 | SKF | GETS
Beech Ridge | E-8 | 15090724 | SKF | GETS
Beech Ridge | E-9 | 15090725 | SKF | Winergy
Beech Ridge | F-2 | 15090726 | SKF | Winergy
Beech Ridge | G-13 | 15090727 | SKF | Winergy
Beech Ridge | G-14 | 15090728 | SKF | Winergy
Beech Ridge | G-16 | 15090729 | SKF | Winergy
Beech Ridge | G-17 | 15090730 | Timken | GETS
Beech Ridge | H-10 | 15090731 | NTN | Winergy
Beech Ridge | J-1 | 15090732 | NTN | Winergy
Beech Ridge | J-2 | 15090733 | SKF | Winergy
Beech Ridge | A-11 | 15090734 | NTN | Winergy
Beech Ridge | A-12 | 15090735 | SKF | GETS
Beech Ridge | A-13 | 15090736 | SKF | Winergy
Beech Ridge | A-14 | 15090737 | Timken | ZF
Beech Ridge | A-15 | 15090738 | SKF | Winergy
Beech Ridge | A-16 | 15090739 | NTN | Winergy
Beech Ridge | A-17 | 15090740 | SKF | Winergy
Beech Ridge | A-18 | 15090741 | Timken | Nanjing
Beech Ridge | A-19 | 15090742 | SKF | Winergy
Beech Ridge | B-1 | 15090743 | SKF | GETS
Beech Ridge | B-3 | 15090744 | SKF | Winergy
Beech Ridge | B-4 | 15090745 | SKF | Winergy
Beech Ridge | B-5 | 15090746 | SKF | Winergy
Beech Ridge | B-6 | 15090747 | NTN | Winergy
Beech Ridge | B-7 | 15090748 | SKF | Winergy
Beech Ridge | E-1 | 15090749 | SKF | ZF
Beech Ridge | E-2 | 15090750 | SKF | GETS
Beech Ridge | E-3 | 15090751 | SKF | Rexroth
Beech Ridge | E-4 | 15090752 | SKF | Winergy
Beech Ridge | E-5 | 15090753 | SKF | Winergy
Beech Ridge | E-6 | 15090754 | SKF | Winergy
Beech Ridge | E-7 | 15090755 | SKF | Winergy
Beech Ridge | E-11 | 15090756 | SKF | Rexroth
Beech Ridge | E-12 | 15090757 | SKF | Winergy
Beech Ridge | E-13 | 15090758 | SKF | Winergy
Beech Ridge | H-1 | 15090759 | NTN
Beech Ridge | H-2 | 15090760 | NTN | Winergy
Beech Ridge | H-3 | 15090761 | NTN | Winergy
Beech Ridge | H-4 | 15090762 | SKF | Winergy
Beech Ridge | H-5 | 15090763 | SKF | GETS
Beech Ridge | H-6 | 15090764 | SKF | GETS
Beech Ridge | H-7 | 15090765 | SKF | Winergy
Beech Ridge | H-8 | 15090766 | SKF | Winergy
Beech Ridge | H-9 | 15090767 | SKF | GETS
Beech Ridge | J-3 | 15090768 | SKF | Winergy
Beech Ridge | J-5 | 15090769 | SKF | Moventas
Beech Ridge | J-6 | 15090770 | SKF | Winergy
Beech Ridge | J-7 | 15090771 | SKF | GETS
Beech Ridge | F-3 | 15090772 | SKF | ZF
Beech Ridge | F-4 | 15090773 | SKF | Winergy
Beech Ridge | F-5 | 15090774 | NTN | Winergy
Beech Ridge | F-6 | 15090775 | SKF | Winergy
Beech Ridge | F-7 | 15090776 | SKF | Winergy
Beech Ridge | F-8 | 15090777 | NTN | Winergy
Gordon Butte | TC-1 | 15723131 |  | Winergy
Gordon Butte | TC-2 | 15723132 |  | Winergy
Gordon Butte | TC-3 | 15723133 |  | Winergy
Gordon Butte | TC-4 | 15723134 |  | Winergy
Gordon Butte | TC-5 | 15723135 |  | Winergy
Gordon Butte | TC-6 | 15723136 |  | Winergy
Cedar Creek II | G-1 | 16101828 | NTN | Nanjing
Cedar Creek II | G-2 | 16101829 | NTN | Nanjing
Cedar Creek II | G-3 | 16101830 | NTN | Nanjing
Cedar Creek II | G-4 | 16101831 | Koyo | Nanjing
Cedar Creek II | G-5 | 16101832 | Koyo | Nanjing
Cedar Creek II | G-6 | 16101833 | Koyo | Nanjing
Cedar Creek II | G-7 | 16101834 | Koyo | Winergy
Cedar Creek II | G-8 | 16101835 | NTN | Winergy
Cedar Creek II | G-9 | 16101836 | Koyo | Nanjing
Cedar Creek II | G-10 | 16101837 | NTN | Nanjing
Cedar Creek II | G-11 | 16101838 | Koyo | Nanjing
Cedar Creek II | G-12 | 16101839 | Koyo | Nanjing
Cedar Creek II | G-13 | 16101840 | Koyo | Nanjing
Cedar Creek II | G-14 | 16101841 | Koyo | Nanjing
Cedar Creek II | G-15 | 16101842 | Koyo | Nanjing
Cedar Creek II | G-16 | 16101843 | Koyo | Nanjing
Cedar Creek II | G-17 | 16101844 | Koyo | Nanjing
Cedar Creek II | G-18 | 16101845 | Koyo | Nanjing
Cedar Creek II | G-19 | 16101846 | Koyo | Nanjing
Cedar Creek II | G-20 | 16101847 | Koyo | Nanjing
Cedar Creek II | G-21 | 16101848 | Koyo | Nanjing
Cedar Creek II | G-22 | 16101849 | Koyo | Nanjing
Cedar Creek II | G-23 | 16101850 | Koyo | Nanjing
Cedar Creek II | G-24 | 16101851 | Koyo | Nanjing
Cedar Creek II | G-25 | 16101852 | Koyo | Nanjing
Cedar Creek II | G-26 | 16101853 | NTN | Nanjing
Cedar Creek II | G-27 | 16101854 | Koyo | Nanjing
Cedar Creek II | G-28 | 16101855 | Koyo | Nanjing
Cedar Creek II | G-29 | 16101856 | Koyo | Nanjing
Cedar Creek II | G-30 | 16101857 | Koyo | Nanjing
Cedar Creek II | G-31 | 16101858 | Koyo | Nanjing
Cedar Creek II | G-32 | 16101859 | Koyo | Nanjing
Cedar Creek II | G-33 | 16101860 | Koyo | Nanjing
Cedar Creek II | G-34 | 16101861 | Koyo | Nanjing
Cedar Creek II | G-35 | 16101862 | NTN | Nanjing
Cedar Creek II | G-36 | 16101863 | Koyo | Nanjing
Cedar Creek II | G-37 | 16101864 | Koyo | Nanjing
Cedar Creek II | G-38 | 16101865 | NTN | Nanjing
Cedar Creek II | G-39 | 16101866 | NTN | Nanjing
Cedar Creek II | G-40 | 16101867 | NTN | Nanjing
Cedar Creek II | G-41 | 16101868 | Koyo | Nanjing
Cedar Creek II | G-42 | 16101869 | Koyo | Nanjing
Cedar Creek II | G-43 | 16101870 | NTN | Nanjing
Cedar Creek II | G-44 | 16101871 | NTN | Nanjing
Cedar Creek II | G-45 | 16101872 | Koyo | Nanjing
Cedar Creek II | G-46 | 16101873 | NTN | Nanjing
Cedar Creek II | G-47 | 16101874 | Koyo | Nanjing
Cedar Creek II | G-48 | 16101875 | Koyo | Nanjing
Cedar Creek II | G-49 | 16101876 | Koyo | Nanjing
Cedar Creek II | G-50 | 16101877 | NTN | Nanjing
Cedar Creek II | G-51 | 16101878 | Koyo | Nanjing
Cedar Creek II | G-52 | 16101879 | Koyo | Nanjing
Cedar Creek II | G-53 | 16101880 | Koyo | Nanjing
Cedar Creek II | G-54 | 16101881 | Koyo | Nanjing
Cedar Creek II | G-55 | 16101882 | Koyo | Nanjing
Cedar Creek II | G-56 | 16101883 | Koyo | Nanjing
Cedar Creek II | G-57 | 16101884 | Koyo | Nanjing
Cedar Creek II | G-58 | 16101885 | NTN | Nanjing
Cedar Creek II | G-59 | 16101886 | Koyo | Nanjing
Cedar Creek II | G-60 | 16101887 | Koyo | Nanjing
Cedar Creek II | G-61 | 16101888 | NTN | Nanjing
Cedar Creek II | G-62 | 16101889 | NTN | Nanjing
Cedar Creek II | G-63 | 16101890 | NTN | Nanjing
Gratiot | 57 | 16105744 | NTN | Nanjing
Gratiot | 58 | 16105745 | NTN | Nanjing
Gratiot | 59 | 16105746 | Timken | Nanjing
Gratiot | 60 | 16105747 | NTN | Nanjing
Gratiot | 61 | 16105748 | NTN | Nanjing
Gratiot | 62 | 16105749 | NTN | Winergy
Gratiot | 63 | 16105750 | NTN | Nanjing
Gratiot | 64 | 16105751 | Timken | Nanjing
Gratiot | 65 | 16105752 | NTN | GETS
Gratiot | 66 | 16105753 | Timken | Nanjing
Gratiot | 67 | 16105754 | Koyo | Winergy
Gratiot | 68 | 16105755 | Koyo | Winergy
Gratiot | 69 | 16105756 | Koyo | Winergy
Gratiot | 70 | 16105757 | Koyo | Winergy
Gratiot | 71 | 16105758 | Pending Repair Report | Nanjing
Gratiot | 72 | 16105759 | Timken | Nanjing
Gratiot | 73 | 16105760 | Koyo | Nanjing
Gratiot | 74 | 16105761 | NTN | Nanjing
Gratiot | 75 | 16105762 | Timken | Nanjing
Gratiot | 76 | 16105763 | NTN | Nanjing
Gratiot | 77 | 16105764 | NTN | Nanjing
Gratiot | 78 | 16105765 | NTN | Nanjing
Gratiot | 79 | 16105766 |  | Nanjing
Gratiot | 80 | 16105767 | NTN | Nanjing
Gratiot | 81 | 16105768 | NTN | Nanjing
Gratiot | 82 | 16105769 | NTN | Nanjing
Gratiot | 83 | 16105770 | NTN | Nanjing
Gratiot | 84 | 16105771 | Koyo | Nanjing
Gratiot | 85 | 16105772 | NTN | Nanjing
Gratiot | 86 | 16105773 | NTN | Nanjing
Gratiot | 87 | 16105774 | NTN | Nanjing
Gratiot | 88 | 16105775 | Timken | Nanjing
Gratiot | 89 | 16105776 | NTN | Nanjing
Gratiot | 90 | 16105777 | Koyo | Nanjing
Gratiot | 91 | 16105778 | NTN | Nanjing
Gratiot | 92 | 16105779 | NTN | GETS
Gratiot | 93 | 16105780 | Koyo | Nanjing
Gratiot | 94 | 16105781 | Koyo | GETS
Gratiot | 95 | 16105782 | Timken | Nanjing
Gratiot | 96 | 16105783 | Timken | Nanjing
Gratiot | 97 | 16105784 | NTN | Nanjing
Gratiot | 98 | 16105785 | NTN | Nanjing
Gratiot | 99 | 16105786 | NTN | Nanjing
Gratiot | 100 | 16105787 | NTN | Nanjing
Gratiot | 101 | 16105788 | NTN | Nanjing
Gratiot | 102 | 16105789 | NTN | Nanjing
Gratiot | 103 | 16105790 | NTN | Nanjing
Gratiot | 104 | 16105791 | Koyo | GETS
Gratiot | 105 | 16105792 | NTN | Nanjing
Gratiot | 106 | 16105793 | Timken | Nanjing
Gratiot | 107 | 16105794 | NTN | GETS
Gratiot | 108 | 16105795 | NTN | GETS
Gratiot | 109 | 16105796 | Koyo | GETS
Gratiot | 110 | 16105797 | Koyo | GETS
Gratiot | 111 | 16105798 | NTN | Nanjing
Gratiot | 112 | 16105799 | NTN | GETS
Gratiot | 116 | 16105800 | Koyo | GETS
Gratiot | 117 | 16105801 | Koyo | GETS
Gratiot | 118 | 16105802 | NTN | GETS
Gratiot | 120 | 16105803 | Timken | GETS
Gratiot | 122 | 16105804 | NTN | GETS
Gratiot | 126 | 16105805 | Timken | Nanjing
Gratiot | 127 | 16105806 | NTN | Nanjing
Gratiot | 128 | 16105807 | NTN | Nanjing
Gratiot | 129 | 16105808 | NTN | Nanjing
Gratiot | 130 | 16105809 | NTN | Nanjing
Gratiot | 131 | 16105810 | NTN | Nanjing
Gratiot | 132 | 16105811 | NTN | Nanjing
Gratiot | 133 | 16105812 | Koyo | Nanjing
Bishop Hill | 10 | 16113134 | Koyo | Winergy
Bishop Hill | 11 | 16113135 | NTN | Nanjing
Bishop Hill | 12 | 16113136 | NTN | Nanjing
Bishop Hill | 13 | 16113137 | NTN | Winergy
Bishop Hill | 14 | 16113138 | NTN | Winergy
Bishop Hill | 15 | 16113139 | NTN | Winergy
Bishop Hill | 16 | 16113140 | NTN | Rexroth
Bishop Hill | 17 | 16113141 | NTN | Nanjing
Bishop Hill | 18 | 16113142 | Koyo | Winergy
Bishop Hill | 19 | 16113143 | NTN | Nanjing
Bishop Hill | 20 | 16113144 | NTN | Nanjing
Bishop Hill | 21 | 16113145 | NTN | Nanjing
Bishop Hill | 22 | 16113146 | Koyo | Nanjing
Bishop Hill | 23 | 16113147 | Koyo | Winergy
Bishop Hill | 24 | 16113148 | Koyo | Nanjing
Bishop Hill | 25 | 16113149 | NTN | Nanjing
Bishop Hill | 26 | 16113150 | Koyo | Winergy
Bishop Hill | 27 | 16113151 | Koyo | Winergy
Bishop Hill | 28 | 16113152 | Koyo | Winergy
Bishop Hill | 29 | 16113153 | Koyo | Winergy
Bishop Hill | 30 | 16113154 | Koyo | Nanjing
Bishop Hill | 31 | 16113155 | NTN | Nanjing
Bishop Hill | 32 | 16113156 | NTN | Nanjing
Bishop Hill | 33 | 16113157 | Koyo | Nanjing
Bishop Hill | 34 | 16113158 | Koyo | Nanjing
Bishop Hill | 35 | 16113159 | Koyo | Nanjing
Bishop Hill | 36 | 16113160 | Koyo | Nanjing
Bishop Hill | 37 | 16113161 | NTN | Nanjing
Bishop Hill | 38 | 16113162 | NTN | Nanjing
Bishop Hill | 39 | 16113163 | Koyo | Nanjing
Bishop Hill | 57 | 16113164 | NTN | Winergy
Bishop Hill | 58 | 16113165 | NTN | Nanjing
Bishop Hill | 62 | 16113166 | NTN | Winergy
Bishop Hill | 63 | 16113167 | NTN | Nanjing
Bishop Hill | 64 | 16113168 | Koyo | Nanjing
Bishop Hill | 65 | 16113169 | NTN | Nanjing
Bishop Hill | 66 | 16113170 | Koyo | Nanjing
Bishop Hill | 67 | 16113171 | Koyo | Nanjing
Bishop Hill | 68 | 16113172 | NTN | Nanjing
Bishop Hill | 69 | 16113173 | NTN | Winergy
Bishop Hill | 70 | 16113174 | Koyo | Winergy
Bishop Hill | 71 | 16113175 |  | Nanjing
Bishop Hill | 72 | 16113176 | NTN | Winergy
Bishop Hill | 80 | 16113177 | Koyo | Winergy
Bishop Hill | 81 | 16113178 | Koyo | Winergy
Bishop Hill | 82 | 16113179 | NTN | Nanjing
Bishop Hill | 83 | 16113180 | NTN | Rexroth
Bishop Hill | 84 | 16113181 | NTN | Nanjing
Bishop Hill | 85 | 16113182 | Koyo | Winergy
Bishop Hill | 86 | 16113183 | NTN | Nanjing
Bishop Hill | 1 | 16113242 | NTN | Nanjing
Bishop Hill | 2 | 16113243 | NTN | Nanjing
Bishop Hill | 3 | 16113244 | NTN | Nanjing
Bishop Hill | 4 | 16113245 | Koyo | Nanjing
Bishop Hill | 5 | 16113246 | Koyo | Nanjing
Bishop Hill | 6 | 16113247 | Koyo | Nanjing
Bishop Hill | 7 | 16113248 | Koyo | Nanjing
Bishop Hill | 8 | 16113249 | Koyo | Nanjing
Bishop Hill | 9 | 16113250 | Koyo | Nanjing
Bishop Hill | 40 | 16113251 | Koyo | Nanjing
Bishop Hill | 41 | 16113252 | NTN | Nanjing
Bishop Hill | 42 | 16113253 | Koyo | Nanjing
Bishop Hill | 43 | 16113254 | Koyo | Nanjing
Bishop Hill | 44 | 16113255 | Koyo | Nanjing
Bishop Hill | 45 | 16113256 | Koyo | Nanjing
Bishop Hill | 46 | 16113257 | Koyo | Nanjing
Bishop Hill | 47 | 16113258 | Koyo | Nanjing
Bishop Hill | 87 | 16113259 | Koyo | Nanjing
Bishop Hill | 88 | 16113260 | Koyo | Nanjing
Bishop Hill | 89 | 16113261 | Koyo | Nanjing
Bishop Hill | 90 | 16113262 | Koyo | Nanjing
Bishop Hill | 91 | 16113263 | Koyo | Nanjing
Bishop Hill | 94 | 16113264 | Koyo | Nanjing
Bishop Hill | 95 | 16113265 | Koyo | Nanjing
Bishop Hill | 96 | 16113266 | Koyo | Nanjing
Bishop Hill | 97 | 16113267 | Koyo | Nanjing
Bishop Hill | 98 | 16113268 | Koyo | Nanjing
Bishop Hill | 99 | 16113269 | Koyo | Nanjing
Bishop Hill | 100 | 16113270 | NTN | Nanjing
Bishop Hill | 101 | 16113271 | Koyo | Nanjing
Bishop Hill | 102 | 16113272 | NTN | Nanjing
Bishop Hill | 103 | 16113273 | Koyo | Nanjing
Bishop Hill | 104 | 16113274 | Koyo | Nanjing
Bishop Hill | 105 | 16113275 | Koyo | Nanjing
Bishop Hill | 106 | 16113276 | Koyo | Nanjing
Bishop Hill | 107 | 16113277 | Koyo | Nanjing
Bishop Hill | 108 | 16113278 | Koyo | Nanjing
Bishop Hill | 109 | 16113279 | NTN | Nanjing
Bishop Hill | 110 | 16113280 | NTN | Nanjing
Bishop Hill | 113 | 16113281 | Koyo | Nanjing
Bishop Hill | 114 | 16113282 | Koyo | Nanjing
Bishop Hill | 115 | 16113283 | Koyo | Nanjing
Bishop Hill | 116 | 16113284 | Koyo | Nanjing
Bishop Hill | 117 | 16113285 | Koyo | Nanjing
Bishop Hill | 118 | 16113286 | Koyo | Nanjing
Bishop Hill | 122 | 16113287 | NTN | Nanjing
Bishop Hill | 128 | 16113288 | Koyo | Nanjing
Bishop Hill | 129 | 16113289 | Koyo | Nanjing
Bishop Hill | 130 | 16113290 | Koyo | Nanjing
California Ridge | 1 | 16116456 | Koyo | Rexroth
California Ridge | 2 | 16116457 | Koyo | Rexroth
California Ridge | 3 | 16116458 | NTN | Nanjing
California Ridge | 4 | 16116459 | NTN | Nanjing
California Ridge | 5 | 16116460 | NTN | Nanjing
California Ridge | 6 | 16116461 | NTN | Rexroth
California Ridge | 7 | 16116462 | Koyo | Nanjing
California Ridge | 8 | 16116463 | NTN | Nanjing
California Ridge | 9 | 16116464 | NTN | Nanjing
California Ridge | 10 | 16116465 | Koyo | Nanjing
California Ridge | 11 | 16116466 | NTN | Nanjing
California Ridge | 12 | 16116467 | Koyo | Nanjing
California Ridge | 13 | 16116468 | NTN | Nanjing
California Ridge | 14 | 16116469 | NTN | Nanjing
California Ridge | 15 | 16116470 | NTN | Nanjing
California Ridge | 16 | 16116471 | NTN | Nanjing
California Ridge | 17 | 16116472 | NTN | Nanjing
California Ridge | 18 | 16116473 | NTN | Nanjing
California Ridge | 19 | 16116474 | NTN | Nanjing
California Ridge | 20 | 16116475 | Koyo | Nanjing
California Ridge | 21 | 16116476 | Koyo | Nanjing
California Ridge | 22 | 16116477 | NTN | Rexroth
California Ridge | 23 | 16116478 | Koyo | Nanjing
California Ridge | 24 | 16116479 | Koyo | Nanjing
California Ridge | 25 | 16116480 | Koyo | Nanjing
California Ridge | 26 | 16116481 | Koyo | Nanjing
California Ridge | 27 | 16116482 | NTN | Nanjing
California Ridge | 28 | 16116483 | NTN | Nanjing
California Ridge | 29 | 16116484 | NTN | Nanjing
California Ridge | 30 | 16116485 | NTN | Nanjing
California Ridge | 31 | 16116486 | Koyo | Rexroth
California Ridge | 32 | 16116487 | Koyo | Nanjing
California Ridge | 33 | 16116488 | Koyo | Nanjing
California Ridge | 34 | 16116489 | Koyo | Rexroth
California Ridge | 35 | 16116490 | Koyo | Nanjing
California Ridge | 36 | 16116491 | NTN | Nanjing
California Ridge | 37 | 16116492 | NTN | Nanjing
California Ridge | 38 | 16116493 | NTN | Nanjing
California Ridge | 39 | 16116494 | NTN | Nanjing
California Ridge | 40 | 16116495 | NTN | Nanjing
California Ridge | 41 | 16116496 | NTN | Nanjing
California Ridge | 42 | 16116497 | NTN | Nanjing
California Ridge | 43 | 16116498 | Koyo | Nanjing
California Ridge | 44 | 16116499 | NTN | Nanjing
California Ridge | 45 | 16116500 | Koyo | Nanjing
California Ridge | 46 | 16116501 | NTN | Rexroth
California Ridge | 47 | 16116502 | Koyo | Nanjing
California Ridge | 48 | 16116503 | Koyo | Nanjing
California Ridge | 49 | 16116504 | NTN | Nanjing
California Ridge | 50 | 16116505 | NTN | Nanjing
California Ridge | 51 | 16116506 | Koyo | Nanjing
California Ridge | 52 | 16116507 | NTN | Nanjing
California Ridge | 53 | 16116508 | NTN | Nanjing
California Ridge | 54 | 16116509 | Koyo | Nanjing
California Ridge | 55 | 16116510 | Koyo | Nanjing
California Ridge | 56 | 16116511 | Koyo | Nanjing
California Ridge | 57 | 16116512 | NTN | Nanjing
California Ridge | 58 | 16116513 | NTN | Nanjing
California Ridge | 59 | 16116514 | Koyo | Nanjing
California Ridge | 60 | 16116515 | Koyo | Nanjing
California Ridge | 61 | 16116516 | Koyo | Nanjing
California Ridge | 62 | 16116517 | Koyo | Rexroth
California Ridge | 63 | 16116518 | Koyo | Nanjing
California Ridge | 64 | 16116519 | Koyo | Nanjing
California Ridge | 65 | 16116520 | NTN | Nanjing
California Ridge | 66 | 16116521 | NTN | Nanjing
California Ridge | 67 | 16116522 | Koyo | Nanjing
California Ridge | 68 | 16116523 | Koyo | Nanjing
California Ridge | 69 | 16116524 | Koyo | Nanjing
California Ridge | 70 | 16116525 | NTN | Nanjing
California Ridge | 71 | 16116526 | NTN | Nanjing
California Ridge | 72 | 16116527 | Koyo | Nanjing
California Ridge | 73 | 16116528 | NTN | Nanjing
California Ridge | 74 | 16116529 | Koyo | Nanjing
California Ridge | 75 | 16116530 | Koyo | Nanjing
California Ridge | 76 | 16116531 | Koyo | Nanjing
California Ridge | 77 | 16116532 | Koyo | Nanjing
California Ridge | 78 | 16116533 | Koyo | Nanjing
California Ridge | 79 | 16116534 | NTN | Nanjing
California Ridge | 80 | 16116535 | NTN | Nanjing
California Ridge | 81 | 16116536 | Koyo | Nanjing
California Ridge | 82 | 16116537 | Koyo | Nanjing
California Ridge | 83 | 16116538 | NTN | Nanjing
California Ridge | 84 | 16116539 | Koyo | Nanjing
California Ridge | 85 | 16116540 | NTN | Nanjing
California Ridge | 86 | 16116541 | NTN | Nanjing
California Ridge | 87 | 16116542 | NTN | Nanjing
California Ridge | 88 | 16116543 | NTN | Nanjing
California Ridge | 89 | 16116544 | Koyo | Nanjing
California Ridge | 90 | 16116545 | NTN | Nanjing
California Ridge | 91 | 16116546 | Koyo | Nanjing
California Ridge | 92 | 16116547 | Koyo | Nanjing
California Ridge | 93 | 16116548 | Koyo | Nanjing
California Ridge | 94 | 16116549 | NTN | Nanjing
California Ridge | 95 | 16116550 | Koyo | Nanjing
California Ridge | 96 | 16116551 | Koyo | Nanjing
California Ridge | 97 | 16116552 | NTN | Nanjing
California Ridge | 98 | 16116553 | NTN | Nanjing
California Ridge | 99 | 16116554 | NTN | Nanjing
California Ridge | 100 | 16116555 | Koyo | Nanjing
California Ridge | 101 | 16116556 | Koyo | Nanjing
California Ridge | 102 | 16116557 | Koyo | Nanjing
California Ridge | 103 | 16116558 | NTN | Rexroth
California Ridge | 104 | 16116559 | Koyo | Nanjing
California Ridge | 105 | 16116560 | Koyo | Nanjing
California Ridge | 106 | 16116561 | NTN | Nanjing
California Ridge | 107 | 16116562 | NTN | Nanjing
California Ridge | 108 | 16116563 | NTN | Nanjing
California Ridge | 109 | 16116564 | Koyo | Nanjing
California Ridge | 110 | 16116565 | NTN | Nanjing
California Ridge | 111 | 16116566 | Koyo | Nanjing
California Ridge | 112 | 16116567 | Koyo | Nanjing
California Ridge | 113 | 16116568 | Koyo | Nanjing
California Ridge | 114 | 16116569 | Koyo | Nanjing
California Ridge | 115 | 16116570 | Koyo | Nanjing
California Ridge | 116 | 16116571 | NTN | Nanjing
California Ridge | 117 | 16116572 | Koyo | Nanjing
California Ridge | 118 | 16116573 | Koyo | Nanjing
California Ridge | 119 | 16116574 | Koyo | Nanjing
California Ridge | 120 | 16116575 | Koyo | Nanjing
California Ridge | 121 | 16116576 | Koyo | Nanjing
California Ridge | 122 | 16116577 | Koyo | Nanjing
California Ridge | 123 | 16116578 | Koyo | Nanjing
California Ridge | 124 | 16116579 | Koyo | Nanjing
California Ridge | 125 | 16116580 | NTN | Nanjing
California Ridge | 126 | 16116581 | Koyo | Nanjing
California Ridge | 127 | 16116582 | Koyo | Nanjing
California Ridge | 128 | 16116583 | Koyo | Nanjing
California Ridge | 129 | 16116584 | NTN | Nanjing
California Ridge | 130 | 16116585 | Koyo | Nanjing
California Ridge | 131 | 16116586 | NTN | Nanjing
California Ridge | 132 | 16116587 | Koyo | Nanjing
California Ridge | 133 | 16116588 | NTN | Nanjing
California Ridge | 134 | 16116589 | Koyo | Nanjing
Orangeville | 1 | 16131371 | Koyo | Nanjing
Orangeville | 2 | 16131372 | Koyo | Nanjing
Orangeville | 3 | 16131373 | Koyo | Nanjing
Orangeville | 4 | 16131374 | NTN | Nanjing
Orangeville | 5 | 16131375 | Koyo | Nanjing
Orangeville | 6 | 16131376 | Koyo | Nanjing
Orangeville | 7 | 16131377 | Koyo
Orangeville | 8 | 16131378 | Koyo | Winergy
Orangeville | 9 | 16131379 | NTN | Winergy
Orangeville | 10 | 16131380 | Koyo | Nanjing
Orangeville | 11 | 16131381 | Koyo | Nanjing
Orangeville | 12 | 16131382 | Koyo | ZF
Orangeville | 13 | 16131383 | Koyo
Orangeville | 14 | 16131384 | Koyo | Nanjing
Orangeville | 15 | 16131385 | Koyo | Nanjing
Orangeville | 16 | 16131386 | NTN | Nanjing
Orangeville | 17 | 16131387 | Koyo | Winergy
Orangeville | 18 | 16131388 | Koyo | Nanjing
Orangeville | 19 | 16131389 | NTN | Replacement Pending
Orangeville | 20 | 16131390 | NTN | Winergy
Orangeville | 21 | 16131391 | Koyo | Nanjing
Orangeville | 22 | 16131392 | Koyo | Nanjing
Orangeville | 23 | 16131393 | Koyo | Nanjing
Orangeville | 24 | 16131394 | NTN | Winergy
Orangeville | 25 | 16131395 | Koyo | Nanjing
Orangeville | 26 | 16131396 | Koyo | Nanjing
Orangeville | 27 | 16131397 | NTN | Winergy
Orangeville | 29 | 16131398 | NTN | Nanjing
Orangeville | 30 | 16131399 | Koyo | Nanjing
Orangeville | 31 | 16131400 | Koyo
Orangeville | 32 | 16131401 | NTN | Nanjing
Orangeville | 33 | 16131402 | NTN | Winergy
Orangeville | 34 | 16131403 | Koyo | ZF
Orangeville | 35 | 16131404 | Koyo | Winergy
Orangeville | 36 | 16131405 | Koyo | Nanjing
Orangeville | 37 | 16131406 | Koyo | Replacement Pending
Orangeville | 38 | 16131407 | Koyo | Nanjing
Orangeville | 39 | 16131408 | Koyo | Winergy
Orangeville | 40 | 16131409 | Koyo | Nanjing
Orangeville | 41 | 16131410 | Koyo | Nanjing
Orangeville | 42 | 16131411 | Koyo | Winergy
Orangeville | 43 | 16131412 | Koyo | Winergy
Orangeville | 44 | 16131413 | NTN | Pending Repair Report
Orangeville | 45 | 16131414 | Koyo | Nanjing
Orangeville | 46 | 16131415
Orangeville | 47 | 16131416 | Koyo | Rexroth
Orangeville | 48 | 16131417 | Koyo | Winergy
Orangeville | 49 | 16131418 | Koyo | Replacement Pending
Orangeville | 50 | 16131419 | NTN | ZF
Orangeville | 51 | 16131420 | Koyo | Nanjing
Orangeville | 52 | 16131421 |  | Nanjing
Orangeville | 53 | 16131422 | Koyo | Nanjing
Orangeville | 54 | 16131423 |  | Nanjing
Orangeville | 55 | 16131424 | Koyo | Nanjing
Orangeville | 56 | 16131425 | Koyo | Nanjing
Orangeville | 57 | 16131426 | Koyo | Nanjing
Orangeville | 58 | 16131427 | NTN
Orangeville | 59 | 16131428 | Koyo | Winergy
Prairie Breeze | 1 | 17130896 | NTN | Nanjing
Prairie Breeze | 2 | 17130897 | NTN | Rexroth
Prairie Breeze | 3 | 17130898 | NTN | Winergy
Prairie Breeze | 4 | 17130899 | Koyo | Winergy
Prairie Breeze | 5 | 17130900 | NTN | Rexroth
Prairie Breeze | 6 | 17130901 | Koyo | Rexroth
Prairie Breeze | 7 | 17130902 | NTN | Nanjing
Prairie Breeze | 8 | 17130903 | Koyo | Nanjing
Prairie Breeze | 9 | 17130904 | NTN | Winergy
Prairie Breeze | 10 | 17130905 | Koyo | Nanjing
Prairie Breeze | 11 | 17130906 | NTN | Winergy
Prairie Breeze | 12 | 17130907 | NTN | Rexroth
Prairie Breeze | 13 | 17130908 | NTN | ZF
Prairie Breeze | 14 | 17130909 | Koyo | Rexroth
Prairie Breeze | 15 | 17130910 | Koyo | Nanjing
Prairie Breeze | 16 | 17130911 | NTN | Nanjing
Prairie Breeze | 17 | 17130912 | Koyo | Nanjing
Prairie Breeze | 18 | 17130913 | NTN | Nanjing
Prairie Breeze | 19 | 17130914 | NTN | Nanjing
Prairie Breeze | 20 | 17130915 | NTN | Nanjing
Prairie Breeze | 21 | 17130916 | Koyo | Nanjing
Prairie Breeze | 22 | 17130917 | NTN | Winergy
Prairie Breeze | 23 | 17130918 | Koyo | Winergy
Prairie Breeze | 24 | 17130919 | Koyo | Winergy
Prairie Breeze | 25 | 17130920 | NTN | Winergy
Prairie Breeze | 26 | 17130921 | Koyo | Winergy
Prairie Breeze | 27 | 17130922 | Koyo | Nanjing
Prairie Breeze | 28 | 17130923 | Koyo | Nanjing
Prairie Breeze | 29 | 17130924 | Koyo | Nanjing
Prairie Breeze | 30 | 17130925 | NTN | Winergy
Prairie Breeze | 31 | 17130926 | Koyo | Winergy
Prairie Breeze | 32 | 17130927 | Koyo | Nanjing
Prairie Breeze | 33 | 17130928 | NTN | Winergy
Prairie Breeze | 34 | 17130929 | NTN | Nanjing
Prairie Breeze | 35 | 17130930 | NTN | Winergy
Prairie Breeze | 36 | 17130931 | NTN | Nanjing
Prairie Breeze | 37 | 17130932 | NTN | Winergy
Prairie Breeze | 38 | 17130933 | NTN | Nanjing
Prairie Breeze | 39 | 17130934 | Koyo | Nanjing
Prairie Breeze | 40 | 17130935 | Koyo | Winergy
Prairie Breeze | 41 | 17130936 | Koyo | Nanjing
Prairie Breeze | 42 | 17130937 | Koyo | Nanjing
Prairie Breeze | 43 | 17130938 | Timken | Winergy
Prairie Breeze | 44 | 17130939 | Koyo | Nanjing
Prairie Breeze | 45 | 17130940 | Koyo | Winergy
Prairie Breeze | 46 | 17130941 | Koyo | Winergy
Prairie Breeze | 47 | 17130942 | Koyo | Nanjing
Prairie Breeze | 48 | 17130943 | NTN | Nanjing
Prairie Breeze | 49 | 17130944 | NTN | Winergy
Prairie Breeze | 50 | 17130945 | Koyo | Nanjing
Prairie Breeze | 51 | 17130946 | NTN | Winergy
Prairie Breeze | 52 | 17130947 | NTN | Winergy
Prairie Breeze | 53 | 17130948 | NTN | Winergy
Prairie Breeze | 54 | 17130949 | Koyo | Winergy
Prairie Breeze | 55 | 17130950 | Koyo | Nanjing
Prairie Breeze | 56 | 17130951 | NTN | Nanjing
Prairie Breeze | 57 | 17130952 | NTN | Nanjing
Prairie Breeze | 58 | 17130953 | NTN | Nanjing
Prairie Breeze | 59 | 17130954 | Koyo | Nanjing
Prairie Breeze | 60 | 17130955 | NTN | Nanjing
Prairie Breeze | 61 | 17130956 | Koyo | Nanjing
Prairie Breeze | 62 | 17130957 | Koyo | Nanjing
Prairie Breeze | 63 | 17130958 | Koyo | Nanjing
Prairie Breeze | 64 | 17130959 | Koyo | Winergy
Prairie Breeze | 65 | 17130960 | Koyo | Winergy
Prairie Breeze | 66 | 17130961 | Koyo | Winergy
Prairie Breeze | 67 | 17130962 | Koyo | Nanjing
Prairie Breeze | 68 | 17130963 | Koyo | Winergy
Prairie Breeze | 69 | 17130964 | Koyo | Winergy
Prairie Breeze | 70 | 17130965 | Koyo | Nanjing
Prairie Breeze | 71 | 17130966 | Koyo | Nanjing
Prairie Breeze | 72 | 17130967 | NTN | Nanjing
Prairie Breeze | 73 | 17130968 | NTN | Nanjing
Prairie Breeze | 74 | 17130969 | NTN | Nanjing
Prairie Breeze | 75 | 17130970 | NTN | Nanjing
Prairie Breeze | 76 | 17130971 | Koyo | Nanjing
Prairie Breeze | 77 | 17130972 | Koyo | Nanjing
Prairie Breeze | 78 | 17130973 | Koyo | Nanjing
Prairie Breeze | 79 | 17130974 | Koyo | Nanjing
Prairie Breeze | 80 | 17130975 | Koyo | Winergy
Prairie Breeze | 81 | 17130976 | NTN | Nanjing
Prairie Breeze | 82 | 17130977 | NTN | Nanjing
Prairie Breeze | 83 | 17130978 | NTN | Nanjing
Prairie Breeze | 84 | 17130979 | Koyo | Nanjing
Prairie Breeze | 85 | 17130980 | NTN | Winergy
Prairie Breeze | 86 | 17130981 | NTN | Winergy
Prairie Breeze | 87 | 17130982 | Koyo | Nanjing
Prairie Breeze | 88 | 17130983 | NTN | ZF
Prairie Breeze | 89 | 17130984 | NTN | Rexroth
Prairie Breeze | 90 | 17130985 | NTN | Nanjing
Prairie Breeze | 91 | 17130986 | NTN | Nanjing
Prairie Breeze | 92 | 17130987 | Koyo | Rexroth
Prairie Breeze | 93 | 17130988 | NTN | Nanjing
Prairie Breeze | 94 | 17130989 | NTN | Winergy
Prairie Breeze | 95 | 17130990 | NTN | Rexroth
Prairie Breeze | 96 | 17130991 | Koyo | Rexroth
Prairie Breeze | 97 | 17130992 | Koyo | Winergy
Prairie Breeze | 98 | 17130993 | NTN | Rexroth
Prairie Breeze | 99 | 17130994 | NTN | Nanjing
Prairie Breeze | 100 | 17130995 | NTN | Nanjing
Prairie Breeze | 101 | 17130996 | NTN | Nanjing
Prairie Breeze | 102 | 17130997 | NTN | Nanjing
Prairie Breeze | 103 | 17130998 | Koyo | Rexroth
Prairie Breeze | 104 | 17130999 | NTN | Nanjing
Prairie Breeze | 105 | 17131000 | NTN | Winergy
Prairie Breeze | 106 | 17131001 | NTN | Nanjing
Prairie Breeze | 107 | 17131002 | NTN | Nanjing
Prairie Breeze | 108 | 17131003 | NTN | Rexroth
Prairie Breeze | 109 | 17131004 | Koyo | Winergy
Prairie Breeze | 110 | 17131005 | Koyo | Winergy
Prairie Breeze | 111 | 17131006 | NTN | Winergy
Prairie Breeze | 112 | 17131007 | NTN | Nanjing
Prairie Breeze | 113 | 17131008 | NTN | Winergy
Prairie Breeze | 114 | 17131009 | Koyo | Winergy
Prairie Breeze | 115 | 17131010 | NTN | Winergy
Prairie Breeze | 116 | 17131011 | NTN | Winergy
Prairie Breeze | 117 | 17131012 | NTN | Winergy
Prairie Breeze | 118 | 17131013 | NTN | Nanjing
Goldthwaite | 3W | 17131431 | Koyo | Pending Repair Report
Goldthwaite | 39E | 17131432 | NTN | Nanjing
Goldthwaite | 3 | 17131433 | Koyo
Goldthwaite | 4 | 17131434 | NTN | Nanjing
Goldthwaite | 5 | 17131435 | Koyo | Nanjing
Goldthwaite | 43E | 17131436 | NTN | Nanjing
Goldthwaite | 43W | 17131437 | NTN | Nanjing
Goldthwaite | 8 | 17131438 |  | Nanjing
Goldthwaite | 9 | 17131439 | Replacement Pending | Replacement Pending
Goldthwaite | 10 | 17131440 | NTN | Nanjing
Goldthwaite | 11 | 17131441 | NTN | Nanjing
Goldthwaite | 12 | 17131442 | Koyo | Rexroth
Goldthwaite | 13 | 17131443 | NTN | Nanjing
Goldthwaite | 14 | 17131444 | Koyo | Nanjing
Goldthwaite | 15 | 17131445 | NTN | Nanjing
Goldthwaite | 16 | 17131446 | Koyo
Goldthwaite | 17 | 17131447 | NTN | Nanjing
Goldthwaite | 18 | 17131448 | NTN | Nanjing
Goldthwaite | 19 | 17131449 | NTN | Replacement Pending
Goldthwaite | 20 | 17131450 |  | Nanjing
Goldthwaite | 21 | 17131451 |  | Nanjing
Goldthwaite | 22 | 17131452 | NTN | Nanjing
Goldthwaite | 23 | 17131453 | NTN
Goldthwaite | 24 | 17131454 | NTN | Nanjing
Goldthwaite | 25 | 17131455 | Koyo | Nanjing
Goldthwaite | 26 | 17131456 | NTN | Nanjing
Goldthwaite | 27 | 17131457 | NTN | Nanjing
Goldthwaite | 28 | 17131458 | NTN | Nanjing
Goldthwaite | 29 | 17131459 | Koyo | Nanjing
Goldthwaite | 30 | 17131460 |  | Nanjing
Goldthwaite | 31 | 17131461 | Koyo | Winergy
Goldthwaite | 32 | 17131462
Goldthwaite | 33 | 17131463 | NTN
Goldthwaite | 34 | 17131464 | NTN | Nanjing
Goldthwaite | 35 | 17131465 |  | Nanjing
Goldthwaite | 36 | 17131466 | NTN | Nanjing
Goldthwaite | 37 | 17131467 | NTN | Nanjing
Goldthwaite | 38 | 17131468 | Replacement Pending | Rexroth
Goldthwaite | 39 | 17131469 |  | Nanjing
Goldthwaite | 43 | 17131470 | Koyo | Nanjing
Goldthwaite | 44 | 17131471
Goldthwaite | 45 | 17131472 | NTN | Nanjing
Goldthwaite | 46 | 17131473 | NTN | Winergy
Goldthwaite | 47 | 17131474 | NTN | Nanjing
Goldthwaite | 48 | 17131475 | NTN | Nanjing
Goldthwaite | 49 | 17131476 |  | Rexroth
Goldthwaite | 50 | 17131477 |  | Nanjing
Goldthwaite | 51 | 17131478 | NTN | Nanjing
Goldthwaite | 52 | 17131479 | NTN
Goldthwaite | 53 | 17131480 | Replacement Pending | Nanjing
Goldthwaite | 54 | 17131481 | Koyo
Goldthwaite | 55 | 17131482 | Koyo | Rexroth
Goldthwaite | 56 | 17131483 | NTN | Nanjing
Goldthwaite | 57 | 17131484 |  | Rexroth
Goldthwaite | 58 | 17131485 | NTN | Nanjing
Goldthwaite | 59 | 17131486 | NTN | Nanjing
Goldthwaite | 60 | 17131487 | NTN | Rexroth
Goldthwaite | 61 | 17131488
Goldthwaite | 62 | 17131489 | NTN | Nanjing
Goldthwaite | 63 | 17131490 | Koyo
Goldthwaite | 64 | 17131491 | NTN
Goldthwaite | 65 | 17131492 | Koyo | Nanjing
Goldthwaite | 66 | 17131493
Goldthwaite | 67 | 17131494 | NTN | Nanjing
Goldthwaite | 68 | 17131495 | NTN | Nanjing
Goldthwaite | 69 | 17131496 |  | Replacement Pending
Goldthwaite | 70 | 17131497 | NTN | Nanjing
Goldthwaite | 71 | 17131498 | NTN | Nanjing
Goldthwaite | 72 | 17131499 | Koyo | Nanjing
Goldthwaite | 73 | 17131500 | NTN | Winergy
Goldthwaite | 74 | 17131501 | NTN
Goldthwaite | 75 | 17131502 | NTN | Nanjing
Goldthwaite | 76 | 17131503 | NTN | Winergy
Goldthwaite | 77 | 17131504 | NTN | Replacement Pending
Goldthwaite | 78 | 17131505 | Koyo | Nanjing
Goldthwaite | 79 | 17131506 | Koyo | Winergy
Goldthwaite | 80 | 17131507 | Koyo | Nanjing
Goldthwaite | 81 | 17131508 | NTN | Nanjing
Goldthwaite | 82 | 17131509 | Koyo | Nanjing
Goldthwaite | 83 | 17131510 | NTN | Nanjing
Goldthwaite | 84 | 17131511 | NTN | Nanjing
Goldthwaite | 85 | 17131512 | Koyo | Nanjing
Goldthwaite | 86 | 17131513
Spring Canyon Expansion | 201 | 17134472 | NTN
Spring Canyon Expansion | 202 | 17134473 | Koyo
Rattlesnake | 1 | 17134474 | Koyo | Rexroth
Rattlesnake | 2 | 17134475 | Koyo | Rexroth
Rattlesnake | 3 | 17134476 | Koyo | Rexroth
Rattlesnake | 4 | 17134477 | Koyo | Rexroth
Rattlesnake | 5 | 17134478 | Koyo | Rexroth
Rattlesnake | 6 | 17134479 | Koyo | Rexroth
Rattlesnake | 7 | 17134480 | Koyo | Rexroth
Rattlesnake | 8 | 17134481 | Koyo | Winergy
Rattlesnake | 9 | 17134482 | Koyo | Winergy
Marsh Hill | 1 | 17140526 | NTN | Nanjing
Marsh Hill | 2 | 17140527 | NTN | Nanjing
Marsh Hill | 3 | 17140528 | NTN | Nanjing
Marsh Hill | 4 | 17140529 | NTN | Nanjing
Marsh Hill | 5 | 17140530 | NTN | Nanjing
Marsh Hill | 6 | 17140531 | NTN
Marsh Hill | 7 | 17140532 | Koyo | Nanjing
Marsh Hill | 8 | 17140533 | NTN | Nanjing
Marsh Hill | 9 | 17140534 | NTN | Nanjing
Marsh Hill | 10 | 17140535 | Koyo | Nanjing
Spring Canyon Expansion | 101 | 17140647 | Koyo | Rexroth
Spring Canyon Expansion | 102 | 17140648 | Koyo | Nanjing
Spring Canyon Expansion | 103 | 17140649 | Timken | Nanjing
Spring Canyon Expansion | 104 | 17140650 | Koyo | Rexroth
Spring Canyon Expansion | 105 | 17140651 | Koyo | Winergy
Spring Canyon Expansion | 106 | 17140652 | NTN
Spring Canyon Expansion | 107 | 17140653 | Koyo | Nanjing
Spring Canyon Expansion | 108 | 17140654 | Timken | Winergy
Spring Canyon Expansion | 109 | 17140655 | Koyo | Nanjing
Spring Canyon Expansion | 110 | 17140656 | Koyo | Nanjing
Spring Canyon Expansion | 111 | 17140657 | Koyo
Spring Canyon Expansion | 112 | 17140658 | Replacement Pending | Pending Repair Report
Spring Canyon Expansion | 113 | 17140659 | NTN | Nanjing
Spring Canyon Expansion | 114 | 17140660 | NTN | Winergy
Spring Canyon Expansion | 115 | 17140661 |  | Nanjing
Spring Canyon Expansion | 116 | 17140662 | Koyo | Replacement Pending
Spring Canyon Expansion | 117 | 17140663 | NTN | ZF
Spring Canyon Expansion | 118 | 17140664 | Koyo
Spring Canyon Expansion | 119 | 17140665 | Koyo | Nanjing
Spring Canyon Expansion | 203 | 17142485 | Timken | Replacement Pending
Spring Canyon Expansion | 204 | 17142486 | Koyo | Nanjing
Spring Canyon Expansion | 205 | 17142487 | Koyo | Winergy
Spring Canyon Expansion | 206 | 17142488 | Koyo | Rexroth
Spring Canyon Expansion | 207 | 17142489 | NTN | Nanjing
Spring Canyon Expansion | 208 | 17142490 | Replacement Pending | Winergy
Spring Canyon Expansion | 209 | 17142491 | Koyo | Nanjing
Spring Canyon Expansion | 210 | 17142492 | Koyo | Winergy
Spring Canyon Expansion | 211 | 17142493 | NTN | Nanjing
Spring Canyon Expansion | 212 | 17142494 | NTN | Rexroth
Spring Canyon Expansion | 213 | 17142495 | NTN | Nanjing
Spring Canyon Expansion | 214 | 17142496 | NTN | Nanjing
Spring Canyon Expansion | 215 | 17142497 | NTN | Nanjing
Spring Canyon Expansion | 216 | 17142498 | NTN | Pending Repair Report
Rattlesnake | 10 | 17142750 | Koyo | Winergy
Rattlesnake | 11 | 17142751 |  | Winergy
Rattlesnake | 12 | 17142752 | NTN | Nanjing
Rattlesnake | 13 | 17142753 | Koyo | Nanjing
Rattlesnake | 14 | 17142754 |  | Winergy
Rattlesnake | 15 | 17142755 | Koyo | Winergy
Rattlesnake | 16 | 17142756 | Koyo | Nanjing
Rattlesnake | 17 | 17142757 | NTN | Winergy
Rattlesnake | 18 | 17142758 | Koyo | Winergy
Rattlesnake | 19 | 17142759 | Koyo | Nanjing
Rattlesnake | 20 | 17142760 | Koyo | Winergy
Rattlesnake | 21 | 17142761 | Koyo | Nanjing
Rattlesnake | 22 | 17142762 | NTN | Nanjing
Rattlesnake | 23 | 17142763 | NTN | Nanjing
Rattlesnake | 24 | 17142764 | Koyo | Nanjing
Rattlesnake | 25 | 17142765 | Koyo | Winergy
Rattlesnake | 26 | 17142766 | Koyo | Winergy
Rattlesnake | 27 | 17142767 | Koyo | Rexroth
Rattlesnake | 28 | 17142768 | Koyo | ZF
Rattlesnake | 29 | 17142769 | Koyo | Winergy
Rattlesnake | 30 | 17142770 | Koyo | Winergy
Rattlesnake | 31 | 17142771 |  | Winergy
Rattlesnake | 32 | 17142772 | Koyo | Winergy
Rattlesnake | 33 | 17142773 | NTN | Winergy
Rattlesnake | 34 | 17142774 | Koyo | Winergy
Rattlesnake | 35 | 17142775 | Koyo | Nanjing
Rattlesnake | 36 | 17142776 | Koyo | Nanjing
Rattlesnake | 37 | 17142777 | Koyo | Nanjing
Rattlesnake | 38 | 17142778 | Koyo | Winergy
Rattlesnake | 39 | 17142779 | Koyo | ZF
Rattlesnake | 40 | 17142780 | Koyo | Winergy
Rattlesnake | 41 | 17142781 | Koyo | Winergy
Rattlesnake | 42 | 17142782 | Koyo | Nanjing
Rattlesnake | 43 | 17142783 | Koyo | Nanjing
Rattlesnake | 44 | 17142784 | Koyo | Winergy
Rattlesnake | 45 | 17142785 | Koyo | Nanjing
Rattlesnake | 46 | 17142786 | Koyo | Nanjing
Rattlesnake | 47 | 17142787 | Koyo | Nanjing
Rattlesnake | 48 | 17142788 | NTN | Nanjing
Rattlesnake | 49 | 17142789 | Koyo | Nanjing
Rattlesnake | 50 | 17142790 | NTN | Nanjing
Rattlesnake | 51 | 17142791 | Koyo | Winergy
Rattlesnake | 52 | 17142792 | Koyo | Nanjing
Rattlesnake | 53 | 17142793 | Koyo | Winergy
Rattlesnake | 54 | 17142794 | Koyo | Winergy
Rattlesnake | 55 | 17142795 | NTN | Nanjing
Rattlesnake | 56 | 17142796 | Koyo | Winergy
Rattlesnake | 57 | 17142797 | Koyo | Nanjing
Rattlesnake | 58 | 17142798 | NTN
Rattlesnake | 59 | 17142799 | Koyo | Nanjing
Rattlesnake | 60 | 17142800 | Koyo | Nanjing
Rattlesnake | 61 | 17142801 | NTN | Nanjing
Rattlesnake | 62 | 17142802 | NTN | Winergy
Rattlesnake | 66 | 17142803 | Koyo | Winergy
Rattlesnake | 67 | 17142804 | Koyo | Nanjing
Rattlesnake | 68 | 17142805 | NTN | Nanjing
Rattlesnake | 69 | 17142806 | Koyo | Winergy
Rattlesnake | 70 | 17142807 | NTN | Nanjing
Rattlesnake | 71 | 17142808 | NTN | Winergy
Rattlesnake | 72 | 17142809 | NTN | Winergy
Rattlesnake | 73 | 17142810 | NTN | Nanjing
Rattlesnake | 74 | 17142811 | Koyo | Nanjing
Rattlesnake | 75 | 17142812 | NTN | Winergy
Rattlesnake | 76 | 17142813 | NTN | Winergy
Rattlesnake | 77 | 17142814 | NTN | Winergy
Rattlesnake | 78 | 17142815 | NTN | Winergy
Rattlesnake | 79 | 17142816 | Koyo | Nanjing
Rattlesnake | 80 | 17142817 | NTN | Winergy
Rattlesnake | 81 | 17142818 | NTN | Nanjing
Rattlesnake | 82 | 17142819 | Koyo | Nanjing
Rattlesnake | 83 | 17142820 | NTN | Nanjing
Rattlesnake | 84 | 17142821 | Koyo | Nanjing
Rattlesnake | 85 | 17142822 | NTN | Winergy
Rattlesnake | 86 | 17142823 | Koyo | Winergy
Rattlesnake | 87 | 17142824 | Koyo | Nanjing
Rattlesnake | 88 | 17142825 | Koyo | Winergy
Rattlesnake | 89 | 17142826 | Koyo | Winergy
Rattlesnake | 90 | 17142827 | Koyo | Winergy
Rattlesnake | 91 | 17142828 | Koyo | Winergy
Rattlesnake | 92 | 17142829 | Koyo | Nanjing
Rattlesnake | 93 | 17142830 | Koyo | Winergy
Rattlesnake | 94 | 17142831 |  | Winergy
Rattlesnake | 95 | 17142832 | Koyo | Winergy
Rattlesnake | 96 | 17142833 | Koyo | Winergy
Rattlesnake | 97 | 17142834 | NTN | Winergy
Rattlesnake | 98 | 17142835 | NTN | Nanjing
Rattlesnake | 99 | 17142836 | Koyo | Winergy
Rattlesnake | 100 | 17142837 | NTN | Nanjing
Rattlesnake | 101 | 17142838 | Koyo | Nanjing
Rattlesnake | 102 | 17142839 | Koyo | Winergy
Rattlesnake | 103 | 17142840 | Koyo | Nanjing
Rattlesnake | 104 | 17142841 | Koyo | Winergy
Rattlesnake | 105 | 17142842 | Koyo | Nanjing
Rattlesnake | 106 | 17142843 | Koyo | Nanjing
Rattlesnake | 107 | 17142844 | Koyo | Winergy
Rattlesnake | 108 | 17142845 | Koyo | Nanjing
Rattlesnake | 109 | 17142846 | NTN | Nanjing
Rattlesnake | 110 | 17142847 | Koyo | Nanjing
Rattlesnake | 111 | 17142848 | Koyo | Nanjing
Rattlesnake | 112 | 17142849 |  | Nanjing
Rattlesnake | 113 | 17142850 | Koyo | Nanjing
Rattlesnake | 114 | 17142851 | NTN | Nanjing
Rattlesnake | 115 | 17142852 | NTN | Nanjing
Rattlesnake | 116 | 17142853 | NTN | Nanjing
Rattlesnake | 117 | 17142854 | Koyo | Winergy
Rattlesnake | 118 | 17142855 | NTN | Nanjing
Rattlesnake | 63 | 17143002 | Koyo | Nanjing
Rattlesnake | 64 | 17143003 | NTN | Winergy
Rattlesnake | 65 | 17143004 | Koyo | Nanjing
Buckeye | 1 | 17143133 | NTN | Winergy
Buckeye | 2 | 17143134 | Timken | Rexroth
Buckeye | 3 | 17143135 | Timken | Nanjing
Buckeye | 4 | 17143136 | Koyo | Rexroth
Buckeye | 5 | 17143137 | NTN | Winergy
Buckeye | 6 | 17143138 | NTN | Winergy
Buckeye | 7 | 17143139 | Koyo | Winergy
Buckeye | 8 | 17143140 | Koyo | Nanjing
Buckeye | 9 | 17143141 | Koyo | Rexroth
Buckeye | 10 | 17143142 | NTN | Winergy
Buckeye | 11 | 17143143 | Replacement Pending | Rexroth
Buckeye | 12 | 17143144 | Koyo | Winergy
Buckeye | 13 | 17143145 | Koyo | Nanjing
Buckeye | 14 | 17143146 | Timken | Nanjing
Buckeye | 15 | 17143147 | Koyo | Winergy
Buckeye | 16 | 17143148 | Koyo | Winergy
Buckeye | 17 | 17143149 | Timken | Rexroth
Buckeye | 18 | 17143150 | NTN | Winergy
Buckeye | 19 | 17143151 | Koyo | Rexroth
Buckeye | 20 | 17143152 | NTN | Rexroth
Buckeye | 21 | 17143153 | NTN | Rexroth
Buckeye | 22 | 17143154 | Timken | Rexroth
Buckeye | 23 | 17143155 | Koyo | Winergy
Buckeye | 24 | 17143156 | NTN | Rexroth
Buckeye | 25 | 17143157 | Koyo | Rexroth
Buckeye | 26 | 17143158 | Koyo | Rexroth
Buckeye | 27 | 17143159 | Koyo | Nanjing
Buckeye | 28 | 17143160 | NTN | Rexroth
Buckeye | 29 | 17143161 | Koyo | Winergy
Buckeye | 30 | 17143162 | Koyo | Nanjing
Buckeye | 31 | 17143163 | Koyo | Winergy
Buckeye | 32 | 17143164 | Koyo | Rexroth
Buckeye | 33 | 17143165 | NTN | Rexroth
Buckeye | 34 | 17143166 | Timken | Nanjing
Buckeye | 35 | 17143167 | Koyo | Rexroth
Buckeye | 36 | 17143168 | Koyo | Rexroth
Buckeye | 37 | 17143169 | NTN | Rexroth
Buckeye | 38 | 17143170 | NTN | Rexroth
Buckeye | 39 | 17143171 | NTN | Rexroth
Buckeye | 40 | 17143172 | NTN | Winergy
Buckeye | 41 | 17143173 | NTN | Winergy
Buckeye | 42 | 17143174 | Koyo | Rexroth
Buckeye | 43 | 17143175 | Koyo | Nanjing
Buckeye | 44 | 17143176 | Pending Repair Report | Rexroth
Buckeye | 45 | 17143177 | Koyo | Winergy
Buckeye | 46 | 17143178 | NTN | Winergy
Buckeye | 47 | 17143179 | Timken | Nanjing
Buckeye | 48 | 17143180 | Pending Repair Report | Rexroth
Buckeye | 49 | 17143181 | Koyo | Winergy
Buckeye | 50 | 17143182 | Koyo | Rexroth
Buckeye | 51 | 17143183 | NTN | Rexroth
Buckeye | 52 | 17143184 | Koyo | Rexroth
Buckeye | 53 | 17143185 | Koyo | Winergy
Buckeye | 54 | 17143186 | NTN | Rexroth
Buckeye | 55 | 17143187 | NTN | Rexroth
Buckeye | 56 | 17143188 | NTN | Rexroth
Buckeye | 57 | 17143189 | NTN | Rexroth
Buckeye | 58 | 17143190 | NTN | Rexroth
Buckeye | 59 | 17143191 | Koyo | Winergy
Buckeye | 60 | 17143192 | NTN | Winergy
Buckeye | 61 | 17143193 | Koyo | Rexroth
Buckeye | 62 | 17143194 | Timken | Winergy
Buckeye | 63 | 17143195 | NTN | Rexroth
Buckeye | 64 | 17143196 | NTN | Nanjing
Buckeye | 65 | 17143197 | NTN | Winergy
Buckeye | 66 | 17143198 | Koyo | Rexroth
Buckeye | 67 | 17143199 | Pending Repair Report | Rexroth
Buckeye | 68 | 17143200 | Koyo | Rexroth
Buckeye | 69 | 17143201 | Koyo | Winergy
Buckeye | 70 | 17143202 | Replacement Pending | Winergy
Buckeye | 71 | 17143203 | Koyo | Winergy
Buckeye | 72 | 17143204 | NTN | Winergy
Buckeye | 73 | 17143205 | NTN | Winergy
Buckeye | 74 | 17143206 | Koyo | Winergy
Buckeye | 75 | 17143207 | Koyo | Nanjing
Buckeye | 76 | 17143208 | Koyo | Rexroth
Buckeye | 77 | 17143209 | Koyo | Winergy
Buckeye | 78 | 17143210 | NTN | Rexroth
Buckeye | 79 | 17143211 | Timken | Winergy
Buckeye | 80 | 17143212 | Replacement Pending | Winergy
Buckeye | 81 | 17143213 | Timken | Nanjing
Buckeye | 82 | 17143214 |  | Rexroth
Buckeye | 83 | 17143215 | Timken | Rexroth
Buckeye | 84 | 17143216 | Timken | Winergy
Buckeye | 85 | 17143217 | Koyo | Rexroth
Buckeye | 86 | 17143218 | Koyo | Rexroth
Buckeye | 87 | 17143219 | Koyo | Rexroth
Buckeye | 88 | 17143220 | Koyo | Winergy
Buckeye | 89 | 17143221 | Koyo | Rexroth
Buckeye | 90 | 17143222 | NTN | Rexroth
Buckeye | 91 | 17143223 | NTN | Rexroth
Buckeye | 92 | 17143224 | Timken | Rexroth
Buckeye | 93 | 17143225 | Koyo | Nanjing
Buckeye | 94 | 17143226 | Koyo | Winergy
Buckeye | 95 | 17143227 | Timken | Winergy
Buckeye | 96 | 17143228 | Koyo | Winergy
Buckeye | 97 | 17143229 | Koyo | Nanjing
Buckeye | 98 | 17143230 |  | Winergy
Buckeye | 99 | 17143231 | NTN | Rexroth
Buckeye | 100 | 17143232 | NTN
Gunsight | 1 | 17144020 | Timken | Nanjing
Gunsight | 2 | 17144021 | SKF | Nanjing
Gunsight | 3 | 17144022 | NTN | Nanjing
Gunsight | 4 | 17144023 | NTN
Gunsight | 5 | 17144024 | NTN | Nanjing
Gunsight | 6 | 17144025 | NTN | Nanjing
Gunsight | 7 | 17144026 | NTN | Nanjing
Gunsight | 8 | 17144027 | NTN | Nanjing
Gunsight | 9 | 17144028 | NTN
Gunsight | 10 | 17144029 | NTN | Winergy
Gunsight | 11 | 17144030 | NTN | Pending Repair Report
Gunsight | 12 | 17144031 | NTN | Nanjing
Gunsight | 13 | 17144032 | NTN | Winergy
Gunsight | 14 | 17144033 | NTN | Winergy
Gunsight | 15 | 17144034 | NTN | Nanjing
Gunsight | 16 | 17144035 |  | Nanjing
Gunsight | 17 | 17144036 | NTN | Nanjing
Gunsight | 18 | 17144037 | NTN | Nanjing
Gunsight | 19 | 17144038 | NTN | Nanjing
Gunsight | 20 | 17144039 | SKF | Nanjing
Gunsight | 21 | 17144040 | SKF | Winergy
Gunsight | 22 | 17144041 | Timken | Nanjing
Gunsight | 23 | 17144042 | SKF | Nanjing
Gunsight | 24 | 17144043 | SKF | Nanjing
Gunsight | 25 | 17144044 | NTN | Nanjing
Gunsight | 26 | 17144045 | NTN | Nanjing
Gunsight | 27 | 17144046 | SKF | Nanjing
Gunsight | 28 | 17144047 | NTN | Nanjing
Gunsight | 29 | 17144048 | SKF | Nanjing
Gunsight | 30 | 17144049 | NTN | Winergy
Gunsight | 31 | 17144050 | NTN | Winergy
Gunsight | 32 | 17144051 | NTN | Nanjing
Gunsight | 33 | 17144052 | NTN | Winergy
Gunsight | 34 | 17144053 | NTN | Winergy
Gunsight | 35 | 17144054 | SKF | Winergy
Gunsight | 36 | 17144055 | NTN | Winergy
Gunsight | 37 | 17144056 | SKF
Gunsight | 38 | 17144057 | NTN | Nanjing
Gunsight | 39 | 17144058 | NTN | Nanjing
Gunsight | 40 | 17144059 | NTN | Nanjing
Gunsight | 41 | 17144060 | NTN | Winergy
Gunsight | 42 | 17144061 | NTN | Winergy
Gunsight | 43 | 17144062 | NTN | Nanjing
Gunsight | 44 | 17144063 | Timken | Winergy
Gunsight | 45 | 17144064 | NTN | Winergy
Gunsight | 46 | 17144065 | NTN | Nanjing
Gunsight | 47 | 17144066 | NTN | Winergy
Gunsight | 48 | 17144067 | SKF | Nanjing
Gunsight | 49 | 17144068 | NTN | Nanjing
Gunsight | 50 | 17144069 | SKF | Winergy
Gunsight | 51 | 17144070 | SKF | Nanjing
Gunsight | 52 | 17144071 | NTN | Nanjing
Gunsight | 53 | 17144072 | NTN | Nanjing
Gunsight | 54 | 17144073 | SKF | Nanjing
Gunsight | 55 | 17144074 | NTN | Nanjing
Gunsight | 56 | 17144075 | NTN | Pending Repair Report
Gunsight | 57 | 17144076 | NTN | Winergy
Gunsight | 58 | 17144077 | NTN | Nanjing
Gunsight | 59 | 17144078 | NTN | Winergy
Gunsight | 60 | 17144079 | NTN | Replacement Pending
Gunsight | 61 | 17144080 | SKF | Nanjing
Gunsight | 62 | 17144081 | NTN | Winergy
Prairie Breeze II | 201 | 17150590 | NTN | Nanjing
Prairie Breeze II | 202 | 17150591 | NTN | ZF
Prairie Breeze II | 203 | 17150592 | NTN | Nanjing
Prairie Breeze II | 204 | 17150593 | NTN | Nanjing
Prairie Breeze III | 301 | 17150594 | NTN | Nanjing
Prairie Breeze III | 302 | 17150595 | NTN | Winergy
Prairie Breeze II | 205 | 17150604 | NTN | Nanjing
Prairie Breeze II | 206 | 17150605 | NTN | Pending Repair Report
Prairie Breeze II | 207 | 17150606 | Koyo | Winergy
Prairie Breeze II | 208 | 17150607 | NTN | Nanjing
Prairie Breeze II | 209 | 17150608 | NTN | Winergy
Prairie Breeze II | 210 | 17150609 | Koyo | Nanjing
Prairie Breeze II | 211 | 17150610 | NTN | Nanjing
Prairie Breeze II | 212 | 17150611 | NTN | Pending Repair Report
Prairie Breeze II | 213 | 17150612 | NTN | Nanjing
Prairie Breeze II | 214 | 17150613 | NTN | Nanjing
Prairie Breeze II | 215 | 17150614 | NTN
Prairie Breeze II | 216 | 17150615 | Timken
Prairie Breeze II | 217 | 17150616 | NTN | Nanjing
Prairie Breeze II | 218 | 17150617 | NTN | Winergy
Prairie Breeze II | 219 | 17150618 | NTN | Pending Repair Report
Prairie Breeze II | 220 | 17150619 | Koyo | Pending Repair Report
Prairie Breeze II | 221 | 17150620 | NTN | Winergy
Prairie Breeze II | 222 | 17150621 | Koyo
Prairie Breeze II | 223 | 17150622 | NTN | Winergy
Prairie Breeze II | 224 | 17150623 | NTN | Nanjing
Prairie Breeze II | 225 | 17150624 | NTN | Winergy
Prairie Breeze II | 226 | 17150625 | NTN | Winergy
Prairie Breeze II | 227 | 17150626 | Pending Repair Report
Prairie Breeze II | 228 | 17150627 | Koyo | Rexroth
Prairie Breeze II | 229 | 17150628 | NTN | Replacement Pending
Prairie Breeze II | 230 | 17150629 | Koyo | Winergy
Prairie Breeze II | 231 | 17150630 | NTN | Winergy
Prairie Breeze II | 232 | 17150631 | NTN | Replacement Pending
Prairie Breeze II | 233 | 17150632 | Timken | Nanjing
Prairie Breeze II | 234 | 17150633 | Koyo | Winergy
Prairie Breeze II | 235 | 17150634 | Koyo | Pending Repair Report
Prairie Breeze II | 236 | 17150635 | NTN | Nanjing
Prairie Breeze II | 237 | 17150636 | Koyo | Pending Repair Report
Prairie Breeze II | 238 | 17150637 | NTN | Winergy
Prairie Breeze II | 239 | 17150638 | NTN | Winergy
Prairie Breeze II | 240 | 17150639 | Koyo
Prairie Breeze II | 241 | 17150640 | Pending Repair Report | Nanjing
Buckeye | 101 | 17151493 | NTN | Winergy
Buckeye | 103 | 17151494 | Koyo | Winergy
Buckeye | 104 | 17151495 | Koyo | Nanjing
Buckeye | 105 | 17151496 | NTN | Pending Repair Report
Buckeye | 106 | 17151497 | NTN | Rexroth
Buckeye | 107 | 17151498 | Koyo | Rexroth
Buckeye | 108 | 17151499 | NTN | Winergy
Buckeye | 109 | 17151500 | Koyo | Rexroth
Buckeye | 111 | 17151501 | NTN | Rexroth
Buckeye | 112 | 17151502 | Timken | Rexroth
Buckeye | 113 | 17151503 | NTN | Winergy
Buckeye | 115 | 17151504 | Koyo | Nanjing
Wake | 1 | 17152493 | NTN | Nanjing
Wake | 2 | 17152494 | NTN | Nanjing
Wake | 3 | 17152495 | NTN | Nanjing
Wake | 4 | 17152496 | Timken | Winergy
Wake | 5 | 17152497 | NTN | Nanjing
Wake | 6 | 17152498 | NTN | Nanjing
Wake | 7 | 17152499 | SKF | Winergy
Wake | 8 | 17152500 | SKF | Nanjing
Wake | 9 | 17152501 | SKF | Nanjing
Wake | 10 | 17152502 | NTN | Pending Repair Report
Wake | 11 | 17152503 | NTN
Wake | 12 | 17152504 | NTN | Nanjing
Wake | 13 | 17152505 | Timken | Pending Repair Report
Wake | 14 | 17152506 | NTN | Winergy
Wake | 15 | 17152507 | SKF
Wake | 16 | 17152508 | NTN | Winergy
Wake | 17 | 17152509 | NTN | Winergy
Wake | 18 | 17152510 | NTN | Nanjing
Wake | 19 | 17152511 | NTN | Nanjing
Wake | 20 | 17152512 | NTN
Wake | 21 | 17152513 | NTN | Winergy
Wake | 22 | 17152514 | SKF | Rexroth
Wake | 23 | 17152515 | NTN | Nanjing
Wake | 24 | 17152516 | NTN | Nanjing
Wake | 25 | 17152517 | SKF | Nanjing
Wake | 26 | 17152518 | NTN | Nanjing
Wake | 27 | 17152519 | SKF | Nanjing
Wake | 28 | 17152520 | NTN | Nanjing
Wake | 29 | 17152521 | NTN | Nanjing
Wake | 30 | 17152522 | NTN | Winergy
Wake | 31 | 17152523 | NTN | Winergy
Wake | 32 | 17152524 | NTN | Nanjing
Wake | 33 | 17152525 | NTN | Nanjing
Wake | 34 | 17152526 | Koyo | Nanjing
Wake | 35 | 17152527 | SKF | Pending Repair Report
Wake | 36 | 17152528 | NTN | Pending Repair Report
Wake | 37 | 17152529 | NTN | Winergy
Wake | 38 | 17152530 | SKF | Nanjing
Wake | 39 | 17152531 | SKF | Nanjing
Wake | 40 | 17152532 | Replacement Pending | Winergy
Wake | 41 | 17152533 | SKF | Rexroth
Wake | 42 | 17152534 | SKF | Nanjing
Wake | 43 | 17152535 | NTN | Winergy
Wake | 44 | 17152536 | NTN | Pending Repair Report
Wake | 45 | 17152537 | NTN
Wake | 46 | 17152538 | NTN | Nanjing
Wake | 47 | 17152539 | NTN | Winergy
Wake | 48 | 17152540 | SKF | Nanjing
Wake | 49 | 17152541 | NTN | Nanjing
Wake | 50 | 17152542 | NTN | Nanjing
Wake | 51 | 17152543 | SKF | Nanjing
Wake | 52 | 17152544 | NTN | Nanjing
Wake | 53 | 17152545 | NTN
Wake | 54 | 17152546
Wake | 55 | 17152547 | NTN
Wake | 56 | 17152548 | NTN | Winergy
Wake | 57 | 17152549 | SKF | Nanjing
Wake | 58 | 17152550 | SKF | Pending Repair Report
Wake | 59 | 17152551 | Koyo | Winergy
Wake | 60 | 17152552 | NTN | Nanjing
Wake | 61 | 17152553 | NTN | Nanjing
Wake | 62 | 17152554 | NTN | Nanjing
Wake | 63 | 17152555 | SKF | Nanjing
Wake | 64 | 17152556 | SKF | Winergy
Wake | 65 | 17152557 | NTN | Winergy
Wake | 66 | 17152558 | SKF | Nanjing
Wake | 67 | 17152559 | NTN | Pending Repair Report
Wake | 68 | 17152560 | NTN | Nanjing
Wake | 69 | 17152561 | Koyo | Winergy
Wake | 70 | 17152562 | SKF | Nanjing
Wake | 71 | 17152563 | NTN | Winergy
Wake | 72 | 17152564 | SKF | Nanjing
Wake | 73 | 17152565 |  | Nanjing
Wake | 74 | 17152566 | NTN | Pending Repair Report
Wake | 75 | 17152567 | NTN | Winergy
Wake | 76 | 17152568 | SKF
Wake | 77 | 17152569 | NTN | Pending Repair Report
Wake | 78 | 17152570 | SKF | Nanjing
Wake | 79 | 17152571 | NTN | Winergy
Wake | 80 | 17152572 | SKF
Wake | 81 | 17152573 | SKF | Nanjing
Wake | 82 | 17152574 | NTN | Nanjing
Wake | 83 | 17152575 | NTN | Nanjing
Wake | 84 | 17152576 | NTN | Nanjing
Wake | 85 | 17152577 | NTN | Nanjing
Wake | 86 | 17152578 | NTN | Nanjing
Wake | 87 | 17152579 | NTN | Pending Repair Report
Wake | 88 | 17152580 | NTN | Nanjing
Wake | 89 | 17152581 | SKF | Nanjing
Wake | 90 | 17152582 | SKF | Nanjing
Wake | 91 | 17152583 | NTN | Nanjing
Wake | 92 | 17152584 | SKF | Nanjing
Wake | 93 | 17152585 | NTN | Nanjing
Wake | 94 | 17152586 | NTN | Winergy
Wake | 95 | 17152587 | NTN | Nanjing
Wake | 96 | 17152588 | SKF | Winergy
Wake | 97 | 17152589 | Timken | Nanjing
Wake | 98 | 17152590 | SKF | Nanjing
Wake | 99 | 17152591 | SKF | Rexroth
Wake | 100 | 17152592 | NTN | Nanjing
Wake | 101 | 17152593 | NTN | Rexroth
Wake | 102 | 17152594 | SKF | Nanjing
Wake | 103 | 17152595 | NTN | Pending Repair Report
Wake | 104 | 17152596 | NTN | Winergy
Wake | 105 | 17152597 | NTN | Nanjing
Wake | 106 | 17152598 | Koyo | Nanjing
Wake | 107 | 17152599
Wake | 108 | 17152600 | NTN
Wake | 109 | 17152601 | NTN | Nanjing
Wake | 110 | 17152602 | NTN | Winergy
Wake | 111 | 17152603 | SKF | Nanjing
Wake | 112 | 17152604 | NTN | Nanjing
Wake | 113 | 17152605 | NTN | Winergy
Wake | 114 | 17152606 | NTN | Pending Repair Report
Wake | 115 | 17152607 | NTN | Nanjing
Wake | 116 | 17152608 | NTN | Winergy
Wake | 117 | 17152609 | NTN | Nanjing
Wake | 118 | 17152610 | Koyo
Wake | 119 | 17152611 | NTN | Nanjing
Wake | 120 | 17152612 | SKF | Nanjing
Wake | 121 | 17152613 | Timken
Wake | 122 | 17152614 | Koyo | Nanjing
Wake | 123 | 17152615 | NTN
Wake | 124 | 17152616 | Koyo | Pending Repair Report
Wake | 125 | 17152617 | NTN | Winergy
Prairie Breeze III | 303 | 17153630 | SKF | Rexroth
Prairie Breeze III | 304 | 17153631 | Timken | Nanjing
Prairie Breeze III | 305 | 17153632 | SKF
Prairie Breeze III | 306 | 17153633 | Pending Repair Report | Pending Repair Report
Prairie Breeze III | 307 | 17153634 | Koyo | Rexroth
Prairie Breeze III | 308 | 17153635 | NTN | Winergy
Prairie Breeze III | 309 | 17153636 | NTN | Rexroth
Prairie Breeze III | 310 | 17153637 | NTN | Pending Repair Report
Prairie Breeze III | 311 | 17153638 | NTN | ZF
Prairie Breeze III | 312 | 17153639 | NTN | Winergy
Prairie Breeze III | 313 | 17153640 | NTN | Winergy
Prairie Breeze III | 314 | 17153641 | NTN | Winergy
Prairie Breeze III | 315 | 17153642 | SKF | Pending Repair Report
Prairie Breeze III | 316 | 17153643 | SKF | Winergy
Prairie Breeze III | 317 | 17153875 | NTN | ZF
Prairie Breeze III | 318 | 17153876 | Timken | Pending Repair Report
Prairie Breeze III | 319 | 17153877 | NTN | Winergy
Prairie Breeze III | 320 | 17153878 | NTN | Winergy
Gunsight | 63 | 17154618 | SKF | Nanjing
Gunsight | 64 | 17154619 | NTN | Winergy
Gunsight | 65 | 17154620 | NTN | Nanjing
Gunsight | 66 | 17154621 | NTN | Nanjing
Gunsight | 67 | 17154622 | NTN | Nanjing
Wake | 126 | 17155157 | SKF | Pending Repair Report
Wake | 127 | 17155158 | NTN | Nanjing
Wake | 128 | 17155159 | SKF | Nanjing
Wake | 129 | 17155160 | NTN | Nanjing
Wake | 130 | 17155161 | NTN | Nanjing
Wake | 131 | 17155162 | NTN | Nanjing
Wake | 132 | 17155163 | Koyo | Nanjing
Wake | 133 | 17155164 | SKF | Nanjing
Wake | 134 | 17155165 | SKF | Pending Repair Report
Wake | 135 | 17155166 | NTN | Nanjing
Wake | 136 | 17155167 | SKF | ZF
Wake | 137 | 17155168 | SKF | Nanjing
Wake | 138 | 17155169 | NTN | Nanjing
Wake | 139 | 17155170 | NTN | Winergy
Wake | 140 | 17155171 | SKF | Nanjing
Wake | 141 | 17155172 | NTN
Wake | 142 | 17155173 | SKF | ZF
Wake | 143 | 17155174 | NTN | Nanjing
Wake | 144 | 17155175 | SKF | Nanjing
Wake | 145 | 17155176 | NTN | Nanjing
Wake | 146 | 17155177 | NTN | Nanjing
Wake | 147 | 17155178 | NTN | Winergy
Wake | 148 | 17155179 | SKF | Nanjing
Wake | 149 | 17155180 | NTN | Nanjing
Wake | 150 | 17155181 | NTN | Nanjing
Miami | 1 | 18133232 | Koyo | Nanjing
Miami | 2 | 18133233 | Koyo | Nanjing
Miami | 3 | 18133234 |  | Nanjing
Miami | 4 | 18133235 | Koyo | Nanjing
Miami | 5 | 18133236 | NTN | Nanjing
Miami | 6 | 18133237 | NTN | Nanjing
Miami | 7 | 18133238 |  | Nanjing
Miami | 8 | 18133239 | Koyo | ZF
Miami | 9 | 18133240
Miami | 10 | 18133241 | NTN | Pending Repair Report
Miami | 11 | 18133242 | NTN | Nanjing
Miami | 12 | 18133243 | NTN | Nanjing
Miami | 13 | 18133244 | NTN | Nanjing
Miami | 14 | 18133245 | Koyo | Nanjing
Miami | 15 | 18133246 |  | Nanjing
Miami | 16 | 18133247 |  | Nanjing
Miami | 17 | 18133248 | NTN | Nanjing
Miami | 18 | 18133249 |  | Nanjing
Miami | 19 | 18133250 | NTN | Nanjing
Miami | 20 | 18133251 |  | Nanjing
Miami | 21 | 18133252 | NTN | Nanjing
Miami | 22 | 18133253 |  | Nanjing
Miami | 23 | 18133254 | Koyo | Nanjing
Miami | 24 | 18133255 | NTN | Nanjing
Miami | 25 | 18133256 | NTN | Nanjing
Miami | 26 | 18133257 | Koyo | Nanjing
Miami | 27 | 18133258 | NTN | Nanjing
Miami | 28 | 18133259
Miami | 29 | 18133260 | Koyo | Nanjing
Miami | 30 | 18133261 | NTN | Nanjing
Miami | 31 | 18133262 | NTN | Nanjing
Miami | 32 | 18133263 | NTN | Nanjing
Miami | 33 | 18133264 |  | Nanjing
Miami | 34 | 18133265 | Koyo | Nanjing
Miami | 35 | 18133266 | NTN | Nanjing
Miami | 36 | 18133267 | NTN | Nanjing
Miami | 37 | 18133268 | NTN
Miami | 38 | 18133269 | Replacement Pending | Replacement Pending
Miami | 39 | 18133270 | Koyo | Nanjing
Miami | 40 | 18133271 | Koyo | Nanjing
Miami | 41 | 18133272 |  | Nanjing
Miami | 42 | 18133273 | NTN | Nanjing
Miami | 43 | 18133274 | NTN | Nanjing
Miami | 44 | 18133275 | Koyo | Nanjing
Miami | 45 | 18133276 | Koyo
Miami | 46 | 18133277 | Koyo
Miami | 47 | 18133278 | Koyo
Miami | 48 | 18133279 | Replacement Pending | Nanjing
Miami | 49 | 18133280 | Koyo | Nanjing
Miami | 50 | 18133281 |  | Nanjing
Miami | 51 | 18133282 |  | Nanjing
Miami | 52 | 18133283 | Koyo
Miami | 53 | 18133284 | NTN | Nanjing
Miami | 54 | 18133285 | NTN
Miami | 55 | 18133286 | NTN | Nanjing
Miami | 56 | 18133287 |  | Nanjing
Miami | 57 | 18133288 | NTN | Nanjing
Miami | 58 | 18133289 | NTN | Nanjing
Miami | 59 | 18133290 | Koyo | Nanjing
Miami | 120 | 18133291 |  | Nanjing
Miami | 60 | 18133292 | Koyo | Nanjing
Miami | 61 | 18133293 | NTN | Nanjing
Miami | 62 | 18133294 | Koyo
Miami | 63 | 18133295 | NTN | Nanjing
Miami | 64 | 18133296 | Koyo | Nanjing
Miami | 65 | 18133297 |  | Nanjing
Miami | 66 | 18133298 |  | Nanjing
Miami | 67 | 18133299 | Koyo | Nanjing
Miami | 68 | 18133300 | NTN | Nanjing
Miami | 69 | 18133301 | NTN
Miami | 70 | 18133302 | NTN | Nanjing
Miami | 71 | 18133303 | Koyo | Pending Repair Report
Miami | 72 | 18133304
Miami | 73 | 18133305 |  | Nanjing
Miami | 74 | 18133306 | NTN | Nanjing
Miami | 75 | 18133307 |  | Nanjing
Miami | 76 | 18133308 | Koyo | Nanjing
Miami | 77 | 18133309
Miami | 78 | 18133310 | NTN | Nanjing
Miami | 79 | 18133311 |  | Nanjing
Miami | 80 | 18133312 | Koyo | Nanjing
Miami | 81 | 18133313 | NTN | Nanjing
Miami | 82 | 18133314 | NTN | Nanjing
Miami | 83 | 18133315 | Koyo | Nanjing
Miami | 84 | 18133316 | NTN | Nanjing
Miami | 85 | 18133317 | NTN | Nanjing
Miami | 86 | 18133318 | Koyo | Nanjing
Miami | 87 | 18133319 |  | Nanjing
Miami | 88 | 18133320 | Koyo | Nanjing
Miami | 89 | 18133321 | NTN | Nanjing
Miami | 90 | 18133322 | Koyo | Nanjing
Miami | 91 | 18133323 | NTN | Nanjing
Miami | 92 | 18133324 | Koyo | Nanjing
Miami | 93 | 18133325 | Koyo | Nanjing
Miami | 94 | 18133326 | Koyo | Nanjing
Miami | 95 | 18133327 | Koyo | Nanjing
Miami | 96 | 18133328
Miami | 97 | 18133329 | Koyo | Nanjing
Miami | 98 | 18133330 |  | Nanjing
Miami | 99 | 18133331 | Koyo | Nanjing
Miami | 100 | 18133332 | Koyo | Nanjing
Miami | 101 | 18133333 | Koyo
Miami | 102 | 18133334 | Koyo | Nanjing
Miami | 103 | 18133335 | Replacement Pending | Nanjing
Miami | 104 | 18133336 | NTN
Miami | 105 | 18133337
Miami | 106 | 18133338 |  | Nanjing
Miami | 107 | 18133339 | Koyo | Nanjing
Miami | 108 | 18133340 | Koyo | Nanjing
Miami | 109 | 18133341 | NTN | Nanjing
Miami | 110 | 18133342
Miami | 111 | 18133343 | Koyo
Miami | 112 | 18133344 | Pending Repair Report | Nanjing
Miami | 113 | 18133345 | NTN
Miami | 114 | 18133346 |  | Nanjing
Miami | 115 | 18133347 | Koyo | Nanjing
Miami | 116 | 18133348 | Koyo | Winergy
Miami | 117 | 18133349 | FAG | Nanjing
Miami | 118 | 18133350 | Koyo | Nanjing
Miami | 119 | 18133351 | Koyo | Nanjing
Miami | 122 | 18133352 | NTN | Nanjing
Miami | 123 | 18133353 | NTN | Nanjing
Miami | 124 | 18133354 | Koyo | Nanjing
Miami | 125 | 18133355 | Koyo | Nanjing
Miami | 126 | 18133356 | Koyo | Nanjing
Miami | 127 | 18133357 | Koyo | ZF
Miami | 128 | 18133358 | Koyo
Miami | 129 | 18133359 | Koyo | Nanjing
Miami | 130 | 18133360 | Koyo
Miami | 131 | 18133361 | Koyo | Nanjing
Miami | 132 | 18133362 | Koyo | Nanjing
Miami | 133 | 18133363 | Koyo | Nanjing
Miami | 134 | 18133364 | Koyo | Nanjing
Miami | 135 | 18133365 | Koyo | Nanjing
Miami | 136 | 18133366 | NTN | Nanjing
Miami | 137 | 18133367 | NTN | Nanjing
Miami | 138 | 18133368 | NTN | Nanjing
Miami | 139 | 18133369 | NTN | Nanjing
Miami | 140 | 18133370 |  | Rexroth
Miami | 141 | 18133371 | Koyo | Nanjing
Miami | 142 | 18133372 |  | Nanjing
Miami | 143 | 18133373 | Koyo | Nanjing
Miami | 144 | 18133374 | Koyo | Nanjing
Miami | 145 | 18133375 | Koyo | Nanjing
Miami | 146 | 18133376 | NTN | Nanjing
Miami | 147 | 18133377 | NTN | Nanjing
Miami | 148 | 18133378 | NTN | Nanjing
Miami | 149 | 18133379 |  | Nanjing
Miami | 150 | 18133380 | Koyo | Nanjing
Miami | 151 | 18133381 | NTN | Nanjing
Miami | 152 | 18133382 | Koyo | Nanjing
Miami | 153 | 18133383 | NTN | Rexroth
Miami | 121 | 18133384 | NTN
Miami | 154 | 18133385 |  | Nanjing
Miami | 155 | 18133386 | Koyo | Rexroth
Miami | 156 | 18133387 |  | Winergy
Forward | 213 | 18133775 | Koyo | Winergy
Bethel | 1 | 23157123 |  | Nanjing
Bethel | 2 | 23157124 | NTN | Nanjing
Bethel | 3 | 23157125 |  | Nanjing
Bethel | 4 | 23157126 | NTN | Nanjing
Bethel | 5 | 23157127 | NTN | Nanjing
Bethel | 6 | 23157128 | NTN | Winergy
Bethel | 7 | 23157129 | NTN
Bethel | 8 | 23157130 | NTN | Winergy
Bethel | 9 | 23157131 | NTN | Winergy
Bethel | 10 | 23157132 | NTN | Nanjing
Bethel | 11 | 23157133 | NTN | Nanjing
Bethel | 12 | 23157134 | NTN | Nanjing
Bethel | 13 | 23157135 |  | Nanjing
Bethel | 14 | 23157136 | NTN | Nanjing
Bethel | 15 | 23157137 |  | Winergy
Bethel | 16 | 23157138 | NTN
Bethel | 17 | 23157139
Bethel | 18 | 23157140 |  | Winergy
Bethel | 19 | 23157141 | NTN | Nanjing
Bethel | 20 | 23157142 | SKF
Bethel | 21 | 23157143 | NTN | Nanjing
Bethel | 22 | 23157144 | NTN | Winergy
Bethel | 23 | 23157145 | NTN
Bethel | 24 | 23157146 | NTN | Nanjing
Bethel | 25 | 23157147 | Timken | Nanjing
Bethel | 26 | 23157148 | NTN | Winergy
Bethel | 27 | 23157149 | NTN | Nanjing
Bethel | 28 | 23157150 | NTN | Winergy
Bethel | 29 | 23157151 | NTN | Nanjing
Bethel | 30 | 23157152 | SKF
Bethel | 31 | 23157153 | Koyo
Bethel | 32 | 23157154 | Koyo | Nanjing
Bethel | 33 | 23157155 | NTN | Winergy
Bethel | 34 | 23157156 | NTN | Nanjing
Bethel | 35 | 23157157 | NTN | Nanjing
Bethel | 36 | 23157158 |  | Nanjing
Bethel | 37 | 23157159 | NTN | Winergy
Bethel | 38 | 23157160 | NTN | Winergy
Bethel | 39 | 23157161 | NTN | Nanjing
Bethel | 40 | 23157162 | NTN | Winergy
Bethel | 41 | 23157163 | Koyo | Nanjing
Bethel | 42 | 23157164 | NTN | Nanjing
Bethel | 43 | 23157165 | NTN | Replacement Pending
Bethel | 44 | 23157166 | NTN | Nanjing
Bethel | 45 | 23157167 | NTN | Winergy
Bethel | 46 | 23157168 | NTN | Winergy
Bethel | 47 | 23157169 | NTN | Winergy
Bethel | 48 | 23157170 | NTN | Replacement Pending
Bethel | 49 | 23157171 | NTN | Nanjing
Bethel | 50 | 23157172 | NTN | Winergy
Bethel | 51 | 23157173 | NTN | Winergy
Bethel | 52 | 23157174 | NTN | Winergy
Bethel | 53 | 23157175 | NTN | Winergy
Bethel | 54 | 23157176 |  | Replacement Pending
Bethel | 55 | 23157177 | NTN | Nanjing
Bethel | 56 | 23157178 | NTN | Replacement Pending
Bethel | 57 | 23157179 | NTN | Winergy
Bethel | 58 | 23157180 | NTN
Bethel | 59 | 23157181 | NTN | Winergy
Bethel | 60 | 23157182 | NTN | Winergy
Bethel | 61 | 23157183 | NTN | Nanjing
Bethel | 62 | 23157184 | NTN | Nanjing
Bethel | 63 | 23157185 | NTN | Nanjing
Bethel | 64 | 23157186 | NTN | Nanjing
Bethel | 65 | 23157187 | NTN | Nanjing
Bethel | 66 | 23157188 | Koyo | Nanjing
Bethel | 67 | 23157189 | NTN | Nanjing
Bethel | 68 | 23157190 | NTN | Nanjing
Bethel | 69 | 23157191 | NTN | Nanjing
Bethel | 70 | 23157192 | NTN | Winergy
Bethel | 71 | 23157193 | NTN | Winergy
Bethel | 72 | 23157194 | NTN | Winergy
Bethel | 73 | 23157195 | NTN | Winergy
Bethel | 74 | 23157196 | NTN | Winergy
Bethel | 75 | 23157197 | NTN | Winergy
Bethel | 76 | 23157198 | NTN | Winergy
Bethel | 77 | 23157199 | NTN | Winergy
Bethel | 78 | 23157200 | NTN
Bethel | 79 | 23157201 |  | Nanjing
Bethel | 80 | 23157202 | NTN
Bethel | 81 | 23157203 | NTN
Bethel | 82 | 23157204 | Pending Repair Report | Nanjing
Bethel | 83 | 23157205 | Koyo | Nanjing
Bethel | 84 | 23157206 | NTN | Nanjing
Bethel | 85 | 23157207 | NTN | Nanjing
Bethel | 86 | 23157208 | NTN
Bethel | 87 | 23157209 | SKF | Nanjing
Bethel | 88 | 23157210 | Koyo | Nanjing
Bethel | 89 | 23157211 | NTN | Nanjing
Bethel | 90 | 23157212 | NTN | Winergy
Bethel | 91 | 23157213 | Timken
Bethel | 92 | 23157214 | NTN | Winergy
Bethel | 93 | 23157215 | NTN | Nanjing
Bethel | 94 | 23157216 | NTN | Winergy
Bethel | 95 | 23157217 | NTN | Winergy
Bethel | 96 | 23157218
Bethel | 97 | 23157219 | NTN | Winergy
Bethel | 98 | 23157220 | NTN | Nanjing
Bethel | 99 | 23157221 | Koyo | Winergy
Bethel | 100 | 23157222 | Koyo | Winergy
Bethel | 101 | 23157223 | NTN | Winergy
Bethel | 102 | 23157224 | NTN | Nanjing
Bethel | 103 | 23157225 | NTN | Winergy
Bethel | 104 | 23157226 | NTN | Winergy
Bethel | 105 | 23157227 | NTN | Replacement Pending
Bethel | 106 | 23157228 | NTN | Winergy
Bethel | 107 | 23157229 | NTN | Winergy
Bethel | 108 | 23157230 |  | Winergy
Bethel | 109 | 23157231 |  | Winergy
Bethel | 110 | 23160750 | NTN | Nanjing
Bethel | 111 | 23160751 | NTN | Winergy
Bethel | 112 | 23160752 | NTN | Winergy
Bethel | 113 | 23160753 | NTN | Winergy
Bethel | 114 | 23160754 | Koyo | Nanjing
Bethel | 115 | 23160755 | Koyo | Winergy
Bethel | 116 | 23160756 | NTN | Nanjing
Bethel | 117 | 23160757 | NTN | Winergy
Bethel | 118 | 23160758 | Koyo | Nanjing
Bethel | 119 | 23160759 | FAG | Nanjing
Bethel | 120 | 23160760 | NTN | Winergy
Roncevaux | 81 | 23160802 | SKF | Nanjing
Roncevaux | 82 | 23160803 | SKF | Nanjing
Roncevaux | 83 | 23160804 | SKF | Nanjing
Roncevaux | 84 | 23160805 | NTN | Nanjing
Roncevaux | 85 | 23160806 | NTN | Nanjing
Roncevaux | 86 | 23160807 | NTN | Nanjing
Roncevaux | 87 | 23160808 | Koyo | Nanjing
Roncevaux | 88 | 23160809 | Koyo | Nanjing
Roncevaux | 89 | 23160810 | SKF | Nanjing
Roncevaux | 90 | 23160811 | Koyo | Nanjing
Roncevaux | 91 | 23160812 | Koyo | Nanjing
Roncevaux | 92 | 23160813 | Koyo | Nanjing
Roncevaux | 93 | 23160814 | NTN | Nanjing
Roncevaux | 95 | 23160815 | NTN | Nanjing
Roncevaux | 94 | 23160816 | Koyo | Nanjing
Roncevaux | 96 | 23160817 | NTN | Nanjing
Roncevaux | 97 | 23160818 | SKF | Nanjing
Roncevaux | 98 | 23160819 | NTN | Nanjing
Roncevaux | 99 | 23160820 | SKF | Nanjing
Roncevaux | 100 | 23160821 | SKF | Nanjing
Roncevaux | 101 | 23160822 | Koyo | Nanjing
Roncevaux | 102 | 23160823 | Koyo | Nanjing
Roncevaux | 103 | 23160824 | Koyo | Nanjing
Roncevaux | 104 | 23160825 | Koyo | Nanjing
Roncevaux | 105 | 23160826 | Koyo | Winergy
Roncevaux | 106 | 23160827 | NTN | Nanjing
Roncevaux | 107 | 23160828 | Koyo | Nanjing
Roncevaux | 108 | 23160829 | Koyo | Nanjing
Roncevaux | 109 | 23160830 | Koyo | Nanjing
Roncevaux | 110 | 23160831 | SKF | Nanjing
Roncevaux | 111 | 23160832 | Koyo | Nanjing
Roncevaux | 112 | 23160833 | Koyo | Nanjing
Roncevaux | 113 | 23160834 | SKF | Nanjing
Number Three | 103 | 23163781 | NTN | Nanjing
Number Three | 105 | 23163782 | NTN | Nanjing
Upland Prairie | 15 | 23163792 | SKF | Nanjing
Upland Prairie | 25 | 23163793 | SKF | Nanjing
Upland Prairie | 26 | 23163794 | SKF | Winergy
Upland Prairie | 27 | 23163795 | Koyo | Nanjing
Upland Prairie | 28 | 23163796 | Koyo | Winergy
Upland Prairie | 35 | 23163797 | NTN | Winergy
Upland Prairie | 37 | 23163798 | SKF | Nanjing
Upland Prairie | 48 | 23163799 | Koyo | Nanjing
Upland Prairie | 54 | 23163800 | SKF | Nanjing
Upland Prairie | 55 | 23163801 | Koyo | Winergy
Upland Prairie | 63 | 23163802 | Koyo | Nanjing
Upland Prairie | 82 | 23163803 | NTN | Nanjing
Upland Prairie | 86 | 23163804 | NTN | Winergy
Upland Prairie | 87 | 23163805 | Koyo | Nanjing
Upland Prairie | 88 | 23163806 | Koyo | Nanjing
Upland Prairie | 130 | 23163807 | Koyo | Nanjing
Kossuth | 34 | 23163826 | NTN | Nanjing
Kossuth | 44 | 23163827 | SKF | Nanjing
Kossuth | 56 | 23163828 | NTN | Nanjing
Kossuth | 57 | 23163829 | Koyo | Nanjing
Kossuth | 59 | 23163830 | SKF | Nanjing
Kossuth | 62 | 23163831 | NTN | Nanjing
Kossuth | 63 | 23163832 | NTN | Nanjing
Kossuth | 66 | 23164431 | NTN | Nanjing
Kossuth | 75 | 23164432 | NTN | Nanjing
Kossuth | 76 | 23164433 | Koyo | Nanjing
Kossuth | 77 | 23164434 | NTN | Nanjing
Bishop Hill III | 301 | 23165404 | NTN | Winergy
Bishop Hill III | 302 | 23165405 | NTN | Winergy
Thunderhead | 8 | 23165432 | NTN | Nanjing
Thunderhead | 31 | 23165433 | NTN | Nanjing
Thunderhead | 32 | 23165434 | NTN | Nanjing
Thunderhead | 58 | 23165435 | NTN | Nanjing
Thunderhead | 60 | 23165436 | NTN | Nanjing
Thunderhead | 61 | 23165437 | NTN | Nanjing
Thunderhead | 62 | 23165438 | NTN | Nanjing
Thunderhead | 63 | 23165439 | NTN | Nanjing
Thunderhead | 64 | 23165440 | NTN | Nanjing
Thunderhead | 65 | 23165441 | NTN | Nanjing
Blooming Grove | WTG-007 | 23165442 | NTN | Nanjing
Blooming Grove | WTG-008 | 23165443 | NTN | Nanjing
Blooming Grove | WTG-033 | 23165444 | NTN | Nanjing
Blooming Grove | WTG-020 | 23165445 | NTN | Nanjing
Blooming Grove | WTG-025 | 23165446 | NTN | Winergy
Blooming Grove | WTG-016 | 23165447 | NTN | Nanjing
Blooming Grove | WTG-036 | 23165448 | NTN | Nanjing
Blooming Grove | WTG-068 | 23165449 | NTN | Nanjing
Sundance | 66 | 23165456 | NTN | Nanjing
Sundance | 67 | 23165457 | NTN | Nanjing
Sundance | 68 | 23165458 | NTN | Nanjing
Sundance | 69 | 23165459 | NTN | Nanjing
Sundance | 70 | 23165460 | NTN | Nanjing
Sundance | 71 | 23165461 | NTN | Nanjing
Sundance | 72 | 23165462 | NTN | Nanjing
Number Three | 104 | 23165463 | NTN | Pending Repair Report
Number Three | 102 | 23165464 | NTN | Nanjing
Number Three | 101 | 23165465 | NTN | Nanjing
Deuel Harvest | 7 | 23165467 | NTN | Winergy
Deuel Harvest | 13 | 23165468 | NTN | Nanjing
Deuel Harvest | 21 | 23165469 | NTN | Nanjing
Deuel Harvest | 73 | 23165470 | NTN | Winergy
Deuel Harvest | 75 | 23165471 | NTN | Winergy
Deuel Harvest | 76 | 23165472 | NTN | Winergy
Deuel Harvest | 77 | 23165473 | NTN | Nanjing
Deuel Harvest | 93 | 23165474 | NTN | Nanjing
Deuel Harvest | 96 | 23165475 | NTN | Nanjing
Deuel Harvest | 98 | 23165476 | NTN | Nanjing
Deuel Harvest | 99 | 23165477 | NTN | Nanjing
Deuel Harvest | 109 | 23165478 | NTN | Nanjing
Plymouth | 24 | 23165485 | NTN | Winergy
Plymouth | 26 | 23165486 | NTN | Nanjing
Plymouth | 81 | 23165487 | NTN | Nanjing
Plymouth | 93 | 23165488 | NTN | Nanjing
Plymouth | 97 | 23165489 | NTN | Winergy
Plymouth | 100 | 23165490 | NTN | Nanjing
Golden Plains | 1 | 23167783 | NTN | Winergy
Golden Plains | 16 | 23167784 | NTN | Winergy
Golden Plains | 19 | 23167785 | NTN | Winergy
Golden Plains | 20 | 23167786 | NTN | Winergy
Golden Plains | 21 | 23167787 | NTN | Winergy
Golden Plains | 23 | 23167788 | NTN | Winergy
Golden Plains | 27 | 23167789 | NTN | Winergy
Golden Plains | 30 | 23167790 | NTN | Winergy
Golden Plains | 36 | 23167791 | NTN | Winergy
Golden Plains | 38 | 23167792 | Koyo | Winergy
Golden Plains | 39 | 23167793 | NTN | Winergy
Golden Plains | 43 | 23167794 | NTN | Winergy
Golden Plains | 44 | 23167795 | NTN | Winergy
Golden Plains | 47 | 23167796 | NTN | Winergy
Golden Plains | 52 | 23167797 | Koyo | Winergy
Golden Plains | 53 | 23167798 | NTN | Winergy
Golden Plains | 56 | 23167799 | NTN | Winergy
Golden Plains | 57 | 23167815 | NTN | Winergy
Golden Plains | 58 | 23167816 | NTN | Winergy
Golden Plains | 59 | 23167817 | Koyo | Nanjing
Golden Plains | 60 | 23167823 | Koyo | Nanjing
Golden Plains | 61 | 23167824 | Koyo | Nanjing
Golden Plains | 62 | 23167825 | NTN | Winergy
Golden Plains | 63 | 23167826 | NTN | Winergy
Golden Plains | 64 | 23167827 | NTN | Winergy
Golden Plains | 67 | 23167828 | NTN | Winergy
Golden Plains | 69 | 23167829 | SKF | Winergy
Golden Plains | 72 | 23167830 | NTN | Nanjing
Golden Plains | 73 | 23167831 | Koyo | Winergy
Golden Plains | 80 | 23167832 | NTN | Winergy
Golden Plains | 81 | 23167833 | NTN | Winergy
Whispering Willow North | 409 | 23167834 | NTN | Winergy
Whispering Willow North | 415 | 23167835 | Koyo | Winergy
Whispering Willow North | 421 | 23167836 | NTN | Winergy
Whispering Willow North | 425 | 23167837 | SKF | Winergy
Whispering Willow North | 426 | 23167838 | NTN | Winergy
Whispering Willow North | 427 | 23167839 | NTN | Nanjing
Whispering Willow North | 431 | 23167840 | NTN | Winergy
Whispering Willow North | 440 | 23167841 | SKF | Winergy
Whispering Willow North | 446 | 23167842 | NTN | Winergy
Whispering Willow North | 449 | 23167843 | Koyo | Nanjing
Whispering Willow North | 456 | 23167844 | NTN | Nanjing
Whispering Willow North | 470 | 23167845 | NTN | Winergy
Whispering Willow North | 481 | 23167846 | SKF | Winergy
Richland | 30 | 23167847 | SKF | Nanjing
Richland | 40 | 23167848 | Koyo | Winergy
Richland | 41 | 23167849 | SKF | Nanjing
Richland | 42 | 23167850 | SKF | Nanjing
Richland | 50 | 23167851 | SKF | Nanjing
Richland | 52 | 23167852 | SKF | Nanjing
Richland | 56 | 23167853 | SKF | Nanjing
Richland | 59 | 23167854 | SKF | Winergy
Richland | 71 | 23167855 | Koyo | Winergy
Richland | 73 | 23167856 | Koyo | Winergy
Richland | 76 | 23167857 | NTN | Nanjing
Richland | 80 | 23167858 | SKF | Nanjing
Tatanka Ridge | E01 | 23168156 | SKF | Nanjing
Tatanka Ridge | E03 | 23168157 | SKF | Nanjing
Tatanka Ridge | G01 | 23168172 | SKF | Nanjing
Tatanka Ridge | G02 | 23168173 | SKF | Nanjing
Tatanka Ridge | G03 | 23168174 | SKF | Winergy
Tatanka Ridge | P03 | 23168175 | NTN | Nanjing
Coyote Ridge | C2 | 23168176 | NTN | Replacement Pending
Coyote Ridge | D2 | 23168177 | SKF | Nanjing
Coyote Ridge | D3 | 23168178 | SKF | Nanjing
Coyote Ridge | D11 | 23168179 | SKF | Nanjing
English Farms | 31 | 23183260 | SKF | Nanjing
English Farms | 29 | 23183261 | NTN | Winergy
English Farms | 19 | 23183262 | Koyo | Winergy
English Farms | 44 | 23183263 | Koyo | Nanjing
English Farms | 42 | 23183264 | Koyo | Winergy
English Farms | 63 | 23183265 | SKF | Winergy
English Farms | 73 | 23183266 | FAG | Winergy
English Farms | 71 | 23183267 | Koyo | Nanjing
English Farms | 83 | 23183268 | SKF | Nanjing
English Farms | 84 | 23183269 | NTN | Nanjing
English Farms | 37 | 23183270 | Koyo | Winergy
Darlowo I | D12 | 25110007 | Koyo | Winergy
Darlowo I | B19 | 25110008 | Koyo | Winergy
Darlowo I | B21 | 25110009 | Koyo | Winergy
Darlowo I | W12 | 25110010 | Koyo | Eickhoff
Darlowo I | D01 | 25110011 | Koyo | Eickhoff
Darlowo I | D02 | 25110012 | Koyo | Winergy
Darlowo I | D04 | 25110013 | Koyo | Winergy
Darlowo I | D03 | 25110014 | Koyo | Winergy
Darlowo I | D06 | 25110015 | Koyo | Winergy
Darlowo I | D07 | 25110016 | Koyo | Eickhoff
Darlowo I | D08 | 25110017 | Koyo | Winergy
Darlowo I | D09 | 25110018 | Koyo | Winergy
Darlowo I | D10 | 25110019 | Koyo | Eickhoff
Darlowo I | D05 | 25110020 | Koyo | Eickhoff
Darlowo I | W04 | 25110021 | Koyo | Winergy
Darlowo I | W07 | 25110022 | Koyo | Winergy
Darlowo I | W08 | 25110023 | Koyo | Winergy
Darlowo I | W01 | 25110024 | Koyo | Eickhoff
Darlowo I | W02 | 25110025 | Koyo | Rexroth
Darlowo I | W03 | 25110026 | Koyo | Winergy
Darlowo I | W05 | 25110027 | Koyo | Winergy
Darlowo I | W06 | 25110028 | Koyo | Winergy
Darlowo I | J01 | 25110040 | Koyo | Eickhoff
Darlowo I | J02 | 25110041 | Koyo | Eickhoff
Darlowo I | J04 | 25110042 | Koyo | Winergy
Darlowo I | J05 | 25110043 | Koyo | Eickhoff
Darlowo I | J06 | 25110044 | Koyo | Eickhoff
Darlowo I | J08 | 25110045 | Koyo | Eickhoff
Darlowo I | J09 | 25110046 | Koyo | Eickhoff
Darlowo I | J10 | 25110047 | Koyo | Winergy
Darlowo I | J03 | 25110048 | Koyo | Winergy
Darlowo I | J07 | 25110049 | Koyo | Eickhoff
Upstream | 1 | 25172993 | SKF | Nanjing
Upstream | 2 | 25172994 | SKF | ZF
Upstream | 3 | 25172995 | SKF | ZF
Upstream | 4 | 25172996 | Koyo | ZF
Upstream | 5 | 25172997 | SKF | ZF
Upstream | 6 | 25172998 | SKF | ZF
Upstream | 7 | 25172999 | NTN | ZF
Upstream | 8 | 25173000 | NTN | Winergy
Upstream | 9 | 25173001 | SKF | Winergy
Upstream | 10 | 25173002 | SKF | Nanjing
Upstream | 11 | 25173003 | SKF | Nanjing
Upstream | 12 | 25173004 | SKF | Nanjing
Upstream | 13 | 25173005 | SKF | ZF
Upstream | 14 | 25173006 | NTN | Winergy
Upstream | 15 | 25173007 | SKF | ZF
Upstream | 16 | 25173008 | SKF | ZF
Upstream | 17 | 25173009 | SKF | Nanjing
Upstream | 18 | 25173010 | SKF | Winergy
Upstream | 19 | 25173011 | SKF | Winergy
Upstream | 20 | 25173012 | NTN | Winergy
Upstream | 21 | 25173013 | SKF | Winergy
Upstream | 22 | 25173014 | SKF | Nanjing
Upstream | 23 | 25173015 | SKF | Nanjing
Upstream | 24 | 25173016 | SKF | ZF
Upstream | 25 | 25173017 | SKF | Winergy
Upstream | 26 | 25173018 | SKF | Winergy
Upstream | 27 | 25173019 | SKF | Replacement Pending
Upstream | 28 | 25173020 | SKF | Nanjing
Upstream | 29 | 25173021 | SKF | Nanjing
Upstream | 30 | 25173022 | SKF | Replacement Pending
Upstream | 31 | 25173023 | SKF | ZF
Upstream | 32 | 25173024 | NTN | ZF
Upstream | 33 | 25173025 | SKF | Winergy
Upstream | 34 | 25173026 | SKF | Replacement Pending
Upstream | 35 | 25173027 | SKF | Nanjing
Upstream | 36 | 25173028 | SKF | ZF
Upstream | 37 | 25173029 | SKF | Winergy
Upstream | 38 | 25173030 | SKF | Nanjing
Upstream | 39 | 25173031 | SKF | ZF
Upstream | 40 | 25173032 | NTN | ZF
Upstream | 41 | 25173033 | SKF | Nanjing
Upstream | 42 | 25173034 | FAG | Winergy
Upstream | 43 | 25173035 | SKF | ZF
Upstream | 44 | 25173036 | SKF | Winergy
Upstream | 45 | 25173037 | SKF | Nanjing
Upstream | 46 | 25173038 | SKF | Nanjing
Upstream | 47 | 25173039 | SKF | Nanjing
Upstream | 48 | 25173040 | SKF | Winergy
Upstream | 49 | 25173041 | SKF | Winergy
Upstream | 50 | 25173042 | SKF | Nanjing
Upstream | 51 | 25173043 | SKF | Winergy
Upstream | 52 | 25173044 | SKF | ZF
Upstream | 53 | 25173045 | SKF | Nanjing
Upstream | 54 | 25173046 | SKF | Winergy
Upstream | 55 | 25173047 | SKF | Nanjing
Upstream | 56 | 25173048 | SKF | Winergy
Upstream | 82 | 25173049 | NTN | ZF
Upstream | 57 | 25173049 | SKF | ZF
Upstream | 82 | 25173049 | NTN | ZF
Upstream | 57 | 25173049 | SKF | ZF
Upstream | 58 | 25173050 | NTN | Nanjing
Upstream | 59 | 25173051 | NTN | Nanjing
Upstream | 60 | 25173052 | NTN | ZF
Upstream | 61 | 25173053 | NTN | Nanjing
Upstream | 62 | 25173054 | SKF | Winergy
Upstream | 63 | 25173055 | SKF | Nanjing
Upstream | 64 | 25173056 | SKF | Winergy
Upstream | 65 | 25173057 | SKF | Nanjing
Upstream | 66 | 25173058 | SKF | Nanjing
Upstream | 67 | 25173059 | SKF | ZF
Upstream | 68 | 25173060 | SKF | Winergy
Upstream | 70 | 25173062 | NTN | Winergy
Upstream | 71 | 25173063 | SKF | Winergy
Upstream | 72 | 25173064 | SKF | Nanjing
Upstream | 73 | 25173065 | SKF | Nanjing
Upstream | 74 | 25173066 | SKF | Nanjing
Upstream | 75 | 25173067 | NTN | Replacement Pending
Upstream | 76 | 25173068 | SKF | Nanjing
Upstream | 77 | 25173069 | NTN | Nanjing
Upstream | 78 | 25173070 | SKF | Winergy
Upstream | 79 | 25173071 | SKF | ZF
Upstream | 80 | 25173072 | SKF | Nanjing
Upstream | 81 | 25173073 | NTN | ZF
Bishop Hill III | 303 | 25174726 | Koyo | Nanjing
Bishop Hill III | 304 | 25174727 | FAG | Nanjing
Bishop Hill III | 305 | 25174728 | Koyo | ZF
Bishop Hill III | 306 | 25174729 | Koyo | Winergy
Bishop Hill III | 307 | 25174730 | Koyo | Nanjing
Bishop Hill III | 308 | 25174731 | Koyo | Nanjing
Bishop Hill III | 309 | 25174732 | Koyo | Replacement Pending
Bishop Hill III | 310 | 25174733 | Koyo | Nanjing
Bishop Hill III | 311 | 25174734 | Koyo | ZF
Bishop Hill III | 312 | 25174735 | Koyo | ZF
Bishop Hill III | 313 | 25174736 | Koyo | Nanjing
Bishop Hill III | 314 | 25174737 | Koyo | Replacement Pending
Bishop Hill III | 315 | 25174738 | NSK | ZF
Bishop Hill III | 316 | 25174739 | Koyo | Nanjing
Bishop Hill III | 317 | 25174740 | Koyo | Nanjing
Bishop Hill III | 318 | 25174741 | Koyo | Nanjing
Bishop Hill III | 319 | 25174742 | SKF | Winergy
Bishop Hill III | 320 | 25174743 | SKF | Winergy
Bishop Hill III | 321 | 25174744 | Koyo | Nanjing
Bishop Hill III | 322 | 25174745 | SKF | Winergy
Bishop Hill III | 323 | 25174746 | SKF | Winergy
Bishop Hill III | 324 | 25174747 | NSK | ZF
Bishop Hill III | 325 | 25174748 | SKF | Winergy
Bishop Hill III | 326 | 25174749 | SKF | Winergy
Bishop Hill III | 327 | 25174750 | SKF | Winergy
Bishop Hill III | 328 | 25174751 | SKF | ZF
Bishop Hill III | 329 | 25174752 | SKF | Winergy
Bishop Hill III | 330 | 25174753 | SKF | Winergy
Bishop Hill III | 331 | 25174754 | SKF | Winergy
Bishop Hill III | 332 | 25174755 | Koyo | Nanjing
Bishop Hill III | 333 | 25174756 | SKF | Winergy
Bishop Hill III | 334 | 25174757 | Koyo | ZF
Bishop Hill III | 335 | 25174758 | Koyo | Nanjing
Bishop Hill III | 336 | 25174759 | Koyo | Nanjing
Bishop Hill III | 337 | 25174760 | Koyo | Replacement Pending
Bishop Hill III | 338 | 25174761 | Koyo | Replacement Pending
Bishop Hill III | 339 | 25174762 | Koyo | Nanjing
Bishop Hill III | 340 | 25174763 | FAG | Nanjing
Bishop Hill III | 341 | 25174764 | SKF | Winergy
Bishop Hill III | 342 | 25174765 | SKF | Nanjing
Bishop Hill III | 343 | 25174766 | NTN | Winergy
Bishop Hill III | 344 | 25174767 | SKF | Winergy
Bishop Hill III | 345 | 25174768 | SKF | Winergy
Bishop Hill III | 346 | 25174769 | NTN | Nanjing
Bishop Hill III | 347 | 25174770 | Koyo | Nanjing
Bishop Hill III | 348 | 25174771 | SKF | Winergy
Bishop Hill III | 349 | 25174772 | SKF | Winergy
Bishop Hill III | 350 | 25174773 | SKF | Winergy
Bishop Hill III | 351 | 25174774 | Koyo | Nanjing
Bishop Hill III | 352 | 25174775 | SKF | Winergy
Bishop Hill III | 353 | 25174776 | Koyo | ZF
Traverse III | 3004 | 25176063 | NTN | Winergy
Traverse III | 3044 | 25176064 | NTN | Winergy
Traverse III | 3045 | 25176065 | NTN | Nanjing
Traverse III | 3047 | 25176066 | NTN | Winergy
Traverse III | 3050 | 25176067 | NTN | Winergy
Traverse III | 3052 | 25176068 | NTN | Winergy
Traverse III | 3053 | 25176069 | NTN | Nanjing
Traverse III | 3054 | 25176070 | NTN | Nanjing
Traverse III | 3056 | 25176071 | NTN | Nanjing
Traverse III | 3057 | 25176072 | NTN | Winergy
Traverse III | 3061 | 25176073 | NTN | Winergy
Traverse III | 3063 | 25176074 | NTN | Winergy
Traverse III | 3064 | 25176075 | NTN | Winergy
Traverse III | 3065 | 25176076 | NTN | Nanjing
Traverse III | 3066 | 25176077 | NTN | Winergy
Traverse III | 3067 | 25176078 | NTN | Winergy
Traverse III | 3068 | 25176079 | NTN | Winergy
Traverse III | 3070 | 25176080 | NTN | Winergy
Traverse III | 3071 | 25176081 | NTN | Winergy
Traverse III | 3072 | 25176082 | NTN | Winergy
Upstream | 69 | 25176139 | NTN | Winergy
Red Barn | 2 | 25176343 | NTN | WINERGY
Red Barn | 7 | 25176344 | NTN | WINERGY
Red Barn | 8 | 25176345 | NTN | Nanjing
Red Barn | 24 | 25176346 | NTN | WINERGY
Upland Prairie | 1 | 25180505 | NTN | Nanjing
Upland Prairie | 2 | 25180506 | NTN | Nanjing
Upland Prairie | 3 | 25180507 | SKF | Nanjing
Upland Prairie | 4 | 25180508 | SKF | Nanjing
Upland Prairie | 5 | 25180509 | NTN | Winergy
Upland Prairie | 7 | 25180510 | NTN | ZF
Upland Prairie | 8 | 25180511 | NTN | Nanjing
Upland Prairie | 9 | 25180512 | NTN | Nanjing
Upland Prairie | 10 | 25180513 | NTN | Winergy
Upland Prairie | 11 | 25180514 | NTN | Winergy
Upland Prairie | 12 | 25180515 | NTN | Nanjing
Upland Prairie | 13 | 25180516 | NTN | Winergy
Upland Prairie | 14 | 25180517 | NTN | Winergy
Upland Prairie | 16 | 25180518 | NTN | ZF
Upland Prairie | 17 | 25180519 | NTN | ZF
Upland Prairie | 18 | 25180520 | NTN | Winergy
Upland Prairie | 20 | 25180521 | NTN | ZF
Upland Prairie | 21 | 25180522 | NTN | Nanjing
Upland Prairie | 22 | 25180523 | NTN | ZF
Upland Prairie | 23 | 25180524 | NTN | ZF
Upland Prairie | 24 | 25180525 | NTN | Nanjing
Upland Prairie | 29 | 25180526 | SKF | Nanjing
Upland Prairie | 30 | 25180527 | SKF | Nanjing
Upland Prairie | 32 | 25180528 | NTN | ZF
Upland Prairie | 33 | 25180529 | NTN | Nanjing
Upland Prairie | 34 | 25180530 | NTN | ZF
Upland Prairie | 38 | 25180531 | NTN | Nanjing
Upland Prairie | 39 | 25180532 | NTN | Winergy
Upland Prairie | 40 | 25180533 | NTN | ZF
Upland Prairie | 41 | 25180534 | NTN | ZF
Upland Prairie | 42 | 25180535 |  | Winergy
Upland Prairie | 43 | 25180536 | NTN | Nanjing
Upland Prairie | 44 | 25180537 | NTN | Nanjing
Upland Prairie | 45 | 25180538 | NTN | Nanjing
Upland Prairie | 46 | 25180539 | NTN | Nanjing
Upland Prairie | 47 | 25180540 | NTN | ZF
Upland Prairie | 49 | 25180541 | SKF | Winergy
Upland Prairie | 51 | 25180542 | NTN | ZF
Upland Prairie | 52 | 25180543 | NTN | ZF
Upland Prairie | 53 | 25180544 | NTN | Nanjing
Upland Prairie | 56 | 25180545 | SKF | ZF
Upland Prairie | 57 | 25180546 | NTN | Nanjing
Upland Prairie | 58 | 25180547 | NTN | ZF
Upland Prairie | 59 | 25180548 | NTN | Nanjing
Upland Prairie | 60 | 25180549 | NTN | Nanjing
Upland Prairie | 61 | 25180550 | NTN | Nanjing
Upland Prairie | 62 | 25180551 | NTN | Nanjing
Upland Prairie | 64 | 25180552 | NTN | Nanjing
Upland Prairie | 65 | 25180553 | NTN | Nanjing
Upland Prairie | 67 | 25180554 | NTN | Nanjing
Upland Prairie | 68 | 25180555 | NTN | Nanjing
Upland Prairie | 71 | 25180556 | NTN | Nanjing
Upland Prairie | 72 | 25180557 | SKF | Nanjing
Upland Prairie | 73 | 25180558 | NTN | Nanjing
Upland Prairie | 75 | 25180559 | NTN | Nanjing
Upland Prairie | 76 | 25180560 | NTN | Winergy
Upland Prairie | 77 | 25180561 | NTN | Nanjing
Upland Prairie | 78 | 25180562 | SKF | Nanjing
Upland Prairie | 79 | 25180563 | SKF | Nanjing
Upland Prairie | 80 | 25180564 | NTN | Nanjing
Upland Prairie | 81 | 25180565 | NTN | Nanjing
Upland Prairie | 83 | 25180566 | SKF | Nanjing
Upland Prairie | 84 | 25180567 | NTN | Nanjing
Upland Prairie | 85 | 25180568 | NTN | Nanjing
Upland Prairie | 89 | 25180569 | SKF | Nanjing
Upland Prairie | 90 | 25180570 | SKF | Nanjing
Upland Prairie | 91 | 25180571 | SKF | Nanjing
Upland Prairie | 92 | 25180572 | NTN | Nanjing
Upland Prairie | 93 | 25180573 | NTN | Nanjing
Upland Prairie | 94 | 25180574 | SKF | Winergy
Upland Prairie | 95 | 25180575 | SKF | Winergy
Upland Prairie | 96 | 25180576 | NTN | Nanjing
Upland Prairie | 97 | 25180577 | NTN | Nanjing
Upland Prairie | 98 | 25180578 | SKF | Winergy
Upland Prairie | 99 | 25180579 | NTN | Nanjing
Upland Prairie | 100 | 25180580 | NTN | Winergy
Upland Prairie | 101 | 25180581 | SKF | Nanjing
Upland Prairie | 103 | 25180582 | SKF | Winergy
Upland Prairie | 104 | 25180583 | SKF | Winergy
Upland Prairie | 105 | 25180584 | NTN | Nanjing
Upland Prairie | 107 | 25180585 | NTN | Nanjing
Upland Prairie | 108 | 25180586 | SKF | Winergy
Upland Prairie | 109 | 25180587 | NTN | Nanjing
Upland Prairie | 110 | 25180588 | NTN | Nanjing
Upland Prairie | 112 | 25180589 | NTN | Winergy
Upland Prairie | 113 | 25180590 | NTN | ZF
Upland Prairie | 114 | 25180591 | NTN | Nanjing
Upland Prairie | 115 | 25180592 | NTN | Winergy
Upland Prairie | 116 | 25180593 | NTN | Nanjing
Upland Prairie | 117 | 25180594 | NTN | Nanjing
Upland Prairie | 118 | 25180595 | SKF | Nanjing
Upland Prairie | 119 | 25180596 | SKF | Nanjing
Upland Prairie | 120 | 25180597 | NTN | Nanjing
Upland Prairie | 121 | 25180598 | NTN | Nanjing
Upland Prairie | 122 | 25180599 | NTN | ZF
Upland Prairie | 124 | 25180600 | NTN | Nanjing
Upland Prairie | 125 | 25180601 | NTN | Winergy
Upland Prairie | 126 | 25180602 | NTN | Nanjing
Upland Prairie | 127 | 25180603 | NTN | Nanjing
Upland Prairie | 128 | 25180604 | NTN | Nanjing
Upland Prairie | 129 | 25180605 | NTN | ZF
Upland Prairie | 131 | 25180606 | NTN | Nanjing
Upland Prairie | 132 | 25180607 | NTN | Nanjing
Upland Prairie | 133 | 25180608 | NTN | Nanjing
Upland Prairie | 134 | 25180609 | NTN | Nanjing
Maverick | 18 | 25180617 | NTN | Winergy
Maverick | 19 | 25180618 | NTN | Winergy
Maverick | 38 | 25180619 | NTN | Winergy
Maverick | 39 | 25180620 | NTN | Winergy
Maverick | 40 | 25180621 | NTN | Winergy
Maverick | 76 | 25180622 | NTN | Winergy
English Farms | 36 | 25183202 | NTN | Nanjing
English Farms | 90 | 25183203 | NTN | Nanjing
English Farms | 89 | 25183204 | NTN | Nanjing
English Farms | 14 | 25183205 | SKF | Winergy
English Farms | 15 | 25183206 | SKF | Winergy
English Farms | 4 | 25183207 | SKF | ZF
English Farms | 2 | 25183208 | SKF | ZF
English Farms | 6 | 25183209 | SKF | Nanjing
English Farms | 3 | 25183210 | SKF | Nanjing
English Farms | 9 | 25183211 | SKF | Nanjing
English Farms | 8 | 25183212 | SKF | Nanjing
English Farms | 32 | 25183213 | SKF | Nanjing
English Farms | 28 | 25183214 | NTN | Nanjing
English Farms | 11 | 25183215 | SKF | Winergy
English Farms | 13 | 25183216 | SKF | Winergy
English Farms | 27 | 25183217 | NTN | Winergy
English Farms | 10 | 25183218 | SKF | Winergy
English Farms | 23 | 25183219 | SKF | Winergy
English Farms | 22 | 25183220 | SKF | Nanjing
English Farms | 39 | 25183221 | SKF | Winergy
English Farms | 25 | 25183222 | SKF | Nanjing
English Farms | 41 | 25183223 | NTN | Nanjing
English Farms | 35 | 25183224 | SKF | Nanjing
English Farms | 40 | 25183225 | SKF | ZF
English Farms | 33 | 25183226 |  | Winergy
English Farms | 34 | 25183227 | SKF | ZF
English Farms | 45 | 25183228 | NTN | ZF
English Farms | 48 | 25183229 | SKF | ZF
English Farms | 49 | 25183230 | NTN | Nanjing
English Farms | 47 | 25183231 | SKF | Winergy
English Farms | 66 | 25183232 | NTN | Winergy
English Farms | 50 | 25183233 | SKF | ZF
English Farms | 67 | 25183234 | SKF | Nanjing
English Farms | 65 | 25183235 | NTN | Winergy
English Farms | 64 | 25183236 | SKF | ZF
English Farms | 60 | 25183237 | SKF | Winergy
English Farms | 52 | 25183238 | SKF | ZF
English Farms | 62 | 25183239 | SKF | Nanjing
English Farms | 55 | 25183240 | SKF | ZF
English Farms | 59 | 25183241 | SKF | Nanjing
English Farms | 54 | 25183242 | SKF | ZF
English Farms | 57 | 25183243 | SKF | ZF
English Farms | 56 | 25183244 | NTN | Nanjing
English Farms | 74 | 25183245 | SKF | Winergy
English Farms | 69 | 25183246 | SKF | Nanjing
English Farms | 88 | 25183247 | NTN | Nanjing
English Farms | 70 | 25183248 | NTN | Nanjing
English Farms | 82 | 25183249 | NTN | Winergy
English Farms | 80 | 25183250 | NTN | Nanjing
English Farms | 92 | 25183251 | NTN | Nanjing
English Farms | 87 | 25183252 | NTN | Nanjing
English Farms | 81 | 25183253 | NTN | Nanjing
English Farms | 79 | 25183254 | NTN | Nanjing
English Farms | 85 | 25183255 | NTN | Nanjing
English Farms | 77 | 25183256 | NTN | Nanjing
English Farms | 75 | 25183257 | NTN | Nanjing
English Farms | 76 | 25183258 |  | Winergy
English Farms | 91 | 25183259 | NTN | Nanjing
Santa Rita East | 1 | 25184058 | NTN | Winergy
Santa Rita East | 2 | 25184059 | NTN | ZF
Santa Rita East | 3 | 25184060 | NTN | Nanjing
Santa Rita East | 4 | 25184061 | NTN | Nanjing
Santa Rita East | 5 | 25184062 | NTN | Nanjing
Santa Rita East | 6 | 25184063 | NTN | Nanjing
Santa Rita East | 7 | 25184064 | FAG | Nanjing
Santa Rita East | 8 | 25184065 | FAG | Winergy
Santa Rita East | 9 | 25184066 | NTN | ZF
Santa Rita East | 10 | 25184067 | NTN | Nanjing
Santa Rita East | 11 | 25184068 | NTN | Nanjing
Santa Rita East | 12 | 25184069 | NTN | Winergy
Santa Rita East | 13 | 25184070 | NTN | Winergy
Santa Rita East | 14 | 25184071 | Timken | Nanjing
Santa Rita East | 15 | 25184072 | NTN | Nanjing
Santa Rita East | 16 | 25184073 | NTN | Nanjing
Santa Rita East | 17 | 25184074 | NTN | ZF
Santa Rita East | 18 | 25184075 | NTN | Nanjing
Santa Rita East | 19 | 25184076 | NTN
Santa Rita East | 20 | 25184077 | Timken | Winergy
Santa Rita East | 21 | 25184078 | FAG | ZF
Santa Rita East | 22 | 25184079 | NTN | Nanjing
Santa Rita East | 23 | 25184080 | NTN | Winergy
Santa Rita East | 24 | 25184081 | NTN | Winergy
Santa Rita East | 25 | 25184082 | NTN | Nanjing
Santa Rita East | 26 | 25184083 | NTN | Nanjing
Santa Rita East | 27 | 25184084 | FAG | Winergy
Santa Rita East | 28 | 25184085 | Timken | Nanjing
Santa Rita East | 29 | 25184086 | Timken | Nanjing
Santa Rita East | 30 | 25184087 | NTN | Nanjing
Santa Rita East | 31 | 25184088 | NTN | ZF
Santa Rita East | 32 | 25184089 | NTN | ZF
Santa Rita East | 33 | 25184090 | NTN | Winergy
Santa Rita East | 34 | 25184091 | FAG | Winergy
Santa Rita East | 35 | 25184092 | NTN | Nanjing
Santa Rita East | 36 | 25184093 | NTN | Nanjing
Santa Rita East | 37 | 25184094 | FAG | Winergy
Santa Rita East | 38 | 25184095 | NTN | Nanjing
Santa Rita East | 39 | 25184096 | NTN | Winergy
Santa Rita East | 40 | 25184097 | FAG | ZF
Santa Rita East | 41 | 25184098 | NTN | Nanjing
Santa Rita East | 42 | 25184099 | FAG | Winergy
Santa Rita East | 43 | 25184100 | NTN | Nanjing
Santa Rita East | 44 | 25184101 | FAG | ZF
Santa Rita East | 45 | 25184102 | NTN | Nanjing
Santa Rita East | 46 | 25184103 | FAG | ZF
Santa Rita East | 47 | 25184104 | NTN | Winergy
Santa Rita East | 48 | 25184105 | FAG | ZF
Santa Rita East | 49 | 25184106 | FAG | ZF
Santa Rita East | 50 | 25184107 | FAG | ZF
Santa Rita East | 51 | 25184108 | NTN | Nanjing
Santa Rita East | 52 | 25184109 | NTN | ZF
Santa Rita East | 53 | 25184110 | NTN | Winergy
Santa Rita East | 54 | 25184111 | NTN | ZF
Santa Rita East | 55 | 25184112 | NTN | Nanjing
Santa Rita East | 56 | 25184113 | NSK | Winergy
Santa Rita East | 57 | 25184114 | FAG | ZF
Santa Rita East | 58 | 25184115 | NTN | Nanjing
Santa Rita East | 59 | 25184116 | FAG | ZF
Santa Rita East | 60 | 25184117 | NTN | Winergy
Santa Rita East | 61 | 25184118 | FAG | Nanjing
Santa Rita East | 62 | 25184119 | NTN | Winergy
Santa Rita East | 63 | 25184120 | Timken | Nanjing
Santa Rita East | 64 | 25184121 | FAG | Winergy
Santa Rita East | 65 | 25184122 | FAG | ZF
Santa Rita East | 66 | 25184123 | FAG | ZF
Santa Rita East | 67 | 25184124 | FAG | ZF
Santa Rita East | 68 | 25184125 | NTN | Winergy
Santa Rita East | 69 | 25184126 | FAG | ZF
Santa Rita East | 70 | 25184127 | FAG | Winergy
Santa Rita East | 71 | 25184128 | FAG | ZF
Santa Rita East | 72 | 25184129 | FAG | ZF
Santa Rita East | 73 | 25184130 | FAG | ZF
Santa Rita East | 74 | 25184131 | NSK | ZF
Santa Rita East | 75 | 25184132 | NSK | Nanjing
Santa Rita East | 76 | 25184133 | FAG | Nanjing
Santa Rita East | 77 | 25184134 | Timken | ZF
Santa Rita East | 78 | 25184135 | FAG | Winergy
Santa Rita East | 79 | 25184136 | FAG | Nanjing
Santa Rita East | 80 | 25184137 | FAG | Nanjing
Santa Rita East | 81 | 25184138 | NTN | Winergy
Santa Rita East | 82 | 25184139 | FAG | ZF
Santa Rita East | 83 | 25184140 | FAG | ZF
Santa Rita East | 84 | 25184141 | FAG | Nanjing
Santa Rita East | 85 | 25184142 | FAG | Winergy
Santa Rita East | 86 | 25184143 | NTN | ZF
Santa Rita East | 87 | 25184144 | NTN | Nanjing
Santa Rita East | 88 | 25184145 |  | Nanjing
Santa Rita East | 89 | 25184146 | NTN | Winergy
Santa Rita East | 90 | 25184147 | Timken | Winergy
Santa Rita East | 91 | 25184148 | FAG | ZF
Santa Rita East | 92 | 25184149 | FAG | Nanjing
Santa Rita East | 93 | 25184150 | FAG | ZF
Santa Rita East | 94 | 25184151 | FAG | Nanjing
Santa Rita East | 95 | 25184152 | NTN | Winergy
Santa Rita East | 96 | 25184153 | Timken | Winergy
Santa Rita East | 97 | 25184154 | FAG | Winergy
Santa Rita East | 98 | 25184155 | NTN | ZF
Santa Rita East | 99 | 25184156 | NTN | Winergy
Santa Rita East | 100 | 25184157 | NTN | ZF
Santa Rita East | 101 | 25184158 | NTN | Winergy
Santa Rita East | 102 | 25184159 | NTN | Winergy
Santa Rita East | 103 | 25184160 | NTN | Winergy
Santa Rita East | 104 | 25184161 | NTN | ZF
Santa Rita East | 105 | 25184162 | NTN | ZF
Santa Rita East | 106 | 25184163 | NTN | Nanjing
Santa Rita East | 107 | 25184164 | FAG | Nanjing
Santa Rita East | 108 | 25184165 | FAG | ZF
Santa Rita East | 109 | 25184166 | FAG | Winergy
Santa Rita East | 110 | 25184167 | FAG | Nanjing
Santa Rita East | 111 | 25184168 | NTN | Winergy
Santa Rita East | 112 | 25184169 | NTN | Nanjing
Santa Rita East | 113 | 25184170 | NTN | ZF
Santa Rita East | 114 | 25184171 | NTN | Nanjing
Santa Rita East | 115 | 25184172 | NTN | Nanjing
Santa Rita East | 116 | 25184173 | NTN | Nanjing
Santa Rita East | 117 | 25184174 | FAG | Winergy
Santa Rita East | 118 | 25184175 | FAG | Winergy
Santa Rita East | 119 | 25184176 | NTN | Nanjing
Santa Rita East | 120 | 25184177 | NTN
Whispering Willow North | 401 | 25187560 | FAG | ZF
Whispering Willow North | 402 | 25187561 | SKF | Nanjing
Whispering Willow North | 403 | 25187562 | SKF | Nanjing
Whispering Willow North | 404 | 25187563 | FAG | Winergy
Whispering Willow North | 405 | 25187564 | FAG | Nanjing
Whispering Willow North | 406 | 25187565 | SKF | ZF
Whispering Willow North | 407 | 25187566 | FAG | Nanjing
Whispering Willow North | 408 | 25187567 | FAG | Nanjing
Whispering Willow North | 410 | 25187568 | FAG | Winergy
Whispering Willow North | 411 | 25187569 | FAG | Nanjing
Whispering Willow North | 412 | 25187570 | SKF | Nanjing
Whispering Willow North | 413 | 25187571 | NTN | Nanjing
Whispering Willow North | 414 | 25187572 | FAG | Nanjing
Whispering Willow North | 416 | 25187573 | SKF | Nanjing
Whispering Willow North | 417 | 25187574 | SKF | ZF
Whispering Willow North | 418 | 25187575 | SKF | ZF
Whispering Willow North | 419 | 25187576 | SKF | Winergy
Whispering Willow North | 420 | 25187577 | FAG | ZF
Whispering Willow North | 423 | 25187578 | FAG | ZF
Whispering Willow North | 424 | 25187579 | SKF | Nanjing
Whispering Willow North | 428 | 25187580 | SKF | Nanjing
Whispering Willow North | 429 | 25187581 | FAG | ZF
Whispering Willow North | 430 | 25187582 | SKF | Winergy
Whispering Willow North | 432 | 25187583 | SKF | ZF
Whispering Willow North | 433 | 25187584 | FAG | ZF
Whispering Willow North | 434 | 25187585 | FAG | Nanjing
Whispering Willow North | 435 | 25187586 | SKF | ZF
Whispering Willow North | 436 | 25187587 | SKF | ZF
Whispering Willow North | 437 | 25187588 | SKF | ZF
Whispering Willow North | 438 | 25187589 | SKF | ZF
Whispering Willow North | 441 | 25187590 | SKF | ZF
Whispering Willow North | 442 | 25187591 | FAG | Nanjing
Whispering Willow North | 443 | 25187592 | FAG | ZF
Whispering Willow North | 444 | 25187593 | SKF | Nanjing
Whispering Willow North | 445 | 25187594 | SKF | ZF
Whispering Willow North | 447 | 25187595 | FAG | ZF
Whispering Willow North | 448 | 25187596 | SKF | ZF
Whispering Willow North | 450 | 25187597 | FAG | Winergy
Whispering Willow North | 451 | 25187598 | FAG | ZF
Whispering Willow North | 452 | 25187599 | FAG | Winergy
Whispering Willow North | 453 | 25187600 | FAG | Nanjing
Whispering Willow North | 454 | 25187601 | FAG | ZF
Whispering Willow North | 455 | 25187602 | FAG | Nanjing
Whispering Willow North | 457 | 25187603 | FAG | ZF
Whispering Willow North | 458 | 25187604 | FAG | Winergy
Whispering Willow North | 459 | 25187605 | FAG | Nanjing
Whispering Willow North | 461 | 25187606 | FAG | Nanjing
Whispering Willow North | 462 | 25187607 | SKF | Nanjing
Whispering Willow North | 463 | 25187608 | SKF | Nanjing
Whispering Willow North | 464 | 25187609 | FAG | ZF
Whispering Willow North | 466 | 25187610 | SKF | ZF
Whispering Willow North | 467 | 25187611 |  | Nanjing
Whispering Willow North | 468 | 25187612 | FAG | Nanjing
Whispering Willow North | 469 | 25187613 | FAG | Nanjing
Whispering Willow North | 471 | 25187614 | FAG | Nanjing
Whispering Willow North | 472 | 25187615 | FAG | Nanjing
Whispering Willow North | 473 | 25187616 | FAG | Nanjing
Whispering Willow North | 474 | 25187617 | SKF | Winergy
Whispering Willow North | 475 | 25187618 | FAG | Nanjing
Whispering Willow North | 476 | 25187619 | FAG | Nanjing
Whispering Willow North | 477 | 25187620 | SKF | Winergy
Whispering Willow North | 478 | 25187621 | SKF | ZF
Whispering Willow North | 479 | 25187622 | SKF | Nanjing
Whispering Willow North | 480 | 25187623 | FAG | Nanjing
Whispering Willow North | 482 | 25187624 | FAG | ZF
Whispering Willow North | 483 | 25187625 | SKF | ZF
Whispering Willow North | 484 | 25187626 | FAG | Nanjing
Whispering Willow North | 485 | 25187627 | SKF | Winergy
Coyote Ridge | A1 | 25190823 | FAG | ZF
Coyote Ridge | A2 | 25190824 | NTN | ZF
Coyote Ridge | A3 | 25190825 | FAG | Nanjing
Coyote Ridge | A4 | 25190826 | FAG | Nanjing
Coyote Ridge | A5 | 25190827 | FAG | Nanjing
Coyote Ridge | A6 | 25190828 | NTN | Nanjing
Coyote Ridge | B1 | 25190829 | FAG | ZF
Coyote Ridge | B2 | 25190830 | FAG | ZF
Coyote Ridge | B3 | 25190831 | FAG | Nanjing
Coyote Ridge | B4 | 25190832 | FAG | Winergy
Coyote Ridge | B5 | 25190833 | NTN | ZF
Coyote Ridge | B7 | 25190834 | FAG | Winergy
Coyote Ridge | B8 | 25190835 | FAG | ZF
Coyote Ridge | C1 | 25190836 | FAG | Winergy
Coyote Ridge | C7 | 25190837 | FAG | Winergy
Coyote Ridge | C8 | 25190838 | Timken | Nanjing
Coyote Ridge | C9 | 25190839 | FAG | Winergy
Coyote Ridge | D1 | 25190840 | FAG | Winergy
Coyote Ridge | D4 | 25190841 | FAG | Nanjing
Coyote Ridge | D5 | 25190842 | FAG | Winergy
Coyote Ridge | D6 | 25190843 | FAG | Winergy
Coyote Ridge | D7 | 25190844 | FAG | Nanjing
Coyote Ridge | D8 | 25190845 | FAG | Nanjing
Coyote Ridge | D9 | 25190846 | FAG | Nanjing
Coyote Ridge | D10 | 25190847 | FAG | Nanjing
Coyote Ridge | D12 | 25190848 | FAG | Nanjing
Coyote Ridge | E1 | 25190849 | FAG | Nanjing
Coyote Ridge | E2 | 25190850 | FAG | Nanjing
Coyote Ridge | E3 | 25190851 | FAG | Nanjing
Coyote Ridge | E4 | 25190852 | FAG | Nanjing
Coyote Ridge | E5 | 25190853 | FAG | Nanjing
Coyote Ridge | E6 | 25190854 | FAG | ZF
Coyote Ridge | F1 | 25190855 | SKF | Nanjing
Coyote Ridge | F2 | 25190856 | SKF | Nanjing
Coyote Ridge | G3 | 25190857 | NTN | Nanjing
Richland | 3 | 25190868 | SKF | Nanjing
Richland | 4 | 25190869 | SKF | ZF
Richland | 5 | 25190870 | SKF | ZF
Richland | 6 | 25190871 | FAG | ZF
Richland | 13 | 25190872 | FAG | Nanjing
Richland | 14 | 25190873 | SKF | ZF
Richland | 18 | 25190874 | FAG | ZF
Richland | 31 | 25190875 | FAG | Nanjing
Richland | 32 | 25190876 | SKF | ZF
Richland | 38 | 25190877 | SKF | ZF
Richland | 39 | 25190878 | FAG | Nanjing
Richland | 47 | 25190879 | FAG | ZF
Richland | 49 | 25190880 | FAG | ZF
Richland | 51 | 25190881 | FAG | ZF
Richland | 53 | 25190882 | FAG | ZF
Richland | 54 | 25190883 | FAG | ZF
Richland | 55 | 25190884 | SKF | ZF
Richland | 57 | 25190885 | SKF | ZF
Richland | 58 | 25190886 | SKF | ZF
Richland | 60 | 25190887 | SKF | ZF
Richland | 61 | 25190888 | FAG | ZF
Richland | 62 | 25190889 | FAG | ZF
Richland | 63 | 25190890 | SKF | ZF
Richland | 64 | 25190891 | SKF | ZF
Richland | 65 | 25190892 | NTN | Nanjing
Richland | 66 | 25190893 | SKF | ZF
Richland | 67 | 25190894 | SKF | ZF
Richland | 68 | 25190895 | SKF | Nanjing
Richland | 69 | 25190896 | SKF | ZF
Richland | 70 | 25190897 | SKF | ZF
Richland | 72 | 25190898 | SKF | ZF
Richland | 74 | 25190899 | SKF | ZF
Richland | 75 | 25190900 | SKF | Nanjing
Richland | 77 | 25190901 | SKF | ZF
Richland | 78 | 25190902 | FAG | Nanjing
Richland | 79 | 25190903 | SKF | ZF
Richland | 81 | 25190904 | FAG | ZF
Richland | 82 | 25190905 | FAG | ZF
Richland | 83 | 25190906 | SKF | ZF
Richland | 84 | 25190907 | SKF | ZF
Richland | 85 | 25190908 | FAG | Nanjing
Darlowo II | N1 | 27120003 | Koyo | Winergy
Darlowo II | N2 | 27120004 | NTN | Winergy
Darlowo II | N3 | 27120005 | NTN | Rexroth
Darlowo II | N4 | 27120006 | NTN | Winergy
Darlowo II | N5 | 27120007 | NTN | Rexroth
Darlowo II | N6 | 27120008 | Koyo | Winergy
Darlowo II | N7 | 27120009 | NTN | Rexroth
Darlowo II | N8 | 27120010 | Koyo | Rexroth
Darlowo II | N9 | 27120011 | Koyo | Winergy
Darlowo II | N10 | 27120012 | NTN | Rexroth
Darlowo II | S11 | 27120013 | NTN | Winergy
Darlowo II | S12 | 27120014 | NTN | Winergy
Darlowo II | S5 | 27120015 | Koyo | Rexroth
Darlowo II | S6 | 27120016 | Koyo | Winergy
Darlowo II | S8 | 27120017 | NTN | Winergy
Darlowo II | S9 | 27120018 | NTN | Winergy
Darlowo II | S10 | 27120019 | Koyo | Winergy
Darlowo II | S3 | 27120020 | NTN | Winergy
Darlowo II | S4 | 27120021 | NTN | Winergy
Darlowo II | K1 | 27120022 | NTN | Rexroth
Darlowo II | K2 | 27120023 | NTN | Winergy
Darlowo II | K3 | 27120024 | NTN | Rexroth
Darlowo II | K4 | 27120025 | NTN | Rexroth
Darlowo II | K5 | 27120026 | Koyo | Winergy
Darlowo II | K6 | 27120027 | Koyo | Winergy
Darlowo II | K7 | 27120028 | Koyo | Winergy
Darlowo II | B14 | 27120029 | NTN | Eickhoff
Darlowo II | B11 | 27120030 | NTN | Eickhoff
Darlowo II | B9 | 27120031 | NTN | Eickhoff
Darlowo II | B13 | 27120032 | NTN | Eickhoff
Darlowo II | B10 | 27120033 | NTN | Eickhoff
Darlowo II | B6 | 27120034 | NTN | Winergy
Darlowo II | B8 | 27120035 | NTN | Eickhoff
Darlowo II | B5 | 27120036 | Koyo | Winergy
Darlowo II | B4 | 27120037 | Koyo | Winergy
Darlowo II | B3 | 27120038 | NTN | Rexroth
Darlowo II | B1 | 27120039 | NTN | Rexroth
Darlowo II | B2 | 27120040 | NTN | Winergy
Darlowo II | W14 | 27123248 | NTN | Winergy
Gordon Butte | TC-9 | 27183794 |  | ZF
Gordon Butte | TC-7 | 27183795 |  | Winergy
Gordon Butte | TC-8 | 27183796 |  | Replacement Pending
Beech Ridge II | 201 | 27190308 | NTN | Winergy
Beech Ridge II | 203 | 27190309 | NTN | Winergy
Maverick | 32 | 27201440 | NTN | Winergy
Maverick | 37 | 27201441 | NTN | Winergy
Maverick | 77 | 27201442 | NTN | Winergy
Maverick | 91 | 27201443 | NTN | Winergy
Maverick | 97 | 27201444 | NTN | Winergy
Maverick | 99 | 27201445 | NTN | Winergy
Goldthwaite | 40 | 28132032 | Koyo | Nanjing
Goldthwaite | 41 | 28132033 | NTN | Nanjing
Goldthwaite | 42 | 28132034 | NTN | Nanjing
Darlowo IIIb | G7 | 28140211 |  | Nanjing
Darlowo IIIb | WK3 | 28140212 |  | Nanjing
Darlowo IIIb | G6 | 28140213 |  | Nanjing
Darlowo IIIb | G17 | 28140214 |  | Nanjing
Darlowo IIIb | G8 | 28140215 |  | Nanjing
Darlowo IIIb | G4 | 28140216 |  | Nanjing
Darlowo IIIb | G5 | 28140217 |  | Nanjing
Darlowo IIIb | G10 | 28140218 |  | Nanjing
Darlowo IIIb | G13 | 28140219 |  | Nanjing
Darlowo IIIb | G16 | 28140220 |  | Nanjing
Darlowo IIIb | G15 | 28140221 |  | Nanjing
Darlowo IIIb | WK6 | 28140222 |  | Winergy
Darlowo IIIb | WK7 | 28140223 |  | Winergy
Darlowo IIIb | WK5 | 28140224 |  | Winergy
Darlowo IIIb | WK4 | 28140225 |  | Winergy
Golden Plains | 2 | 28190734 | SKF | ZF
Golden Plains | 3 | 28190735 | FAG | ZF
Golden Plains | 4 | 28190736 | FAG | Nanjing
Golden Plains | 5 | 28190737 | SKF | Nanjing
Golden Plains | 6 | 28190738 | SKF | Nanjing
Golden Plains | 7 | 28190739 | FAG | Nanjing
Golden Plains | 8 | 28190740 | FAG | Nanjing
Golden Plains | 9 | 28190741 | FAG | Nanjing
Golden Plains | 10 | 28190742 | FAG | Nanjing
Golden Plains | 11 | 28190743 | FAG | Nanjing
Golden Plains | 12 | 28190744 | SKF | Winergy
Golden Plains | 13 | 28190745 | FAG | Winergy
Golden Plains | 14 | 28190746 | FAG | Winergy
Golden Plains | 15 | 28190747 | FAG | Nanjing
Golden Plains | 17 | 28190748 | SKF | Nanjing
Golden Plains | 18 | 28190749 | FAG | ZF
Golden Plains | 22 | 28190750 | SKF | ZF
Golden Plains | 24 | 28190751 | SKF | Nanjing
Golden Plains | 25 | 28190752 | SKF | Nanjing
Golden Plains | 26 | 28190753 | SKF | Nanjing
Golden Plains | 28 | 28190754 | SKF | Nanjing
Golden Plains | 29 | 28190755 | SKF | Nanjing
Golden Plains | 31 | 28190756 | NTN | Nanjing
Golden Plains | 32 | 28190757 | NTN | Nanjing
Golden Plains | 33 | 28190758 | SKF | Nanjing
Golden Plains | 34 | 28190759 | NTN | Nanjing
Golden Plains | 35 | 28190764 | FAG | Nanjing
Golden Plains | 37 | 28190765 | FAG | Nanjing
Golden Plains | 40 | 28190766 | SKF | Nanjing
Golden Plains | 41 | 28190767 | NTN | Nanjing
Golden Plains | 45 | 28190768 | SKF | Nanjing
Golden Plains | 46 | 28190769 | NTN | Nanjing
Golden Plains | 48 | 28190770 | SKF | Nanjing
Golden Plains | 49 | 28190771 | SKF | Nanjing
Golden Plains | 50 | 28190772 | SKF | Nanjing
Golden Plains | 51 | 28190773 | SKF | Nanjing
Golden Plains | 54 | 28190774 | FAG | Nanjing
Golden Plains | 55 | 28190775 | FAG | Nanjing
Golden Plains | 65 | 28190776 | FAG | ZF
Golden Plains | 66 | 28190777 | NTN | Nanjing
Golden Plains | 68 | 28190778 | SKF | Nanjing
Golden Plains | 70 | 28190779 | SKF | Nanjing
Golden Plains | 71 | 28190780 | SKF | Nanjing
Golden Plains | 74 | 28190781 | NTN | Nanjing
Golden Plains | 75 | 28190782 | SKF | ZF
Golden Plains | 76 | 28190783 | SKF | Nanjing
Golden Plains | 77 | 28190784 | SKF | Nanjing
Golden Plains | 78 | 28190785 | FAG | ZF
Golden Plains | 79 | 28190786 | SKF | Nanjing
Golden Plains | 82 | 28191646 | NTN | Nanjing
Golden Plains | 83 | 28191647 | FAG | Nanjing
Beech Ridge II | 202 | 28192631 | SKF | Nanjing
Beech Ridge II | 204 | 28192632 | FAG | Nanjing
Beech Ridge II | 205 | 28192633 | FAG | Replacement Pending
Beech Ridge II | 206 | 28192634 | FAG | Replacement Pending
Beech Ridge II | 207 | 28192635 | FAG | Nanjing
Beech Ridge II | 208 | 28192636 | NSK | Nanjing
Beech Ridge II | 209 | 28192637 | FAG | Nanjing
Beech Ridge II | 210 | 28192638 | FAG | Nanjing
Beech Ridge II | 211 | 28192639 | NSK | Nanjing
Beech Ridge II | 212 | 28192640 | FAG | Nanjing
Beech Ridge II | 213 | 28192641 | SKF | Nanjing
Beech Ridge II | 214 | 28192642 | Timken | Nanjing
Beech Ridge II | 215 | 28192643 | FAG | Nanjing
Beech Ridge II | 216 | 28192644 | SKF | Nanjing
Beech Ridge II | 217 | 28192645 | FAG | Nanjing
Beech Ridge II | 218 | 28192646 | FAG | Nanjing
Beech Ridge II | 219 | 28192647 | SKF | Nanjing
Beech Ridge II | 220 | 28192648 | FAG | Nanjing
Thunderhead | 1 | 28192650 | FAG | Nanjing
Thunderhead | 2 | 28192651 | FAG | ZF
Thunderhead | 3 | 28192652 | FAG | Nanjing
Thunderhead | 4 | 28192653 | SKF | Nanjing
Thunderhead | 5 | 28192654 | FAG | Nanjing
Thunderhead | 6 | 28192655 | SKF | Nanjing
Thunderhead | 7 | 28192656 | SKF | Nanjing
Thunderhead | 9 | 28192657 | FAG | Nanjing
Thunderhead | 10 | 28192658 | FAG | Nanjing
Thunderhead | 11 | 28192659 | Replacement Pending | Nanjing
Thunderhead | 12 | 28192660 | SKF | Nanjing
Thunderhead | 13 | 28192661 | NTN | Nanjing
Thunderhead | 14 | 28192662 | SKF | ZF
Thunderhead | 15 | 28192663 | SKF | Nanjing
Thunderhead | 16 | 28192664 | FAG | Nanjing
Thunderhead | 17 | 28192665 | FAG | Nanjing
Thunderhead | 18 | 28192666 | SKF | Nanjing
Thunderhead | 19 | 28192667 | SKF | Nanjing
Thunderhead | 20 | 28192668 | FAG | Nanjing
Thunderhead | 21 | 28192669 | FAG | Nanjing
Thunderhead | 22 | 28192670 | FAG | Nanjing
Thunderhead | 23 | 28192671 | SKF | Nanjing
Thunderhead | 24 | 28192672 | FAG | Nanjing
Thunderhead | 25 | 28192673 | SKF | ZF
Thunderhead | 26 | 28192674 | SKF | Nanjing
Thunderhead | 27 | 28192675 | FAG | Nanjing
Thunderhead | 28 | 28192676 | SKF | Nanjing
Thunderhead | 29 | 28192677 | FAG | Nanjing
Thunderhead | 30 | 28192678 | FAG | ZF
Thunderhead | 33 | 28192679 | SKF | Nanjing
Thunderhead | 34 | 28192680 | FAG | Nanjing
Thunderhead | 35 | 28192681 | SKF | Nanjing
Thunderhead | 36 | 28192682 | SKF | ZF
Thunderhead | 37 | 28192683 | SKF | ZF
Thunderhead | 38 | 28192684 | FAG | Nanjing
Thunderhead | 39 | 28192685 | FAG | Nanjing
Thunderhead | 40 | 28192686 | SKF | ZF
Thunderhead | 41 | 28192687 | FAG | Nanjing
Thunderhead | 42 | 28192688 | FAG | Nanjing
Thunderhead | 43 | 28192689 | FAG
Thunderhead | 44 | 28192690 | SKF | Nanjing
Thunderhead | 45 | 28192691 | SKF | Nanjing
Thunderhead | 46 | 28192692 | SKF | Nanjing
Thunderhead | 47 | 28192693 | SKF | Nanjing
Thunderhead | 48 | 28192694 | NTN | Nanjing
Thunderhead | 49 | 28192695 | SKF | Nanjing
Thunderhead | 50 | 28192696 | SKF | Nanjing
Thunderhead | 51 | 28192697 | FAG | Nanjing
Thunderhead | 52 | 28192698 | SKF | Nanjing
Thunderhead | 53 | 28192699 | SKF | Nanjing
Thunderhead | 54 | 28192700 | SKF | Nanjing
Thunderhead | 55 | 28192701 | SKF | Nanjing
Thunderhead | 56 | 28192702 | SKF | Nanjing
Thunderhead | 57 | 28192703 | SKF | Nanjing
Thunderhead | 59 | 28192704 | SKF | ZF
Thunderhead | 66 | 28192705 | FAG | Nanjing
Thunderhead | 67 | 28192706 | SKF | Nanjing
Thunderhead | 68 | 28192707 | FAG | Nanjing
Thunderhead | 69 | 28192708 | SKF | Nanjing
Thunderhead | 70 | 28192709 | FAG | Nanjing
Thunderhead | 71 | 28192710 | SKF | Nanjing
Thunderhead | 72 | 28192711 | SKF | Nanjing
Thunderhead | 73 | 28192712 | SKF | Nanjing
Thunderhead | 74 | 28192713 | SKF | Nanjing
Thunderhead | 75 | 28192714 | SKF | Nanjing
Thunderhead | 76 | 28192715 | SKF | Nanjing
Thunderhead | 77 | 28192716 | SKF | Nanjing
Thunderhead | 78 | 28192717 | FAG | Nanjing
Thunderhead | 79 | 28192718 | NTN | Nanjing
Thunderhead | 80 | 28192719 | SKF | Nanjing
Thunderhead | 81 | 28192720 | FAG | Nanjing
Thunderhead | 82 | 28192721 | FAG | Nanjing
Thunderhead | 83 | 28192722 | SKF | ZF
Thunderhead | 84 | 28192723 | SKF | ZF
Thunderhead | 85 | 28192724 | SKF | Nanjing
Thunderhead | 86 | 28192725 | FAG | Nanjing
Thunderhead | 87 | 28192726 | FAG | Nanjing
Thunderhead | 88 | 28192727 | FAG | Nanjing
Thunderhead | 89 | 28192728 | SKF | Nanjing
Thunderhead | 90 | 28192729 | FAG | Nanjing
Thunderhead | 91 | 28192730 | SKF | ZF
Thunderhead | 92 | 28192731 | SKF | Nanjing
Thunderhead | 93 | 28192732 | SKF | Nanjing
Thunderhead | 94 | 28192733 | FAG | Nanjing
Thunderhead | 95 | 28192734 | SKF | Nanjing
Thunderhead | 96 | 28192735 | FAG | ZF
Thunderhead | 97 | 28192736 | SKF | Nanjing
Thunderhead | 98 | 28192737 | SKF | Nanjing
Thunderhead | 99 | 28192738 | SKF | Nanjing
Thunderhead | 100 | 28192739 | FAG | ZF
Thunderhead | 101 | 28192740 | FAG | Nanjing
Thunderhead | 102 | 28192741 | SKF | Nanjing
Thunderhead | 103 | 28192742 | SKF | ZF
Thunderhead | 104 | 28192743 | FAG | ZF
Thunderhead | 105 | 28192744 | FAG | Nanjing
Thunderhead | 106 | 28192745 | SKF | Nanjing
Thunderhead | 107 | 28192746 | SKF | Nanjing
Thunderhead | 108 | 28192747 | SKF | Nanjing
Blooming Grove | WTG-001 | 28196579 | FAG | Nanjing
Blooming Grove | WTG-002 | 28196580 | FAG | Replacement Pending
Blooming Grove | WTG-003 | 28196581 | NSK | Nanjing
Blooming Grove | WTG-004 | 28196582 | FAG | Nanjing
Blooming Grove | WTG-005 | 28196583 | FAG | Nanjing
Blooming Grove | WTG-006 | 28196584 | FAG | Nanjing
Blooming Grove | WTG-009 | 28196585 | FAG | Nanjing
Blooming Grove | WTG-013 | 28196586 | Replacement Pending | Nanjing
Blooming Grove | WTG-014 | 28196587 |  | Nanjing
Blooming Grove | WTG-015 | 28196588 | FAG | Winergy
Blooming Grove | WTG-034 | 28196589 | FAG | Replacement Pending
Blooming Grove | WTG-031 | 28196590 | FAG | ZF
Blooming Grove | WTG-032 | 28196591 | NTN | ZF
Blooming Grove | WTG-037 | 28196592 | NTN | Nanjing
Blooming Grove | WTG-035 | 28196593 | NTN | Replacement Pending
Blooming Grove | WTG-023 | 28196594 | FAG | Nanjing
Blooming Grove | WTG-022 | 28196595 | NTN | ZF
Blooming Grove | WTG-019 | 28196596 | FAG | Nanjing
Blooming Grove | WTG-021 | 28196597 | FAG | ZF
Blooming Grove | WTG-024 | 28196598 | NTN | Nanjing
Blooming Grove | WTG-017 | 28196599 | FAG | Nanjing
Blooming Grove | WTG-040 | 28196600 | FAG | Nanjing
Blooming Grove | WTG-041 | 28196601 | FAG | ZF
Blooming Grove | WTG-042 | 28196602 | FAG | Nanjing
Blooming Grove | WTG-043 | 28196603 | FAG | ZF
Blooming Grove | WTG-039 | 28196604 | FAG | ZF
Blooming Grove | WTG-038 | 28196605 | FAG | Nanjing
Blooming Grove | WTG-067 | 28196606 | Replacement Pending | ZF
Blooming Grove | WTG-051 | 28196607 | FAG | Nanjing
Blooming Grove | WTG-046 | 28196608 | FAG | Nanjing
Blooming Grove | WTG-052 | 28196609 | FAG | Nanjing
Blooming Grove | WTG-050 | 28196610 | NTN | Nanjing
Blooming Grove | WTG-054 | 28196611 | NTN | Nanjing
Blooming Grove | WTG-053 | 28196612 | Replacement Pending | Nanjing
Blooming Grove | WTG-057 | 28196613 | NSK | Nanjing
Blooming Grove | WTG-058 | 28196614 | FAG | Nanjing
Blooming Grove | WTG-072 | 28196615 | FAG | Nanjing
Blooming Grove | WTG-059 | 28196616 | NTN | Nanjing
Blooming Grove | WTG-060 | 28196617 | NSK | Nanjing
Blooming Grove | WTG-061 | 28196618 | FAG | Nanjing
Blooming Grove | WTG-063 | 28196619 | NTN | Nanjing
Blooming Grove | WTG-062 | 28196620 | FAG | Nanjing
Blooming Grove | WTG-065 | 28196621 | NSK | ZF
Blooming Grove | WTG-064 | 28196622 | NTN | Nanjing
Blooming Grove | WTG-074 | 28196623 | FAG | ZF
Blooming Grove | WTG-075 | 28196624 | NTN | Nanjing
Blooming Grove | WTG-066 | 28196625 | NSK | ZF
Blooming Grove | WTG-070 | 28196626 | FAG | Nanjing
Blooming Grove | WTG-069 | 28196627 | Replacement Pending | Nanjing
Blooming Grove | WTG-076 | 28196628 | NTN | Nanjing
Blooming Grove | WTG-071 | 28196629 | FAG | Nanjing
Blooming Grove | WTG-073 | 28196630 | FAG | Nanjing
Blooming Grove | WTG-085 | 28196631 | Replacement Pending | ZF
Blooming Grove | WTG-084 | 28196632 | Replacement Pending | ZF
Blooming Grove | WTG-083 | 28196633 | FAG | Nanjing
Blooming Grove | WTG-087 | 28196634 | FAG | Nanjing
Blooming Grove | WTG-086 | 28196635 | NTN | Nanjing
Blooming Grove | WTG-081 | 28196636 | FAG | Nanjing
Blooming Grove | WTG-082 | 28196637 | FAG | Nanjing
Blooming Grove | WTG-080 | 28196638 | FAG | Nanjing
Blooming Grove | WTG-077 | 28196639 | FAG | Nanjing
Blooming Grove | WTG-078 | 28196640 | NTN | Nanjing
Blooming Grove | WTG-079 | 28196641 | NTN | Nanjing
Blooming Grove | WTG-049 | 28196642 | FAG | ZF
Blooming Grove | WTG-048 | 28196643 | NTN | Nanjing
Blooming Grove | WTG-047 | 28196644 | NTN | Nanjing
Blooming Grove | WTG-027 | 28196645 | FAG | Replacement Pending
Blooming Grove | WTG-026 | 28196646 | FAG | Nanjing
Blooming Grove | WTG-044 | 28196647 | FAG | Nanjing
Blooming Grove | WTG-045 | 28196648 | FAG | Winergy
Blooming Grove | WTG-055 | 28196649 | FAG | Nanjing
Blooming Grove | WTG-056 | 28196650 | NTN | ZF
Blooming Grove | WTG-088 | 28196651 | NTN | ZF
Blooming Grove | WTG-089 | 28196652 | Replacement Pending | ZF
Blooming Grove | WTG-090 | 28196653 | FAG | Nanjing
Blooming Grove | WTG-091 | 28196654 | NTN | Replacement Pending
Blooming Grove | WTG-092 | 28196655 | FAG | Nanjing
Blooming Grove | WTG-093 | 28196656 | FAG | Nanjing
Blooming Grove | WTG-094 | 28196657 | NTN | Nanjing
Blooming Grove | WTG-028 | 28196658 | NTN | ZF
Blooming Grove | WTG-029 | 28196659 | NTN | Nanjing
Blooming Grove | WTG-030 | 28196660 | NTN | ZF
Blooming Grove | WTG-018 | 28196661 | Replacement Pending | ZF
Blooming Grove | WTG-012 | 28196662 | NTN | ZF
Blooming Grove | WTG-011 | 28196663 | FAG | ZF
Blooming Grove | WTG-010 | 28196664 | FAG | ZF
Kossuth | 30 | 28196760 | FAG | Nanjing
Kossuth | 31 | 28196761 | FAG | Winergy
Kossuth | 32 | 28196762 | FAG | Winergy
Kossuth | 33 | 28196763 | FAG | Winergy
Kossuth | 35 | 28196764 | FAG | Winergy
Kossuth | 36 | 28196765 | FAG | Winergy
Kossuth | 37 | 28196766 | FAG | Winergy
Kossuth | 43 | 28196767 | NTN | ZF
Kossuth | 45 | 28196768 | NTN | ZF
Kossuth | 46 | 28196769 | NTN | ZF
Kossuth | 47 | 28196770 | NTN | ZF
Kossuth | 48 | 28196771 |  | ZF
Kossuth | 49 | 28196772 | NTN | ZF
Kossuth | 50 | 28196773 | NTN | ZF
Kossuth | 51 | 28196774 | NTN | ZF
Kossuth | 52 | 28196775 | FAG | Winergy
Kossuth | 53 | 28196776 | FAG | Nanjing
Kossuth | 54 | 28196777 | FAG | ZF
Kossuth | 55 | 28196778 | FAG | ZF
Kossuth | 58 | 28196779 | FAG | Winergy
Kossuth | 60 | 28196780 | FAG | ZF
Kossuth | 64 | 28196781 | FAG | ZF
Kossuth | 65 | 28196782 | FAG | Winergy
Kossuth | 67 | 28196783 | FAG | Winergy
Kossuth | 68 | 28196784 | FAG | Winergy
Kossuth | 69 | 28196785 | FAG | ZF
Kossuth | 70 | 28196786 | SKF | Nanjing
Kossuth | 71 | 28196787 | FAG | Winergy
Kossuth | 72 | 28196788 | NTN | ZF
Kossuth | 73 | 28196789 | SKF | Nanjing
Kossuth | 74 | 28196790 | FAG | ZF
Kossuth | 78 | 28196791 | NTN | ZF
Kossuth | 79 | 28196792 | NTN | ZF
Kossuth | 80 | 28196793 | FAG | ZF
Kossuth | 81 | 28196794 | FAG | ZF
Kossuth | 82 | 28196795 | FAG | ZF
Kossuth | 83 | 28196796 | FAG | Winergy
Kossuth | 84 | 28196797 | FAG | Winergy
Kossuth | 85 | 28196798 | FAG | Winergy
Kossuth | 86 | 28196799 | FAG | ZF
Kossuth | 87 | 28196800 | FAG | Nanjing
Kossuth | 88 | 28196801 | SKF | Nanjing
Kossuth | 89 | 28196802 | SKF | ZF
Kossuth | 90 | 28196803 | FAG | ZF
Kossuth | 91 | 28196804 | FAG | Winergy
Tatanka Ridge | B02 | 28201803 | FAG | Nanjing
Tatanka Ridge | B03 | 28201804 | FAG | Nanjing
Tatanka Ridge | C05 | 28203454 | FAG | Nanjing
Tatanka Ridge | E02 | 28203455 | FAG | Nanjing
Tatanka Ridge | E04 | 28203456 | NTN | Nanjing
Tatanka Ridge | E05 | 28203457 | FAG | ZF
Tatanka Ridge | E06 | 28203458 | FAG | Nanjing
Tatanka Ridge | F01 | 28203459 | FAG | Nanjing
Tatanka Ridge | F02 | 28203460 | Replacement Pending | Nanjing
Tatanka Ridge | H01 | 28203461 | FAG | Nanjing
Tatanka Ridge | H02 | 28203462 | NTN | Nanjing
Tatanka Ridge | H03 | 28203463 | NTN | ZF
Tatanka Ridge | H04 | 28203464 | NTN | Nanjing
Tatanka Ridge | H05 | 28203465 | FAG | ZF
Tatanka Ridge | I02 | 28203466 | NSK | Nanjing
Tatanka Ridge | I03 | 28203467 | FAG | Nanjing
Tatanka Ridge | I04 | 28203468 | FAG | Nanjing
Tatanka Ridge | I05 | 28203469 | FAG | Nanjing
Tatanka Ridge | J01 | 28203470 | FAG | Nanjing
Tatanka Ridge | J02 | 28203471 | FAG | Nanjing
Tatanka Ridge | K00 | 28203472 | FAG | Nanjing
Tatanka Ridge | K01 | 28203473 | NTN | Nanjing
Tatanka Ridge | K02 | 28203474 | FAG | Nanjing
Tatanka Ridge | K03 | 28203475 | FAG | Nanjing
Tatanka Ridge | K04 | 28203476 | FAG | ZF
Tatanka Ridge | K06 | 28203477 | FAG | ZF
Tatanka Ridge | K07 | 28203478 | FAG | Replacement Pending
Tatanka Ridge | K08 | 28203479 | FAG | Nanjing
Tatanka Ridge | L01 | 28203480 | FAG | Nanjing
Tatanka Ridge | L02 | 28203481 | FAG | Nanjing
Tatanka Ridge | L03 | 28203482 | FAG | Nanjing
Tatanka Ridge | L04 | 28203483 | FAG | Nanjing
Tatanka Ridge | L05 | 28203484 | NTN | Nanjing
Tatanka Ridge | L06 | 28203485 | FAG | Nanjing
Tatanka Ridge | L07 | 28203486 | FAG | Nanjing
Tatanka Ridge | L08 | 28203487 | FAG | Nanjing
Tatanka Ridge | L09 | 28203488 | NTN | Nanjing
Tatanka Ridge | L10 | 28203489 | NTN | Nanjing
Tatanka Ridge | L11 | 28203490 | NTN | ZF
Tatanka Ridge | P01 | 28203491 | FAG | Nanjing
Tatanka Ridge | P04 | 28203492 | FAG | Nanjing
Tatanka Ridge | P06 | 28203493 | FAG | Nanjing
Tatanka Ridge | P07 | 28203494 | FAG | Nanjing
Tatanka Ridge | P08 | 28203495 | FAG | Nanjing
Tatanka Ridge | S05 | 28203496 | FAG | Nanjing
Tatanka Ridge | S06 | 28203497 | FAG | Nanjing
Tatanka Ridge | S08 | 28203498 | FAG | Nanjing
Maverick | 1 | 28205131 | FAG | ZF
Maverick | 2 | 28205132 | SKF | ZF
Maverick | 3 | 28205133 | NTN | Nanjing
Maverick | 4 | 28205134 |  | Nanjing
Maverick | 5 | 28205135 | FAG | ZF
Maverick | 6 | 28205136 | FAG | ZF
Maverick | 7 | 28205137 | NSK | ZF
Maverick | 8 | 28205138 |  | ZF
Maverick | 9 | 28205139 | NTN | ZF
Maverick | 10 | 28205140 |  | ZF
Maverick | 11 | 28205141 | NSK | ZF
Maverick | 12 | 28205142 | NTN | ZF
Maverick | 13 | 28205143 |  | ZF
Maverick | 14 | 28205144 | FAG | ZF
Maverick | 15 | 28205145 | FAG | ZF
Maverick | 16 | 28205146 | FAG | ZF
Maverick | 17 | 28205147 | SKF | ZF
Maverick | 20 | 28205148 |  | ZF
Maverick | 21 | 28205149 | FAG
Maverick | 22 | 28205150 | FAG | ZF
Maverick | 23 | 28205151 | FAG | ZF
Maverick | 24 | 28205152 |  | Nanjing
Maverick | 25 | 28205153 |  | ZF
Maverick | 26 | 28205154 |  | ZF
Maverick | 27 | 28205155 | SKF | ZF
Maverick | 28 | 28205156 |  | ZF
Maverick | 29 | 28205157 |  | Nanjing
Maverick | 30 | 28205158 | FAG | ZF
Maverick | 31 | 28205159 | FAG | Nanjing
Maverick | 33 | 28205160 | SKF | ZF
Maverick | 34 | 28205161 | FAG | ZF
Maverick | 35 | 28205162 |  | ZF
Maverick | 36 | 28205163 | FAG | ZF
Maverick | 41 | 28205164 | FAG | ZF
Maverick | 42 | 28205165 | FAG | Nanjing
Maverick | 43 | 28205166 | SKF | ZF
Maverick | 44 | 28205167 | SKF | ZF
Maverick | 45 | 28205168 | SKF | ZF
Maverick | 46 | 28205169 | FAG | Nanjing
Maverick | 47 | 28205170 |  | Nanjing
Maverick | 48 | 28205171 |  | ZF
Maverick | 49 | 28205172 | FAG | ZF
Maverick | 50 | 28205173 | FAG | Nanjing
Maverick | 51 | 28205174 | FAG | ZF
Maverick | 52 | 28205175 | FAG | ZF
Maverick | 53 | 28205176 | SKF | ZF
Maverick | 54 | 28205177 | SKF | ZF
Maverick | 55 | 28205178 | SKF | ZF
Maverick | 56 | 28205179 |  | Nanjing
Maverick | 58 | 28205180 | NTN | Nanjing
Maverick | 59 | 28205181 | FAG | Nanjing
Maverick | 60 | 28205182 | SKF | ZF
Maverick | 61 | 28205183 | SKF | ZF
Maverick | 62 | 28205184 | FAG | ZF
Maverick | 63 | 28205185 | NSK | ZF
Maverick | 64 | 28205186 | FAG | Nanjing
Maverick | 65 | 28205187 | FAG | Nanjing
Maverick | 66 | 28205188 | NSK | ZF
Maverick | 67 | 28205189 | SKF | ZF
Maverick | 68 | 28205190 | SKF | ZF
Maverick | 69 | 28205191 | NTN | ZF
Maverick | 70 | 28205192 | FAG | ZF
Maverick | 71 | 28205193 | FAG | ZF
Maverick | 73 | 28205194 |  | ZF
Maverick | 74 | 28205195 | SKF | ZF
Maverick | 75 | 28205196 | FAG | ZF
Maverick | 79 | 28205197 |  | ZF
Maverick | 80 | 28205198 |  | ZF
Maverick | 81 | 28205199 |  | ZF
Maverick | 82 | 28205200 | FAG | Nanjing
Maverick | 83 | 28205201 | SKF | ZF
Maverick | 85 | 28205202 | NSK | ZF
Maverick | 86 | 28205203 |  | ZF
Maverick | 87 | 28205204 | NSK | ZF
Maverick | 88 | 28205205 |  | ZF
Maverick | 89 | 28205206 |  | Nanjing
Maverick | 90 | 28205207 |  | ZF
Maverick | 92 | 28205208 | FAG | Nanjing
Maverick | 93 | 28205209 | SKF | Nanjing
Maverick | 94 | 28205210 | FAG | Nanjing
Maverick | 95 | 28205211 | FAG | ZF
Maverick | 96 | 28205212 |  | ZF
Maverick | 98 | 28205213 | SKF | Nanjing
Maverick | 100 | 28205214 | FAG | ZF
Maverick | 102 | 28205215 | NSK | ZF
Maverick | 103 | 28205216 | NSK | ZF
Maverick | 57 | 28205217 | SKF | ZF
Maverick | 72 | 28205218 | FAG | Nanjing
Maverick | 78 | 28205219 |  | ZF
Maverick | 84 | 28205220 |  | ZF
Maverick | 101 | 28205221 |  | ZF
Traverse I | 1001 | 28207026 |  | ZF
Traverse I | 1002 | 28207027 | FAG
Traverse I | 1003 | 28207028 | FAG | Nanjing
Traverse I | 1004 | 28207029 | FAG | Winergy
Traverse I | 1005 | 28207030 | FAG | Nanjing
Traverse I | 1006 | 28207031 | Timken | ZF
Traverse I | 1007 | 28207032 | FAG | ZF
Traverse I | 1008 | 28207033 |  | ZF
Traverse I | 1009 | 28207034 | FAG | ZF
Traverse I | 1010 | 28207035 |  | Winergy
Traverse I | 1011 | 28207036 | FAG | Nanjing
Traverse I | 1012 | 28207037 | NTN | ZF
Traverse I | 1013 | 28207038 | Timken | Winergy
Traverse I | 1014 | 28207039 | NTN | ZF
Traverse I | 1015 | 28207040 | FAG | Nanjing
Traverse I | 1016 | 28207041 | FAG | ZF
Traverse I | 1017 | 28207042 |  | ZF
Traverse I | 1018 | 28207043 | FAG | Winergy
Traverse I | 1019 | 28207044 |  | ZF
Traverse I | 1020 | 28207045 | FAG | Winergy
Traverse I | 1021 | 28207046 | FAG | ZF
Traverse I | 1022 | 28207047 | FAG | Winergy
Traverse I | 1023 | 28207048 |  | ZF
Traverse I | 1024 | 28207049 | FAG | Nanjing
Traverse I | 1025 | 28207050 | FAG | Nanjing
Traverse I | 1026 | 28207051 | FAG | Nanjing
Traverse I | 1027 | 28207052 | FAG | Nanjing
Traverse I | 1028 | 28207053 | NTN | Winergy
Traverse I | 1029 | 28207054 | NTN | ZF
Traverse I | 1030 | 28207055 | NTN | Winergy
Traverse I | 1031 | 28207056 | NTN | ZF
Traverse I | 1032 | 28207057 | NTN | ZF
Traverse I | 1033 | 28207058 | NTN | ZF
Traverse I | 1034 | 28207059 | Timken | Winergy
Traverse I | 1035 | 28207060 | FAG | ZF
Traverse I | 1036 | 28207061 | Timken | Winergy
Traverse I | 1037 | 28207062 | FAG
Traverse I | 1038 | 28207063 |  | Winergy
Traverse I | 1039 | 28207064 |  | Winergy
Traverse I | 1040 | 28207065 | NTN | Winergy
Traverse I | 1041 | 28207066 | FAG | Nanjing
Traverse I | 1042 | 28207067 | FAG | Nanjing
Traverse I | 1043 | 28207068 | FAG | Nanjing
Traverse I | 1044 | 28207069 | FAG | Nanjing
Traverse I | 1050 | 28207070 | FAG | Nanjing
Traverse I | 1052 | 28207071 | FAG | Nanjing
Traverse I | 1053 | 28207072 | FAG | Nanjing
Traverse I | 1054 | 28207073 | FAG | Nanjing
Traverse I | 1055 | 28207074 | FAG | Nanjing
Traverse I | 1056 | 28207075 | FAG
Traverse I | 1057 | 28207076 | FAG | Nanjing
Traverse I | 1058 | 28207077 | FAG | Nanjing
Traverse I | 1059 | 28207078 | FAG | Nanjing
Traverse I | 1060 | 28207079 | FAG | Nanjing
Traverse I | 1061 | 28207080 | NTN | ZF
Traverse I | 1067 | 28207081 | FAG | Nanjing
Traverse I | 1075 | 28207082 | FAG | Nanjing
Traverse I | 1079 | 28207083 | FAG | Nanjing
Traverse I | 1083 | 28207084 | FAG | Nanjing
Traverse I | 1088 | 28207085 | FAG | Nanjing
Traverse I | 1092 | 28207086 | FAG | Nanjing
Traverse I | 1093 | 28207087 | FAG | Nanjing
Traverse I | 1094 | 28207088 | FAG | Nanjing
Traverse I | 1095 | 28207089 | FAG | Nanjing
Traverse I | 1096 | 28207090 | FAG | Nanjing
Traverse I | 1110 | 28207091 | FAG | Nanjing
Traverse I | 1114 | 28207092 | FAG | Nanjing
Traverse I | 1119 | 28207093 | NTN | ZF
Traverse I | 1120 | 28207094 | FAG | Nanjing
Traverse I | 1122 | 28207095 | FAG | Nanjing
Traverse I | 1123 | 28207096 | FAG | Nanjing
Traverse I | 1124 | 28207097 | FAG | Nanjing
Traverse I | 1125 | 28207098 | FAG | Nanjing
Traverse I | 1126 | 28207099 | FAG | Nanjing
Traverse I | 1128 | 28207100 | FAG | Nanjing
Traverse I | 1129 | 28207101 | FAG | Nanjing
Traverse I | 1130 | 28207102 | FAG | Nanjing
Traverse I | 1131 | 28207103 | FAG | Nanjing
Traverse I | 1132 | 28207104 | FAG | Nanjing
Traverse I | 1135 | 28207105 | FAG | Nanjing
Traverse I | 1142 | 28207106 | FAG | Nanjing
Traverse II | 2001 | 28207107 | FAG | Nanjing
Traverse II | 2002 | 28207108 | FAG | Nanjing
Traverse II | 2003 | 28207109 | Timken | Nanjing
Traverse II | 2004 | 28207110 | FAG | Nanjing
Traverse II | 2005 | 28207111 | NTN | ZF
Traverse II | 2006 | 28207112 | FAG | Nanjing
Traverse II | 2007 | 28207113 | FAG | Nanjing
Traverse II | 2008 | 28207114 | NTN | Winergy
Traverse II | 2009 | 28207115 | FAG | Nanjing
Traverse II | 2010 | 28207116 | FAG | Nanjing
Traverse II | 2011 | 28207117 | FAG | Nanjing
Traverse II | 2012 | 28207118 | FAG | Nanjing
Traverse II | 2013 | 28207119 | FAG | Winergy
Traverse II | 2014 | 28207120 | FAG | Nanjing
Traverse II | 2015 | 28207121 | FAG | Nanjing
Traverse II | 2016 | 28207122 | NTN | ZF
Traverse II | 2017 | 28207123 | FAG | Nanjing
Traverse II | 2018 | 28207124 | FAG | Nanjing
Traverse II | 2019 | 28207125 | NTN | ZF
Traverse II | 2020 | 28207126 | Timken | ZF
Traverse II | 2021 | 28207127 | NTN | Nanjing
Traverse II | 2022 | 28207128 | FAG | Nanjing
Traverse II | 2023 | 28207129 | NTN | Nanjing
Traverse II | 2024 | 28207130 | NTN | Nanjing
Traverse II | 2025 | 28207131 | NTN | ZF
Traverse II | 2026 | 28207132 | NTN | ZF
Traverse II | 2027 | 28207133 | FAG | Nanjing
Traverse II | 2028 | 28207134 | FAG | Nanjing
Traverse II | 2029 | 28207135 | FAG | Winergy
Traverse II | 2030 | 28207136 | NTN | Nanjing
Traverse II | 2031 | 28207137 | FAG | Nanjing
Traverse II | 2032 | 28207138 | FAG | ZF
Traverse II | 2033 | 28207139 | SKF | Nanjing
Traverse II | 2034 | 28207140 | FAG | Nanjing
Traverse II | 2035 | 28207141 | SKF | ZF
Traverse II | 2036 | 28207142 | SKF | Nanjing
Traverse II | 2037 | 28207143 | SKF | ZF
Traverse II | 2038 | 28207144 | FAG | ZF
Traverse II | 2039 | 28207145 | SKF | ZF
Traverse II | 2040 | 28207146 | NTN | ZF
Traverse II | 2041 | 28207147 | NTN | ZF
Traverse II | 2042 | 28207148 | FAG | Nanjing
Traverse II | 2043 | 28207149 | FAG | Nanjing
Traverse II | 2044 | 28207150 | NTN | Nanjing
Traverse II | 2045 | 28207151 | FAG | Nanjing
Traverse II | 2046 | 28207152 | NTN | Winergy
Traverse II | 2047 | 28207153 | NTN | Nanjing
Traverse II | 2048 | 28207154 | NTN | Nanjing
Traverse II | 2049 | 28207155 | FAG | Nanjing
Traverse II | 2050 | 28207156 | FAG | ZF
Traverse II | 2051 | 28207157 | FAG | ZF
Traverse II | 2052 | 28207158 | SKF | ZF
Traverse II | 2053 | 28207159 | FAG | Nanjing
Traverse II | 2054 | 28207160 | SKF
Traverse II | 2055 | 28207161 | FAG | Nanjing
Traverse II | 2056 | 28207162 | FAG | Nanjing
Traverse II | 2057 | 28207163 | FAG | Nanjing
Traverse II | 2058 | 28207164 | NTN | ZF
Traverse II | 2059 | 28207165 | NTN | Nanjing
Traverse II | 2060 | 28207166 | NTN | Nanjing
Traverse II | 2061 | 28207167 | NTN | Nanjing
Traverse II | 2062 | 28207168 | NTN | Nanjing
Traverse II | 2063 | 28207169 | NTN | Nanjing
Traverse II | 2064 | 28207170 | FAG | Nanjing
Traverse II | 2065 | 28207171 | NTN | ZF
Traverse II | 2066 | 28207172 | FAG | ZF
Traverse II | 2067 | 28207173 | SKF | ZF
Traverse II | 2068 | 28207174 | SKF | ZF
Traverse II | 2069 | 28207175 | FAG | ZF
Traverse II | 2070 | 28207176 | SKF | Nanjing
Traverse II | 2071 | 28207177 | SKF | ZF
Traverse II | 2072 | 28207178 | SKF | Nanjing
Traverse II | 2073 | 28207179 | SKF | Nanjing
Traverse II | 2074 | 28207180 | FAG | Nanjing
Traverse II | 2075 | 28207181 | NTN | Nanjing
Traverse II | 2076 | 28207182 | FAG | Nanjing
Traverse II | 2077 | 28207183 | FAG | Nanjing
Traverse II | 2078 | 28207184 | NTN | ZF
Traverse II | 2079 | 28207185 | NTN | ZF
Traverse II | 2080 | 28207186 | SKF | ZF
Traverse II | 2081 | 28207187 | NTN | ZF
Traverse II | 2082 | 28207188 | NTN | Nanjing
Traverse II | 2083 | 28207189 | NTN | Nanjing
Traverse II | 2084 | 28207190 | NTN | ZF
Traverse II | 2085 | 28207191 | Timken | ZF
Traverse II | 2086 | 28207192 | NTN | ZF
Traverse II | 2087 | 28207193 | NTN | ZF
Traverse II | 2088 | 28207194 | NTN | ZF
Traverse II | 2089 | 28207195 | Timken | ZF
Traverse II | 2090 | 28207196 | FAG | Nanjing
Traverse II | 2091 | 28207197 | NTN | Nanjing
Traverse II | 2092 | 28207198 | NTN
Traverse II | 2093 | 28207199 | NTN | Nanjing
Traverse II | 2094 | 28207200 | NTN | Nanjing
Traverse II | 2095 | 28207201 | NTN | Winergy
Traverse II | 2096 | 28207202 | NTN | Winergy
Traverse II | 2097 | 28207203 | NTN | Nanjing
Traverse II | 2098 | 28207204 | FAG | Nanjing
Traverse II | 2099 | 28207205 | FAG | Nanjing
Traverse II | 2100 | 28207206 | FAG | Nanjing
Traverse II | 2101 | 28207207 | FAG | Nanjing
Traverse II | 2102 | 28207208 | NTN | Nanjing
Traverse II | 2103 | 28207209 | FAG | Nanjing
Traverse II | 2104 | 28207210 | NTN | Nanjing
Traverse II | 2105 | 28207211 | FAG | Nanjing
Traverse II | 2106 | 28207212 | NTN | Nanjing
Traverse II | 2107 | 28207213 | NTN | Nanjing
Traverse II | 2108 | 28207214 | NTN | Nanjing
Traverse II | 2109 | 28207215 | NTN | Nanjing
Traverse II | 2110 | 28207216 | NTN | Nanjing
Traverse II | 2111 | 28207217 | FAG | Nanjing
Traverse II | 2112 | 28207218 | NTN | Nanjing
Traverse II | 2113 | 28207219 | NTN | Winergy
Traverse II | 2114 | 28207220 | FAG | Nanjing
Traverse II | 2115 | 28207221 | NTN | Nanjing
Traverse II | 2116 | 28207222 | FAG | Nanjing
Traverse II | 2117 | 28207223 |  | Nanjing
Traverse II | 2118 | 28207224 | FAG | ZF
Traverse II | 2119 | 28207225 | SKF | ZF
Traverse II | 2120 | 28207226 | FAG | Nanjing
Traverse II | 2121 | 28207227 | NTN | ZF
Traverse II | 2122 | 28207228 | NTN | Nanjing
Traverse II | 2123 | 28207229 | NTN | Nanjing
Traverse II | 2124 | 28207230 | NTN | Nanjing
Traverse II | 2125 | 28207231 | SKF | ZF
Traverse II | 2126 | 28207232 | NTN | ZF
Traverse II | 2127 | 28207233 | NTN | Winergy
Traverse II | 2128 | 28207234 | FAG | Nanjing
Traverse II | 2129 | 28207235 | NTN | Nanjing
Traverse II | 2130 | 28207236 | NTN | Winergy
Traverse II | 2131 | 28207237 | NTN
Traverse II | 2132 | 28207238 | NTN | Nanjing
Traverse II | 2133 | 28207239 | NTN | Winergy
Traverse II | 2134 | 28207240 | SKF | ZF
Traverse II | 2135 | 28207241 | NTN | Winergy
Traverse II | 2136 | 28207242 | NTN | Winergy
Traverse II | 2137 | 28207243 | NTN | Winergy
Traverse II | 2138 | 28207244 | NTN | Winergy
Traverse II | 2139 | 28207245 | NTN | Nanjing
Traverse II | 2140 | 28207246 | FAG | Nanjing
Traverse II | 2141 | 28207247 | NTN | Winergy
Traverse II | 2142 | 28207248 | FAG | Nanjing
Traverse III | 3001 | 28207249 | FAG | Nanjing
Traverse III | 3002 | 28207250 | FAG | Nanjing
Traverse III | 3003 | 28207251 | FAG | Nanjing
Traverse III | 3005 | 28207252 | FAG | Nanjing
Traverse III | 3006 | 28207253 | FAG | Nanjing
Traverse III | 3007 | 28207254 | FAG | Nanjing
Traverse III | 3008 | 28207255 | FAG | Nanjing
Traverse III | 3009 | 28207256 | FAG | Nanjing
Traverse III | 3010 | 28207257 | FAG | Nanjing
Traverse III | 3011 | 28207258 | FAG | Nanjing
Traverse III | 3012 | 28207259 | FAG | Nanjing
Traverse III | 3013 | 28207260 | FAG | Nanjing
Traverse III | 3014 | 28207261 | FAG | Nanjing
Traverse III | 3015 | 28207262 | FAG | Nanjing
Traverse III | 3016 | 28207263 |  | Nanjing
Traverse III | 3017 | 28207264 | FAG | Nanjing
Traverse III | 3018 | 28207265 | FAG | Nanjing
Traverse III | 3019 | 28207266 | FAG | Nanjing
Traverse III | 3020 | 28207267 | FAG | Nanjing
Traverse III | 3021 | 28207268 | FAG | Nanjing
Traverse III | 3022 | 28207269 | FAG | Nanjing
Traverse III | 3023 | 28207270 | FAG | Nanjing
Traverse III | 3024 | 28207271 | FAG | Nanjing
Traverse III | 3025 | 28207272 | FAG | Nanjing
Traverse III | 3026 | 28207273 | FAG | Nanjing
Traverse III | 3027 | 28207274 | FAG | Nanjing
Traverse III | 3028 | 28207275 | FAG | Nanjing
Traverse III | 3029 | 28207276 | FAG | Nanjing
Traverse III | 3030 | 28207277 | FAG | Nanjing
Traverse III | 3031 | 28207278 | FAG | Nanjing
Traverse III | 3032 | 28207279 | FAG | Nanjing
Traverse III | 3033 | 28207280 | FAG | Nanjing
Traverse III | 3034 | 28207281 | FAG | Nanjing
Traverse III | 3035 | 28207282 | FAG | Nanjing
Traverse III | 3036 | 28207283 | FAG | Nanjing
Traverse III | 3037 | 28207284 | FAG | Nanjing
Traverse III | 3038 | 28207285 | FAG | Nanjing
Traverse III | 3039 | 28207286 | FAG | Nanjing
Traverse III | 3040 | 28207287 | FAG | Nanjing
Traverse III | 3041 | 28207288 | FAG | Nanjing
Traverse III | 3042 | 28207289 | FAG | Nanjing
Traverse III | 3043 | 28207290 | FAG | Nanjing
Traverse III | 3046 | 28207291 | FAG | Nanjing
Traverse III | 3048 | 28207292 | FAG | Nanjing
Traverse III | 3049 | 28207293 | FAG | Nanjing
Traverse III | 3051 | 28207294 | FAG | Nanjing
Traverse III | 3055 | 28207295 | FAG | Nanjing
Traverse III | 3058 | 28207296 | FAG | Nanjing
Traverse III | 3059 | 28207297 | FAG | Nanjing
Traverse III | 3060 | 28207298 | FAG | Nanjing
Traverse III | 3062 | 28207299 | FAG | Nanjing
Traverse III | 3069 | 28207300 | FAG | Nanjing
Traverse I | 1045 | 28207301 | NTN | ZF
Traverse I | 1046 | 28207302 | NTN | Winergy
Traverse I | 1047 | 28207303 |  | Winergy
Traverse I | 1048 | 28207304 |  | Winergy
Traverse I | 1049 | 28207305 | FAG | ZF
Traverse I | 1051 | 28207306 | NTN | ZF
Traverse I | 1062 | 28207307 | FAG | Nanjing
Traverse I | 1063 | 28207308 | NTN | ZF
Traverse I | 1064 | 28207309 | NTN | ZF
Traverse I | 1065 | 28207310 | NTN | ZF
Traverse I | 1066 | 28207311 | NTN | ZF
Traverse I | 1068 | 28207312 | FAG | Nanjing
Traverse I | 1069 | 28207313 | FAG | Nanjing
Traverse I | 1070 | 28207314 | FAG | Nanjing
Traverse I | 1071 | 28207315 | FAG | Nanjing
Traverse I | 1072 | 28207316 | FAG | Nanjing
Traverse I | 1073 | 28207317 | FAG | Nanjing
Traverse I | 1074 | 28207318 | FAG | Nanjing
Traverse I | 1076 | 28207319 | NTN | Winergy
Traverse I | 1077 | 28207320 | NTN | Winergy
Traverse I | 1078 | 28207321 | NTN | ZF
Traverse I | 1080 | 28207322 | FAG | Nanjing
Traverse I | 1081 | 28207323 | NTN | Nanjing
Traverse I | 1082 | 28207324 | NTN | ZF
Traverse I | 1084 | 28207325 | NTN | ZF
Traverse I | 1085 | 28207326 | FAG | Nanjing
Traverse I | 1086 | 28207327 | FAG | Nanjing
Traverse I | 1087 | 28207328 | FAG | Nanjing
Traverse I | 1089 | 28207329 | FAG | Nanjing
Traverse I | 1090 | 28207330 | FAG | Nanjing
Traverse I | 1091 | 28207331 | FAG | Nanjing
Traverse I | 1097 | 28207332 | FAG | Nanjing
Traverse I | 1098 | 28207333 |  | ZF
Traverse I | 1099 | 28207334 | FAG | Winergy
Traverse I | 1100 | 28207335 | Timken | Winergy
Traverse I | 1101 | 28207336 | FAG | Nanjing
Traverse I | 1102 | 28207337 | FAG
Traverse I | 1103 | 28207338 | FAG | Nanjing
Traverse I | 1104 | 28207339 | FAG | Nanjing
Traverse I | 1105 | 28207340 | FAG | Nanjing
Traverse I | 1106 | 28207341 | FAG | Nanjing
Traverse I | 1107 | 28207342 | FAG | Nanjing
Traverse I | 1108 | 28207343 | FAG | Nanjing
Traverse I | 1109 | 28207344
Traverse I | 1111 | 28207345 | FAG | Nanjing
Traverse I | 1112 | 28207346 |  | ZF
Traverse I | 1113 | 28207347 | FAG | Nanjing
Traverse I | 1115 | 28207348 | FAG | Nanjing
Traverse I | 1116 | 28207349 | Timken | Winergy
Traverse I | 1117 | 28207350 | Timken | Winergy
Traverse I | 1118 | 28207351 | NTN | ZF
Traverse I | 1121 | 28207352 | FAG | ZF
Traverse I | 1127 | 28207353 | FAG | Nanjing
Traverse I | 1133 | 28207354 | NTN | Nanjing
Traverse I | 1134 | 28207355 | FAG | Nanjing
Traverse I | 1136 | 28207356 | NTN | Winergy
Traverse I | 1137 | 28207357 | FAG | Nanjing
Traverse I | 1138 | 28207358 | FAG | ZF
Traverse I | 1139 | 28207359 | NTN | Winergy
Traverse I | 1140 | 28207360
Traverse I | 1141 | 28207361 | FAG | Nanjing
Maverick | 88 | 28216754 | FAG | Nanjing
Traverse I | 2119 | 28216755 | NTN | Winergy
Chickasaw | 57 | 28216760 | NTN | Nanjing
Chickasaw | 73 | 28216761 | FAG | Winergy
Chickasaw | 74 | 28216762 | NTN | Winergy
Chickasaw | 75 | 28216763 | NTN | Nanjing
Chickasaw | 76 | 28216764 | NTN | Nanjing
Chickasaw | 80 | 28216765 | NTN | Nanjing
Chickasaw | 84 | 28216766 | NTN | Winergy
Chickasaw | 85 | 28216767 | FAG | ZF
Red Barn | 1 | 34218241 | FAG | WINERGY
Red Barn | 3 | 34218242 | FAG | WINERGY
Red Barn | 4 | 34218243 | FAG | WINERGY
Red Barn | 5 | 34218244 | NTN | WINERGY
Red Barn | 6 | 34218245 | NTN | WINERGY
Red Barn | 9 | 34218246 | NTN | WINERGY
Red Barn | 10 | 34218247 | FAG | WINERGY
Red Barn | 11 | 34218248 | FAG | WINERGY
Red Barn | 12 | 34218249 | FAG | WINERGY
Red Barn | 13 | 34218250 | FAG | Winergy
Red Barn | 14 | 34218251 | FAG | WINERGY
Red Barn | 15 | 34218252 | FAG | WINERGY
Red Barn | 16 | 34218253 | FAG | WINERGY
Red Barn | 17 | 34218254 | FAG | WINERGY
Red Barn | 18 | 34218255 | FAG | WINERGY
Red Barn | 19 | 34218256 | FAG | WINERGY
Red Barn | 20 | 34218257 | FAG | WINERGY
Red Barn | 21 | 34218258 | NTN | WINERGY
Red Barn | 22 | 34218259 | NTN | WINERGY
Red Barn | 23 | 34218260 | NTN | WINERGY
Red Barn | 25 | 34218261 |  | WINERGY
Red Barn | 26 | 34218262 | FAG | WINERGY
Red Barn | 27 | 34218263 | FAG | Replacement Pending
Red Barn | 28 | 34218264 | FAG | WINERGY
Deuel Harvest | 1 | 281911739 | NTN | Nanjing
Deuel Harvest | 2 | 281911740 | FAG | Nanjing
Deuel Harvest | 3 | 281911741 | NTN | Nanjing
Deuel Harvest | 4 | 281911742 | NTN | Nanjing
Deuel Harvest | 5 | 281911743 | NTN | Nanjing
Deuel Harvest | 6 | 281911744 | NTN | Nanjing
Deuel Harvest | 8 | 281911745 | FAG | Nanjing
Deuel Harvest | 9 | 281911746 | FAG | Nanjing
Deuel Harvest | 10 | 281911747 | FAG
Deuel Harvest | 11 | 281911748 | NTN | Nanjing
Deuel Harvest | 12 | 281911749 | NTN | Nanjing
Deuel Harvest | 14 | 281911750 | Replacement Pending | ZF
Deuel Harvest | 15 | 281911751 | FAG | Nanjing
Deuel Harvest | 16 | 281911752 | FAG | Nanjing
Deuel Harvest | 17 | 281911753 | FAG | Nanjing
Deuel Harvest | 18 | 281911754 | FAG | Nanjing
Deuel Harvest | 19 | 281911755 | FAG | Nanjing
Deuel Harvest | 20 | 281911756 | FAG | Nanjing
Deuel Harvest | 22 | 281911757 | NTN | Nanjing
Deuel Harvest | 23 | 281911758 | NTN | Nanjing
Deuel Harvest | 24 | 281911759 | NTN | Nanjing
Deuel Harvest | 25 | 281911760 | Pending Repair Report | Nanjing
Deuel Harvest | 26 | 281911761 | NTN | Nanjing
Deuel Harvest | 27 | 281911762 | FAG | Nanjing
Deuel Harvest | 28 | 281911763 | NTN | Nanjing
Deuel Harvest | 29 | 281911764 | NTN | Nanjing
Deuel Harvest | 30 | 281911765 | FAG | Nanjing
Deuel Harvest | 31 | 281911766 | NTN | Nanjing
Deuel Harvest | 32 | 281911767 | FAG | Nanjing
Deuel Harvest | 33 | 281911768 | FAG | Nanjing
Deuel Harvest | 34 | 281911769 | FAG
Deuel Harvest | 35 | 281911770 | NTN | Nanjing
Deuel Harvest | 36 | 281911771 | FAG | Nanjing
Deuel Harvest | 37 | 281911772 | FAG | Nanjing
Deuel Harvest | 38 | 281911773 | FAG | Nanjing
Deuel Harvest | 39 | 281911774 | Replacement Pending | Pending Repair Report
Deuel Harvest | 40 | 281911775 | FAG | Nanjing
Deuel Harvest | 41 | 281911776 |  | Nanjing
Deuel Harvest | 42 | 281911777 | NTN | Nanjing
Deuel Harvest | 43 | 281911778 | FAG | Nanjing
Deuel Harvest | 44 | 281911779 | NTN | Replacement Pending
Deuel Harvest | 45 | 281911780 | NTN | ZF
Deuel Harvest | 46 | 281911781 | FAG | ZF
Deuel Harvest | 47 | 281911782 | NTN | ZF
Deuel Harvest | 48 | 281911783 | NTN | ZF
Deuel Harvest | 49 | 281911784 | Replacement Pending
Deuel Harvest | 50 | 281911785 | NTN | ZF
Deuel Harvest | 51 | 281911786 | Replacement Pending | ZF
Deuel Harvest | 52 | 281911787 | NTN | ZF
Deuel Harvest | 53 | 281911788 | NTN | ZF
Deuel Harvest | 54 | 281911789 | NTN | ZF
Deuel Harvest | 55 | 281911790 | FAG | Nanjing
Deuel Harvest | 56 | 281911791 | FAG | Nanjing
Deuel Harvest | 57 | 281911792 | NTN | Nanjing
Deuel Harvest | 58 | 281911793 | FAG | Nanjing
Deuel Harvest | 59 | 281911794 | NTN | ZF
Deuel Harvest | 60 | 281911795 | NTN | ZF
Deuel Harvest | 61 | 281911796 | FAG | Nanjing
Deuel Harvest | 62 | 281911797 | Replacement Pending | ZF
Deuel Harvest | 63 | 281911798 | NTN
Deuel Harvest | 64 | 281911799 | Pending Repair Report | Nanjing
Deuel Harvest | 65 | 281911800 | NTN | ZF
Deuel Harvest | 66 | 281911801 | FAG | Nanjing
Deuel Harvest | 67 | 281911802 | FAG | Nanjing
Deuel Harvest | 68 | 281911803 | FAG | Nanjing
Deuel Harvest | 69 | 281911804 | FAG | Nanjing
Deuel Harvest | 70 | 281911805 | FAG
Deuel Harvest | 71 | 281911806 | NTN | ZF
Deuel Harvest | 72 | 281911807 | NTN | ZF
Deuel Harvest | 74 | 281911808 | NTN | ZF
Deuel Harvest | 78 | 281911809 | NTN | ZF
Deuel Harvest | 79 | 281911810 | NTN | Nanjing
Deuel Harvest | 80 | 281911811 | NTN | ZF
Deuel Harvest | 81 | 281911812 | FAG | Nanjing
Deuel Harvest | 82 | 281911813 | NTN | ZF
Deuel Harvest | 83 | 281911814 | FAG | Nanjing
Deuel Harvest | 84 | 281911815 | NTN | ZF
Deuel Harvest | 85 | 281911816 | Replacement Pending | Nanjing
Deuel Harvest | 86 | 281911817 | NTN | ZF
Deuel Harvest | 87 | 281911818 | NTN | ZF
Deuel Harvest | 88 | 281911819 | Replacement Pending | ZF
Deuel Harvest | 89 | 281911820 | FAG | Nanjing
Deuel Harvest | 90 | 281911821 | FAG | ZF
Deuel Harvest | 91 | 281911822 | FAG | ZF
Deuel Harvest | 92 | 281911823 | FAG | ZF
Deuel Harvest | 94 | 281911824 | NTN | ZF
Deuel Harvest | 95 | 281911825 | NTN | ZF
Deuel Harvest | 97 | 281911826 | NTN | ZF
Deuel Harvest | 100 | 281911827 | NTN | ZF
Deuel Harvest | 101 | 281911828 | NTN | Replacement Pending
Deuel Harvest | 102 | 281911829 | NTN | ZF
Deuel Harvest | 103 | 281911830 | NTN | ZF
Deuel Harvest | 104 | 281911831 | FAG | ZF
Deuel Harvest | 105 | 281911832 | FAG | Nanjing
Deuel Harvest | 106 | 281911833 | NTN | ZF
Deuel Harvest | 107 | 281911834 | FAG | Nanjing
Deuel Harvest | 108 | 281911835 | FAG | Nanjing
Sundance | 1 | 281911836 | NTN | Nanjing
Sundance | 2 | 281911837 | NSK | Nanjing
Sundance | 3 | 281911838 | FAG | Nanjing
Sundance | 4 | 281911839 | NTN | Nanjing
Sundance | 5 | 281911840 | NTN | Nanjing
Sundance | 6 | 281911841 | NTN | Nanjing
Sundance | 7 | 281911842 |  | Nanjing
Sundance | 8 | 281911843 | NTN | Nanjing
Sundance | 9 | 281911844 | FAG | Nanjing
Sundance | 10 | 281911845 | NTN | Nanjing
Sundance | 11 | 281911846 | FAG | ZF
Sundance | 12 | 281911847 | FAG | Nanjing
Sundance | 13 | 281911848 | NTN | Nanjing
Sundance | 14 | 281911849 |  | Nanjing
Sundance | 15 | 281911850 |  | Nanjing
Sundance | 16 | 281911851 | NTN | Nanjing
Sundance | 17 | 281911852 | NTN | Nanjing
Sundance | 18 | 281911853 | NTN | ZF
Sundance | 19 | 281911854 | NTN | Winergy
Sundance | 20 | 281911855 | FAG | Nanjing
Sundance | 21 | 281911856 | FAG | Nanjing
Sundance | 22 | 281911857 | NTN
Sundance | 23 | 281911858 |  | ZF
Sundance | 24 | 281911859 | NTN | Nanjing
Sundance | 25 | 281911860 | NTN | ZF
Sundance | 26 | 281911861 |  | Nanjing
Sundance | 27 | 281911862 | NTN | ZF
Sundance | 28 | 281911863 | NTN | Nanjing
Sundance | 29 | 281911864 | FAG | Nanjing
Sundance | 30 | 281911865 | NTN | ZF
Sundance | 31 | 281911866 | FAG | Nanjing
Sundance | 32 | 281911867 | NTN | Nanjing
Sundance | 33 | 281911868 | NTN | Nanjing
Sundance | 34 | 281911869 | FAG | Nanjing
Sundance | 35 | 281911870 | NTN | Nanjing
Sundance | 36 | 281911871 | Timken | Nanjing
Sundance | 37 | 281911872 | NTN | Nanjing
Sundance | 38 | 281911873 |  | Nanjing
Sundance | 39 | 281911874 |  | Nanjing
Sundance | 40 | 281911875 | FAG | Nanjing
Sundance | 41 | 281911876 | NTN | Nanjing
Sundance | 42 | 281911877 | NTN | Nanjing
Sundance | 43 | 281911878 | FAG | Nanjing
Sundance | 44 | 281911879 | NTN | Nanjing
Sundance | 45 | 281911880 |  | Nanjing
Sundance | 46 | 281911881 | NTN | Nanjing
Sundance | 47 | 281911882 | NTN | Nanjing
Sundance | 48 | 281911883 | NTN | Nanjing
Sundance | 49 | 281911884 | NSK | Nanjing
Sundance | 50 | 281911885 | NTN | Nanjing
Sundance | 51 | 281911886 | NTN | Nanjing
Sundance | 52 | 281911887 |  | Nanjing
Sundance | 53 | 281911888 | NTN | Nanjing
Sundance | 54 | 281911889 | FAG | ZF
Sundance | 55 | 281911890 | NTN | Nanjing
Sundance | 56 | 281911891 | NTN | Nanjing
Sundance | 57 | 281911892 | FAG | ZF
Sundance | 58 | 281911893 |  | Nanjing
Sundance | 59 | 281911894 | NTN | Nanjing
Sundance | 60 | 281911895 | NTN | Nanjing
Sundance | 61 | 281911896 | NSK | Nanjing
Sundance | 62 | 281911897 | NTN | Nanjing
Sundance | 63 | 281911898 |  | ZF
Sundance | 64 | 281911899 | FAG | ZF
Sundance | 65 | 281911900 | NTN | Nanjing
Tatanka Ridge | A01 | 281912144 | FAG | Nanjing
Tatanka Ridge | A02 | 281912145 | FAG | Nanjing
Tatanka Ridge | B01 | 281912146 | FAG | Nanjing
Plymouth | 1 | 282012550 | FAG | Winergy
Plymouth | 2 | 282012551 | FAG | ZF
Plymouth | 3 | 282012552 | FAG | Winergy
Plymouth | 4 | 282012553 | FAG | Nanjing
Plymouth | 5 | 282012554 | FAG | Nanjing
Plymouth | 6 | 282012555 | FAG | ZF
Plymouth | 7 | 282012556 | FAG | ZF
Plymouth | 8 | 282012557 | FAG | Winergy
Plymouth | 10 | 282012558 | FAG | ZF
Plymouth | 11 | 282012559 | NTN | Nanjing
Plymouth | 12 | 282012560 | FAG | ZF
Plymouth | 13 | 282012561 | FAG | Nanjing
Plymouth | 15 | 282012562 | FAG | Nanjing
Plymouth | 16 | 282012563 | FAG | ZF
Plymouth | 17 | 282012564 | FAG | ZF
Plymouth | 18 | 282012565 | FAG | ZF
Plymouth | 19 | 282012566 | FAG | ZF
Plymouth | 21 | 282012567 | FAG | Winergy
Plymouth | 22 | 282012568 | FAG | ZF
Plymouth | 23 | 282012569 | FAG | Winergy
Plymouth | 27 | 282012570 | FAG | Nanjing
Plymouth | 28 | 282012571 | FAG | Nanjing
Plymouth | 29 | 282012572 | FAG | Nanjing
Plymouth | 31 | 282012573 | FAG | ZF
Plymouth | 32 | 282012574 | FAG | Nanjing
Plymouth | 33 | 282012575 | FAG | ZF
Plymouth | 35 | 282012576 | FAG | ZF
Plymouth | 36 | 282012577 | FAG | ZF
Plymouth | 37 | 282012578 | FAG | ZF
Plymouth | 40 | 282012579 | NTN | Nanjing
Plymouth | 41 | 282012580 | FAG | Nanjing
Plymouth | 43 | 282012581 | FAG | Nanjing
Plymouth | 44 | 282012582 | FAG | Nanjing
Plymouth | 46 | 282012583 | FAG
Plymouth | 48 | 282012584 | FAG | ZF
Plymouth | 49 | 282012585 | NTN | ZF
Plymouth | 50 | 282012586 | FAG | Nanjing
Plymouth | 59 | 282012587 | FAG | ZF
Plymouth | 60 | 282012588 | NTN | ZF
Plymouth | 63 | 282012589 | FAG | Nanjing
Plymouth | 64 | 282012590 | FAG | ZF
Plymouth | 65 | 282012591 | NTN | Nanjing
Plymouth | 66 | 282012592 | NTN | Nanjing
Plymouth | 67 | 282012593 | Pending Repair Report | Nanjing
Plymouth | 68 | 282012594 | Pending Repair Report | Nanjing
Plymouth | 69 | 282012595 | Pending Repair Report | Nanjing
Plymouth | 70 | 282012596 | Replacement Pending | Replacement Pending
Plymouth | 71 | 282012597 | NTN | Nanjing
Plymouth | 72 | 282012598 | FAG | Nanjing
Plymouth | 73 | 282012599 | Pending Repair Report | Nanjing
Plymouth | 74 | 282012600 | FAG | Winergy
Plymouth | 75 | 282012601 | FAG | ZF
Plymouth | 76 | 282012602 | FAG | Nanjing
Plymouth | 77 | 282012603 | FAG | ZF
Plymouth | 78 | 282012604 | FAG | Nanjing
Plymouth | 79 | 282012605 | FAG | ZF
Plymouth | 82 | 282012606 | FAG | Nanjing
Plymouth | 83 | 282012607 | FAG | ZF
Plymouth | 84 | 282012608 | FAG | Nanjing
Plymouth | 92 | 282012609 | NTN | Nanjing
Plymouth | 95 | 282012610 | FAG | ZF
Plymouth | 96 | 282012611 | FAG | ZF
Plymouth | 98 | 282012612 | FAG | Winergy
Plymouth | 99 | 282012613 | FAG | ZF
Plymouth | 101 | 282012614 | FAG | ZF
Plymouth | 102 | 282012615 | NTN | Nanjing
Plymouth | 103 | 282012616 | NTN | Nanjing
Jayhawk | A03 | 282014179 | FAG | Nanjing
Jayhawk | A04 | 282014180 | FAG | Nanjing
Jayhawk | A07 | 282014181 | FAG | Nanjing
Jayhawk | A08 | 282014182 | FAG | Nanjing
Jayhawk | A09 | 282014183 | FAG | Nanjing
Jayhawk | B01 | 282014184 | FAG | Nanjing
Jayhawk | B02 | 282014185 | FAG | Nanjing
Jayhawk | B03 | 282014186 | FAG | Nanjing
Jayhawk | B04 | 282014187 | FAG | Nanjing
Jayhawk | B05 | 282014188 | FAG | Nanjing
Jayhawk | B06 | 282014189 | FAG | Nanjing
Jayhawk | C02 | 282014190 | FAG | Nanjing
Jayhawk | C03 | 282014191 | FAG | Nanjing
Jayhawk | C04 | 282014192 | FAG | Nanjing
Jayhawk | C05 | 282014193 | FAG | Winergy
Jayhawk | C06 | 282014194 | FAG | Nanjing
Jayhawk | C07 | 282014195 | NTN | Nanjing
Jayhawk | D02 | 282014196 | FAG | Winergy
Jayhawk | D04 | 282014197 | Replacement Pending | Winergy
Jayhawk | D05 | 282014198 | FAG | Winergy
Jayhawk | D07 | 282014199 | NTN | Nanjing
Jayhawk | E01 | 282014200 | FAG | ZF
Jayhawk | E02 | 282014201 | Replacement Pending | Winergy
Jayhawk | E03 | 282014202 | NTN | Nanjing
Jayhawk | E04 | 282014203 | FAG | ZF
Jayhawk | E05 | 282014204 | FAG | Nanjing
Jayhawk | E06 | 282014205 | NTN | Nanjing
Jayhawk | E07 | 282014206 | NTN | Nanjing
Jayhawk | E08 | 282014207 | Replacement Pending | Nanjing
Jayhawk | E09 | 282014208 | NTN | Winergy
Jayhawk | E10 | 282014209 | FAG | Nanjing
Jayhawk | E12 | 282014210 | FAG | Nanjing
Jayhawk | F02 | 282014211 | FAG | Nanjing
Jayhawk | F04 | 282014212 | Replacement Pending | Nanjing
Jayhawk | F05 | 282014213 | FAG | Nanjing
Jayhawk | F06 | 282014214 | FAG | Nanjing
Jayhawk | F07 | 282014215 | FAG | Nanjing
Jayhawk | F08 | 282014216 | NTN | Winergy
Jayhawk | F09 | 282014217 | NTN | Winergy
Jayhawk | F10 | 282014218 | NTN | Nanjing
Jayhawk | F11 | 282014219 | NTN | Winergy
Jayhawk | F12 | 282014220 | FAG | Nanjing
Jayhawk | G01 | 282014221 | FAG | Nanjing
Jayhawk | G03 | 282014222 | FAG | Nanjing
Jayhawk | G06 | 282014223 | FAG | Nanjing
Jayhawk | G07 | 282014224 | FAG | Nanjing
Jayhawk | G08 | 282014225 | FAG | Nanjing
Jayhawk | G09 | 282014226 | FAG | Nanjing
Jayhawk | G10 | 282014227 | FAG | Nanjing
Jayhawk | G11 | 282014228 | FAG | Nanjing
Jayhawk | G12 | 282014229 | FAG | Nanjing
Jayhawk | G14 | 282014230 | FAG | Winergy
Jayhawk | G16 | 282014231 | FAG | Nanjing
Jayhawk | H03 | 282014232 |  | Nanjing
Jayhawk | H05 | 282014233 | FAG | Nanjing
Jayhawk | H06 | 282014234 | FAG | Nanjing
Jayhawk | H08 | 282014235 | FAG | Nanjing
Jayhawk | H09 | 282014236 | FAG | Nanjing
Jayhawk | I05 | 282014237 | FAG | Winergy
Jayhawk | I08 | 282014238 | FAG | Winergy
Jayhawk | I09 | 282014239 | FAG | Nanjing
Jayhawk | I10 | 282014240 | FAG | Nanjing
Jayhawk | I11 | 282014241 | FAG | Nanjing
Jayhawk | I13 | 282014242 | FAG | Nanjing
Jayhawk | J02 | 282014243 | FAG | Nanjing
Jayhawk | J03 | 282014244 | FAG | Winergy
Jayhawk | J07 | 282014245 | FAG | Winergy
Jayhawk | J08 | 282014246 | FAG | Nanjing
Jayhawk | J10 | 282014247 | NTN | Nanjing
Jayhawk | J17 | 282014248 | FAG | Winergy
Diversion | 1 | 342205113 | FAG | Winergy
Diversion | 2 | 342205114 | FAG | Pending Repair Report
Diversion | 3 | 342205115 | FAG | Winergy
Diversion | 4 | 342205116 | NTN | Winergy
Diversion | 8 | 342205117 | NTN | Winergy
Diversion | 9 | 342205118 | FAG | Nanjing
Diversion | 10 | 342205119 | FAG | Nanjing
Diversion | 11 | 342205120 | FAG | Nanjing
Diversion | 12 | 342205121 | FAG | Winergy
Diversion | 13 | 342205122 | NTN | Pending Repair Report
Diversion | 14 | 342205123 | FAG | Winergy
Diversion | 15 | 342205124 | FAG | Winergy
Diversion | 16 | 342205125 | NTN | Winergy
Diversion | 17 | 342205126 | FAG | Winergy
Diversion | 18 | 342205127 | FAG | Winergy
Diversion | 21 | 342205128 | NTN | Winergy
Diversion | 22 | 342205129 | FAG | Winergy
Diversion | 23 | 342205130 | FAG | Winergy
Diversion | 24 | 342205131 | FAG | Winergy
Diversion | 26 | 342205132 | FAG | Winergy
Diversion | 27 | 342205133 | FAG | Winergy
Diversion | 28 | 342205134 | FAG | Winergy
Diversion | 29 | 342205135 | FAG | Winergy
Diversion | 30 | 342205136 | FAG | Winergy
Diversion | 31 | 342205137 | FAG | Winergy
Diversion | 32 | 342205138 | FAG | Winergy
Diversion | 33 | 342345071 | FAG | Winergy
Diversion | 34 | 342345072 | FAG | Winergy
Diversion | 35 | 342345073 | FAG | Winergy
Diversion | 36 | 342345074 | FAG | Winergy
Diversion | 37 | 342345075 | FAG | Winergy
Diversion | 45 | 342345076 | FAG | Pending Repair Report
Diversion | 47 | 342345077 | FAG | Winergy
Diversion | 48 | 342345078 | FAG | Winergy
Diversion | 49 | 342345079 | FAG | Winergy
Diversion | 50 | 342345080 | FAG | Winergy
Diversion | 51 | 342345081 | FAG | Winergy
Diversion | 52 | 342345082 | FAG | Winergy
Diversion | 53 | 342345083 | NTN | Winergy
Diversion | 58 | 342345084 | NTN | Winergy
Diversion | 59 | 342345085 | NTN | Winergy
Diversion | 60 | 342345086 | NTN | Pending Repair Report
Diversion | 61 | 342345087 | NTN | Winergy
Diversion | 62 | 342345088 | NTN | Winergy
Diversion | 63 | 342345089 | FAG | Nanjing
Diversion | 64 | 342345090 | FAG | Pending Repair Report
Diversion | 65 | 342345091 | FAG | Nanjing
Diversion | 66 | 342345092 | FAG | Winergy
Diversion | 67 | 342345093 | NTN | Winergy
Diversion | 69 | 342345094 | NTN | Nanjing
Diversion | 70 | 342345095 | FAG | Nanjing
Diversion | 71 | 342345096 | FAG | Nanjing
Diversion | 72 | 342345097 | NTN | Nanjing
Diversion | 73 | 342345098 | NTN | Winergy
Diversion | 76 | 342345099 | NTN | Winergy
Diversion | 78 | 342345100 | FAG | Winergy
Diversion | 85 | 342345101 | NTN | Winergy
Diversion | 92 | 342345102 | FAG | Nanjing
Diversion | 93 | 342345103 | FAG | Nanjing
Rock Creek I | 1 | 612346225 | FAG | ZF
Rock Creek I | 2 | 612346226 | FAG | ZF
Rock Creek I | 3 | 612346227 | FAG | ZF
Rock Creek I | 4 | 612346228 | FAG | ZF
Rock Creek I | 5 | 612346229 | FAG | ZF
Rock Creek I | 6 | 612346230 | FAG | ZF
Rock Creek I | 7 | 612346231 | FAG | ZF
Rock Creek I | 8 | 612346232 | FAG | ZF
Rock Creek I | 9 | 612346233 | FAG | ZF
Rock Creek I | 10 | 612346234 | FAG | ZF
Rock Creek I | 11 | 612346235 | FAG | ZF
Rock Creek I | 12 | 612346236 | FAG | ZF
Rock Creek I | 13 | 612346237 | FAG | ZF
Rock Creek I | 14 | 612346238 | FAG | ZF
Rock Creek I | 15 | 612346239 | FAG | ZF
Rock Creek I | 16 | 612346240 | FAG | ZF
Rock Creek I | 17 | 612346241 | FAG | ZF
Rock Creek I | 18 | 612346242 | FAG | ZF
Rock Creek I | 19 | 612346243 | FAG | ZF
Rock Creek I | 20 | 612346244 | FAG | ZF
Rock Creek I | 21 | 612346245 | FAG | ZF
Rock Creek I | 22 | 612346246 | FAG | ZF
Rock Creek I | 23 | 612346247 | FAG | ZF
Rock Creek I | 24 | 612346248 | FAG | ZF
Rock Creek I | 25 | 612346249 | FAG | ZF
Rock Creek I | 26 | 612346250 | FAG | ZF
Rock Creek I | 27 | 612346251 | FAG | ZF
Rock Creek I | 28 | 612346252 | FAG | ZF
Rock Creek I | 29 | 612346253 | FAG | ZF
Rock Creek I | 30 | 612346254 | FAG | ZF
Rock Creek I | 31 | 612346255 | FAG | ZF
Rock Creek I | 32 | 612346256 | FAG | ZF
Rock Creek II | 33 | 612446476 | FAG | Winergy
Rock Creek II | 34 | 612446477 | FAG | ZF
Rock Creek II | 35 | 612446478 | FAG | ZF
Rock Creek II | 36 | 612446479 | FAG | ZF
Rock Creek II | 37 | 612446480 | NTN | ZF
Rock Creek II | 38 | 612446481 | FAG | Winergy
Rock Creek II | 39 | 612446482 | FAG | ZF
Rock Creek II | 40 | 612446483 | NTN | ZF
Rock Creek II | 41 | 612446484 | NTN | ZF
Rock Creek II | 42 | 612446485 | NTN | ZF
Rock Creek II | 43 | 612446486 | FAG | Winergy
Rock Creek II | 44 | 612446487 | FAG
Rock Creek II | 45 | 612446488 | NTN | ZF
Rock Creek II | 46 | 612446489 | FAG | Winergy
Rock Creek II | 47 | 612446490 | FAG | Winergy
Rock Creek II | 48 | 612446491 | NTN | ZF
Rock Creek II | 49 | 612446492 | NTN | ZF
Rock Creek II | 50 | 612446493 | FAG | ZF
Rock Creek II | 51 | 612446494 | FAG | Winergy
Rock Creek II | 52 | 612446495 | FAG | Winergy
Rock Creek II | 53 | 612446496 | NTN | ZF
Rock Creek II | 54 | 612446497 | NTN | ZF
Rock Creek II | 55 | 612446498 | NTN | ZF
Rock Creek II | 56 | 612446499 | NTN | ZF
Rock Creek II | 57 | 612446500 | FAG | Winergy
Rock Creek II | 58 | 612446501 | FAG | ZF
Rock Creek II | 59 | 612446502 | FAG | ZF
Rock Creek II | 60 | 612446503 | NTN | ZF
Rock Creek II | 61 | 612446504 | NTN | ZF
Rock Creek II | 62 | 612446505 | FAG | ZF
Rock Creek II | 63 | 612446506 | FAG | Winergy
Rock Creek II | 64 | 612446507 | FAG | Winergy
Rock Creek II | 65 | 612446508 | FAG | ZF
Rock Creek II | 66 | 612446509 | FAG | ZF
Rock Creek II | 67 | 612446510 | FAG | ZF
Rock Creek II | 68 | 612446511 | FAG | ZF
Rock Creek II | 69 | 612446512 | FAG | ZF
Rock Creek II | 70 | 612446513 | FAG | ZF
Rock Creek II | 71 | 612446514 | FAG | ZF
Rock Creek II | 72 | 612446515 | FAG | ZF
Rock Creek II | 73 | 612446516 | FAG | ZF
Rock Creek II | 74 | 612446517 | FAG | ZF
Rock Creek II | 75 | 612446518 | NTN | ZF
Rock Creek II | 76 | 612446519 | FAG | ZF
Rock Creek II | 77 | 612446520 | NTN | ZF
Rock Creek II | 78 | 612446521 | NTN | ZF
Rock Creek II | 79 | 612446522 | FAG | ZF
Rock Creek II | 80 | 612446523 | NTN | Winergy
Rock Creek II | 81 | 612446524 | NTN | ZF
Rock Creek II | 82 | 612446525 | NTN | Winergy
Rock Creek II | 83 | 612446526 | NTN | ZF
Rock Creek II | 84 | 612446527 | FAG | Winergy
Rock Creek II | 85 | 612446528 | FAG | Winergy
Rock Creek II | 86 | 612446529 | FAG | Winergy
Rock Creek II | 87 | 612446530 | FAG | Winergy
Rock Creek II | 88 | 612446531 | FAG | Winergy
Rock Creek II | 89 | 612446532 | NTN
Rock Creek II | 90 | 612446533 | FAG | Winergy
Rock Creek II | 91 | 612446534 | NTN | Winergy
Rock Creek II | 92 | 612446535 | NTN | Winergy
Rock Creek II | 93 | 612446536 | NTN
Rock Creek II | 94 | 612446537 | FAG | ZF
Rock Creek II | 95 | 612446538 | NTN | Winergy
Rock Creek II | 96 | 612446539 | NTN | ZF
Rock Creek II | 97 | 612446540 | NTN | Winergy
Rock Creek II | 98 | 612446541 | NTN | Winergy
Bishop Hill | 48 | 714609048 | SKF | Winergy
Bishop Hill | 49 | 714609049 | FAG | Winergy
Bishop Hill | 50 | 714609050 | SKF | Winergy
Bishop Hill | 51 | 714609051 | Timken | Winergy
Bishop Hill | 52 | 714609052 |  | Winergy
Bishop Hill | 53 | 714609053 | SKF | Winergy
Bishop Hill | 54 | 714609054 | SKF | Winergy
Bishop Hill | 55 | 714609055 | SKF | Winergy
Bishop Hill | 56 | 714609056 |  | Winergy
Bishop Hill | 59 | 714609059 | SKF | Winergy
Bishop Hill | 60 | 714609060 |  | Winergy
Bishop Hill | 61 | 714609061 | FAG | Winergy
Bishop Hill | 73 | 714609073 | SKF | Winergy
Bishop Hill | 74 | 714609074 | SKF | Winergy
Bishop Hill | 75 | 714609075 | FAG | Winergy
Bishop Hill | 76 | 714609076 | SKF | Winergy
Bishop Hill | 77 | 714609077 | SKF | Winergy
Bishop Hill | 78 | 714609078 |  | Winergy
Bishop Hill | 79 | 714609079 |  | Winergy
Bishop Hill | 92 | 714609092 |  | Winergy
Bishop Hill | 93 | 714609093 |  | Winergy
Bishop Hill | 111 | 714609111 |  | Winergy
Bishop Hill | 112 | 714609112 | FAG | Winergy
Bishop Hill | 119 | 714609119 |  | Winergy
Bishop Hill | 120 | 714609120 |  | Winergy
Bishop Hill | 121 | 714609121 |  | Winergy
Bishop Hill | 123 | 714609123 |  | Winergy
Bishop Hill | 124 | 714609124 |  | Winergy
Bishop Hill | 125 | 714609125 |  | Winergy
Bishop Hill | 126 | 714609126 |  | Winergy
Bishop Hill | 127 | 714609127 |  | Winergy
Bishop Hill | 131 | 714609131 |  | Winergy
Bishop Hill | 132 | 714609132 | FAG | Winergy
Bishop Hill | 133 | 714609133 |  | Winergy
Judith Gap | 1 | 840031001 | SKF | ZF
Judith Gap | 2 | 840031002 | SKF | Winergy
Judith Gap | 3 | 840031003 | SKF | Winergy
Judith Gap | 4 | 840031004 | SKF | Winergy
Judith Gap | 5 | 840031005 | SKF | Winergy
Judith Gap | 6 | 840031006 | SKF | Winergy
Judith Gap | 7 | 840031007 | SKF | Nanjing
Judith Gap | 8 | 840031008 | SKF | Nanjing
Judith Gap | 9 | 840031009 | SKF | Winergy
Judith Gap | 10 | 840031010 | SKF | Winergy
Judith Gap | 11 | 840031011 | FAG | Moventas
Judith Gap | 12 | 840031012 | SKF | Nanjing
Judith Gap | 13 | 840031013 | SKF | Rexroth
Judith Gap | 14 | 840031014 | SKF | Winergy
Judith Gap | 15 | 840031015 | SKF | Winergy
Judith Gap | 16 | 840031016 | SKF | Winergy
Judith Gap | 17 | 840031017 | SKF | ZF
Judith Gap | 18 | 840031018 | SKF | Winergy
Judith Gap | 19 | 840031019 | SKF | Winergy
Judith Gap | 20 | 840031020 | SKF | Nanjing
Judith Gap | 21 | 840031021 | SKF | Replacement Pending
Judith Gap | 22 | 840031022 | SKF | Winergy
Judith Gap | 23 | 840031023 | SKF | Winergy
Judith Gap | 24 | 840031024 | SKF | Winergy
Judith Gap | 25 | 840031025 | SKF | Rexroth
Judith Gap | 26 | 840031026 | SKF | Pending Repair Report
Judith Gap | 27 | 840031027 | SKF | Winergy
Judith Gap | 28 | 840031028 | SKF | Winergy
Judith Gap | 29 | 840031029 | SKF | ZF
Judith Gap | 30 | 840031030 | Timken | Winergy
Judith Gap | 31 | 840031031 | SKF | Winergy
Judith Gap | 32 | 840031032 | SKF | Winergy
Judith Gap | 33 | 840031033 | SKF | Winergy
Judith Gap | 34 | 840031034 | SKF | Replacement Pending
Judith Gap | 35 | 840031035 | FAG | Nanjing
Judith Gap | 36 | 840031036 | SKF | Winergy
Judith Gap | 37 | 840031037 | SKF | Winergy
Judith Gap | 38 | 840031038 | SKF | Winergy
Judith Gap | 39 | 840031039 | SKF | Winergy
Judith Gap | 40 | 840031040 | SKF | Winergy
Judith Gap | 41 | 840031041 | FAG | Nanjing
Judith Gap | 42 | 840031042 | FAG | Winergy
Judith Gap | 43 | 840031043 | SKF | Winergy
Judith Gap | 44 | 840031044 | FAG | ZF
Judith Gap | 45 | 840031045 | FAG | Winergy
Judith Gap | 46 | 840031046 | FAG | Winergy
Judith Gap | 47 | 840031047 | FAG | Winergy
Judith Gap | 48 | 840031048 | Timken | Winergy
Judith Gap | 49 | 840031049 | FAG | Winergy
Judith Gap | 50 | 840031050 | FAG | Winergy
Judith Gap | 51 | 840031051 | FAG | Winergy
Judith Gap | 52 | 840031052 | FAG | Moventas
Judith Gap | 53 | 840031053 | SKF | Moventas
Judith Gap | 54 | 840031054 | SKF | Winergy
Judith Gap | 57 | 840031057 | Timken | Nanjing
Judith Gap | 60 | 840031060 | SKF | Winergy
Judith Gap | 61 | 840031061 | SKF | Winergy
Judith Gap | 62 | 840031062 | SKF | Winergy
Judith Gap | 63 | 840031063 | SKF | Winergy
Judith Gap | 64 | 840031064 | SKF | Winergy
Judith Gap | 65 | 840031065 | SKF | Nanjing
Judith Gap | 66 | 840031066 | SKF | Winergy
Judith Gap | 67 | 840031067 | SKF | Winergy
Judith Gap | 72 | 840031072 | SKF | Winergy
Judith Gap | 73 | 840031073 | FAG | Winergy
Judith Gap | 74 | 840031074 | SKF | Nanjing
Judith Gap | 75 | 840031075 | SKF | Winergy
Judith Gap | 76 | 840031076 | SKF | Winergy
Judith Gap | 77 | 840031077 | Timken | Moventas
Judith Gap | 78 | 840031078 | SKF | Winergy
Judith Gap | 79 | 840031079 | SKF | Nanjing
Judith Gap | 82 | 840031082 | SKF | Moventas
Judith Gap | 83 | 840031083 | FAG | Winergy
Judith Gap | 84 | 840031084 | SKF | Winergy
Judith Gap | 85 | 840031085 | SKF | Moventas
Judith Gap | 86 | 840031086 | FAG | Winergy
Judith Gap | 87 | 840031087 | Timken | Nanjing
Judith Gap | 88 | 840031088 | FAG | Winergy
Judith Gap | 89 | 840031089 | FAG | Winergy
Judith Gap | 90 | 840031090 | Timken | Winergy
Judith Gap | 91 | 840031091 | SKF | Replacement Pending
Judith Gap | 92 | 840031092 |  | Winergy
Judith Gap | 93 | 840031093 | FAG | Winergy
Judith Gap | 94 | 840031094 | Replacement Pending | Winergy
Judith Gap | 95 | 840031095 | FAG | Winergy
Judith Gap | 96 | 840031096 | SKF | Winergy
Judith Gap | 97 | 840031097 | FAG | Winergy
Judith Gap | 98 | 840031098 | Timken | Winergy
Judith Gap | 99 | 840031099 | SKF | Winergy
Judith Gap | 100 | 840031100 | SKF | Winergy
Wolverine Creek | 1 | 840037001 | SKF | Winergy
Wolverine Creek | 2 | 840037002 | SKF | Winergy
Wolverine Creek | 3 | 840037003 | Replacement Pending | Winergy
Wolverine Creek | 4 | 840037004 | SKF | Winergy
Wolverine Creek | 5 | 840037005 | SKF | Winergy
Wolverine Creek | 6 | 840037006 | SKF | Nanjing
Wolverine Creek | 7 | 840037007 | SKF | Winergy
Wolverine Creek | 8 | 840037008 | SKF | Winergy
Wolverine Creek | 9 | 840037009 | Timken | GETS
Wolverine Creek | 10 | 840037010 | SKF | Winergy
Wolverine Creek | 11 | 840037011 | SKF | Winergy
Wolverine Creek | 12 | 840037012 | SKF | Winergy
Wolverine Creek | 13 | 840037013 | SKF | Winergy
Wolverine Creek | 14 | 840037014 | SKF | Winergy
Wolverine Creek | 15 | 840037015 | SKF | Winergy
Wolverine Creek | 16 | 840037016 | SKF | Winergy
Wolverine Creek | 17 | 840037017 | SKF | Winergy
Wolverine Creek | 18 | 840037018 | SKF | Winergy
Wolverine Creek | 19 | 840037019 | SKF | Winergy
Wolverine Creek | 20 | 840037020 | SKF | Winergy
Wolverine Creek | 21 | 840037021 | SKF | Winergy
Wolverine Creek | 22 | 840037022 | SKF | Winergy
Wolverine Creek | 23 | 840037023 | SKF | GETS
Wolverine Creek | 24 | 840037024 |  | Winergy
Wolverine Creek | 25 | 840037025 | SKF | Winergy
Wolverine Creek | 26 | 840037026 | SKF | Winergy
Wolverine Creek | 27 | 840037027 | Replacement Pending | Winergy
Wolverine Creek | 28 | 840037028 | SKF | Winergy
Wolverine Creek | 29 | 840037029 | SKF | Winergy
Wolverine Creek | 30 | 840037030 | Timken | Winergy
Wolverine Creek | 31 | 840037031 | SKF | Winergy
Wolverine Creek | 32 | 840037032 | SKF | Winergy
Wolverine Creek | 33 | 840037033 | SKF | Winergy
Wolverine Creek | 34 | 840037034 | SKF | Winergy
Wolverine Creek | 35 | 840037035 | SKF | Winergy
Wolverine Creek | 36 | 840037036 | SKF | Winergy
Wolverine Creek | 37 | 840037037 | SKF | Winergy
Wolverine Creek | 38 | 840037038 | SKF | Winergy
Wolverine Creek | 39 | 840037039 | SKF | Winergy
Wolverine Creek | 40 | 840037040 | SKF | Winergy
Wolverine Creek | 41 | 840037041 | SKF | Winergy
Wolverine Creek | 42 | 840037042 | SKF | Replacement Pending
Wolverine Creek | 43 | 840037043 | SKF | Winergy
Spring Canyon | 1 | 840039001 | SKF | Nanjing
Spring Canyon | 2 | 840039002 | SKF | Nanjing
Spring Canyon | 3 | 840039003 | SKF | Winergy
Spring Canyon | 4 | 840039004 | SKF | Winergy
Spring Canyon | 5 | 840039005 | SKF | Winergy
Spring Canyon | 6 | 840039006 | SKF | Rexroth
Spring Canyon | 7 | 840039007 | SKF | Winergy
Spring Canyon | 8 | 840039008 | SKF | Winergy
Spring Canyon | 9 | 840039009 | SKF | Winergy
Spring Canyon | 10 | 840039010 | SKF | Winergy
Spring Canyon | 11 | 840039011 | SKF | Winergy
Spring Canyon | 12 | 840039012 | SKF | GETS
Spring Canyon | 13 | 840039013 | SKF | Winergy
Spring Canyon | 14 | 840039014 | SKF | Winergy
Spring Canyon | 15 | 840039015 | SKF | Winergy
Spring Canyon | 16 | 840039016 | SKF | Moventas
Spring Canyon | 17 | 840039017 | SKF | Moventas
Spring Canyon | 18 | 840039018 | Timken | Winergy
Spring Canyon | 19 | 840039019 | SKF | Moventas
Spring Canyon | 20 | 840039020 | FAG | Winergy
Spring Canyon | 21 | 840039021 | Timken | Nanjing
Spring Canyon | 22 | 840039022 | SKF | Rexroth
Spring Canyon | 23 | 840039023 | SKF | Moventas
Spring Canyon | 24 | 840039024 | FAG | Winergy
Spring Canyon | 25 | 840039025 | Timken | Moventas
Spring Canyon | 26 | 840039026 | SKF | Nanjing
Spring Canyon | 27 | 840039027 | SKF | Moventas
Spring Canyon | 28 | 840039028 | SKF | Winergy
Spring Canyon | 29 | 840039029 | SKF | Nanjing
Spring Canyon | 30 | 840039030 | SKF | Moventas
Spring Canyon | 31 | 840039031 | SKF | Moventas
Spring Canyon | 32 | 840039032 | SKF | Moventas
Spring Canyon | 33 | 840039033 | FAG | Moventas
Spring Canyon | 34 | 840039034 | FAG | Moventas
Spring Canyon | 35 | 840039035 | SKF | Winergy
Spring Canyon | 36 | 840039036 | SKF | Nanjing
Spring Canyon | 37 | 840039037 | SKF | Nanjing
Spring Canyon | 38 | 840039038 | SKF | Nanjing
Spring Canyon | 39 | 840039039 | SKF | Rexroth
Spring Canyon | 40 | 840039040 | SKF | Rexroth
Camp Springs I | 1 | 840058001 | SKF | Moventas
Camp Springs I | 2 | 840058002 | SKF | Moventas
Camp Springs I | 3 | 840058003 | SKF | Winergy
Camp Springs I | 4 | 840058004 | SKF
Camp Springs I | 5 | 840058005 | SKF | Moventas
Camp Springs I | 6 | 840058006 | SKF
Camp Springs I | 7 | 840058007 | SKF | GETS
Camp Springs I | 8 | 840058008 | SKF | Moventas
Camp Springs I | 9 | 840058009 | SKF | Winergy
Camp Springs I | 10 | 840058010 | SKF | Winergy
Camp Springs I | 11 | 840058011 | SKF
Camp Springs I | 12 | 840058012 | SKF | Moventas
Camp Springs I | 13 | 840058013 | SKF | Winergy
Camp Springs I | 14 | 840058014 | SKF | Winergy
Camp Springs I | 15 | 840058015 | SKF | Winergy
Camp Springs I | 16 | 840058016 | SKF | Moventas
Camp Springs I | 17 | 840058017 | SKF | Moventas
Camp Springs I | 18 | 840058018 | Replacement Pending | Moventas
Camp Springs I | 19 | 840058019 | SKF | Moventas
Camp Springs I | 20 | 840058020 | SKF | Moventas
Camp Springs I | 21 | 840058021 | SKF | Moventas
Camp Springs I | 22 | 840058022 | SKF | Moventas
Camp Springs I | 23 | 840058023 | SKF | Moventas
Camp Springs I | 24 | 840058024 | SKF | Winergy
Camp Springs I | 25 | 840058025 | SKF | Moventas
Camp Springs I | 26 | 840058026 | SKF | Winergy
Camp Springs I | 27 | 840058027 | SKF | Winergy
Camp Springs I | 28 | 840058028 | SKF | Rexroth
Camp Springs I | 29 | 840058029 | SKF | Winergy
Camp Springs I | 30 | 840058030 | SKF | Moventas
Camp Springs I | 31 | 840058031 | SKF | Winergy
Camp Springs I | 32 | 840058032 | SKF | Winergy
Camp Springs I | 33 | 840058033 | SKF | Winergy
Camp Springs I | 34 | 840058034 | SKF | Winergy
Camp Springs I | 35 | 840058035 | SKF | Moventas
Camp Springs I | 36 | 840058036 | SKF | Winergy
Camp Springs I | 37 | 840058037 | Pending Repair Report | Winergy
Camp Springs I | 38 | 840058038 | SKF | Moventas
Camp Springs I | 39 | 840058039 | SKF | Rexroth
Camp Springs I | 40 | 840058040 | SKF | Moventas
Camp Springs I | 41 | 840058041 | SKF | Winergy
Camp Springs I | 42 | 840058042 | SKF | Rexroth
Camp Springs I | 43 | 840058043 | SKF | Winergy
Camp Springs I | 44 | 840058044 | SKF | Winergy
Camp Springs I | 45 | 840058045 | SKF | Moventas
Camp Springs I | 46 | 840058046 | SKF | Winergy
Camp Springs I | 47 | 840058047 | Koyo | Moventas
Camp Springs I | 48 | 840058048 | Timken | Winergy
Camp Springs I | 49 | 840058049 | SKF | Winergy
Camp Springs I | 50 | 840058050 | SKF | Winergy
Camp Springs I | 51 | 840058051 | SKF | Moventas
Camp Springs I | 52 | 840058052 | SKF | Winergy
Camp Springs I | 53 | 840058053 | Koyo | Moventas
Camp Springs I | 54 | 840058054 | SKF | Winergy
Camp Springs I | 55 | 840058055 | Replacement Pending | Winergy
Camp Springs I | 56 | 840058056 | SKF | Winergy
Camp Springs I | 57 | 840058057 | SKF | Winergy
Camp Springs I | 58 | 840058058 | SKF | Winergy
Camp Springs I | 59 | 840058059 | Koyo | Winergy
Camp Springs I | 60 | 840058060 | SKF | Moventas
Camp Springs I | 61 | 840058061 | Replacement Pending | Winergy
Camp Springs I | 62 | 840058062 | SKF | Winergy
Camp Springs I | 63 | 840058063 | SKF | Moventas
Camp Springs I | 64 | 840058064 | SKF | Moventas
Camp Springs I | 65 | 840058065 | SKF | Moventas
Camp Springs I | 66 | 840058066 | SKF
Camp Springs I | 67 | 840058067 | SKF | Winergy
Camp Springs I | 68 | 840058068 | SKF | Moventas
Camp Springs I | 69 | 840058069 | SKF | Moventas
Camp Springs I | 70 | 840058070 | SKF | Replacement Pending
Camp Springs I | 71 | 840058071 | Koyo
Camp Springs I | 72 | 840058072 | SKF | Winergy
Camp Springs I | 73 | 840058073 | SKF
Camp Springs I | 74 | 840058074 | SKF | Winergy
Camp Springs I | 75 | 840058075 | SKF | Winergy
Camp Springs I | 76 | 840058076 | SKF | Moventas
Camp Springs I | 77 | 840058077 | SKF | Moventas
Camp Springs I | 78 | 840058078 | SKF | Winergy
Camp Springs I | 79 | 840058079 | SKF | Winergy
Camp Springs I | 80 | 840058080 | SKF | Winergy
Camp Springs I | 81 | 840058081 | SKF | Winergy
Camp Springs I | 82 | 840058082 | SKF | Moventas
Camp Springs I | 83 | 840058083 | SKF | Winergy
Camp Springs I | 84 | 840058084 | SKF | Winergy
Camp Springs I | 85 | 840058085 | SKF | Winergy
Camp Springs I | 86 | 840058086 | SKF | Winergy
Camp Springs I | 87 | 840058087 | SKF | Replacement Pending
Stanton | 1 | 840078001 |  | GETS
Stanton | 2 | 840078002 | SKF | Moventas
Stanton | 3 | 840078003 | FAG | Moventas
Stanton | 4 | 840078004 | Timken | Nanjing
Stanton | 5 | 840078005 | SKF | Moventas
Stanton | 6 | 840078006 | SKF | Winergy
Stanton | 7 | 840078007 | Timken | GETS
Stanton | 8 | 840078008 | SKF | Winergy
Stanton | 9 | 840078009 | Timken | GETS
Stanton | 10 | 840078010 | Timken | GETS
Stanton | 11 | 840078011 | SKF | Moventas
Stanton | 12 | 840078012 | Timken | GETS
Stanton | 13 | 840078013 | FAG | Moventas
Stanton | 14 | 840078014 | SKF | Moventas
Stanton | 15 | 840078015 | FAG | Nanjing
Stanton | 16 | 840078016 | SKF | Nanjing
Stanton | 17 | 840078017 |  | GETS
Stanton | 18 | 840078018 |  | GETS
Stanton | 19 | 840078019 |  | GETS
Stanton | 20 | 840078020 | Replacement Pending | ZF
Stanton | 21 | 840078021 | SKF | Rexroth
Stanton | 22 | 840078022
Stanton | 23 | 840078023 |  | Rexroth
Stanton | 24 | 840078024 | FAG | Moventas
Stanton | 25 | 840078025 | SKF | Winergy
Stanton | 26 | 840078026 |  | Rexroth
Stanton | 27 | 840078027 |  | Winergy
Stanton | 28 | 840078028 |  | GETS
Stanton | 29 | 840078029 | SKF | Rexroth
Stanton | 30 | 840078030 | SKF | Winergy
Stanton | 31 | 840078031 |  | GETS
Stanton | 32 | 840078032 | SKF | Winergy
Stanton | 33 | 840078033 | SKF | Rexroth
Stanton | 34 | 840078034 | SKF | Rexroth
Stanton | 35 | 840078035 |  | Rexroth
Stanton | 36 | 840078036 | Replacement Pending | Winergy
Stanton | 37 | 840078037 | SKF | Rexroth
Stanton | 38 | 840078038 | Timken | Nanjing
Stanton | 39 | 840078039 | FAG | Moventas
Stanton | 40 | 840078040 | SKF | Moventas
Stanton | 41 | 840078041 | FAG | Moventas
Stanton | 42 | 840078042 | FAG | Moventas
Stanton | 43 | 840078043 | SKF | GETS
Stanton | 44 | 840078044 | Replacement Pending | Moventas
Stanton | 45 | 840078045 | SKF | Moventas
Stanton | 46 | 840078046 | SKF | Moventas
Stanton | 47 | 840078047 | SKF | Moventas
Stanton | 48 | 840078048 | SKF | Moventas
Stanton | 49 | 840078049 | SKF | Moventas
Stanton | 50 | 840078050 | SKF | Winergy
Stanton | 51 | 840078051 | SKF | Winergy
Stanton | 52 | 840078052 | SKF | Moventas
Stanton | 53 | 840078053 | SKF | Moventas
Stanton | 54 | 840078054 | SKF | Moventas
Stanton | 55 | 840078055 | SKF | Moventas
Stanton | 56 | 840078056 | SKF | Moventas
Stanton | 57 | 840078057 | Timken | Winergy
Stanton | 58 | 840078058 | SKF | Rexroth
Stanton | 59 | 840078059 | FAG | Moventas
Stanton | 60 | 840078060 | SKF | Winergy
Stanton | 61 | 840078061 | SKF | Winergy
Stanton | 62 | 840078062 | SKF | Moventas
Stanton | 63 | 840078063 | SKF | Winergy
Stanton | 64 | 840078064 | SKF | Winergy
Stanton | 65 | 840078065 | Timken | Moventas
Stanton | 66 | 840078066 | SKF | Winergy
Stanton | 67 | 840078067 | SKF | Winergy
Stanton | 68 | 840078068 | SKF | Winergy
Stanton | 69 | 840078069 | Timken | Winergy
Stanton | 70 | 840078070 | FAG | Winergy
Stanton | 71 | 840078071 | SKF | Winergy
Stanton | 72 | 840078072 | SKF | Winergy
Stanton | 73 | 840078073 | FAG | Winergy
Stanton | 74 | 840078074 | FAG | Winergy
Stanton | 75 | 840078075 |  | Winergy
Stanton | 76 | 840078076 | Timken | Nanjing
Stanton | 77 | 840078077 |  | Rexroth
Stanton | 78 | 840078078 | SKF | Winergy
Stanton | 79 | 840078079 |  | GETS
Stanton | 80 | 840078080 |  | Rexroth
Forward | 1 | 840079001 |  | Winergy
Forward | 2C | 840079002 | Timken | Winergy
Forward | 3A | 840079003 | FAG | Winergy
Forward | 4 | 840079004 | NTN | Winergy
Forward | 6 | 840079006 | NTN | Winergy
Forward | 7 | 840079007 | NTN | Winergy
Forward | 8 | 840079008 | Koyo | Winergy
Forward | 9 | 840079009 | SKF | Winergy
Forward | 10 | 840079010 | SKF | Winergy
Forward | 11 | 840079011 | NTN | Winergy
Forward | 12 | 840079012 | Timken | Winergy
Forward | 13 | 840079013 | Koyo | Moventas
Forward | 16 | 840079016 | Timken | Winergy
Forward | 17 | 840079017 | FAG | Winergy
Forward | 18 | 840079018 |  | Winergy
Forward | 19A | 840079019 | FAG | Rexroth
Forward | 20 | 840079020 | Timken | Winergy
Forward | 21 | 840079021 | NTN | Winergy
Forward | 22 | 840079022 | NTN | Winergy
Forward | 23A | 840079023 | SKF | Winergy
Forward | 24 | 840079024 | Timken | Winergy
Forward | 25 | 840079025 | Timken | Winergy
Forward | 26 | 840079026 | Timken | Winergy
Forward | 27 | 840079027 | NTN | Winergy
Forward | 28 | 840079028 | SKF | Winergy
Forward | 29A | 840079029 | Timken | Winergy
Forward | 30 | 840079030 |  | Winergy
Forward | 31 | 840079031 | Timken | Moventas
Forward | 32 | 840079032 | SKF | Winergy
Forward | 33 | 840079033 | NTN | Winergy
Forward | 34 | 840079034 | Timken | Winergy
Forward | 35 | 840079035 | Timken | Winergy
Forward | 36 | 840079036 | NTN | Winergy
Forward | 37 | 840079037 | NTN | Winergy
Forward | 38 | 840079038 | FAG | Moventas
Forward | 39 | 840079039 | SKF | Winergy
Forward | 40A | 840079040 | Timken | Nanjing
Forward | 41A | 840079041 | Timken | Winergy
Forward | 42 | 840079042 |  | Moventas
Forward | 43 | 840079043 | SKF | Winergy
Forward | 44 | 840079044 | NTN | Winergy
Forward | 45 | 840079045 | FAG | Winergy
Forward | 46 | 840079046 | FAG | Moventas
Forward | 47 | 840079047 | SKF | Winergy
Forward | 48 | 840079048 | SKF | Winergy
Forward | 49A | 840079049 | SKF | Winergy
Forward | 50 | 840079050 | SKF | Winergy
Forward | 53 | 840079053 | FAG | Winergy
Forward | 55A | 840079055 | FAG | Winergy
Forward | 56A | 840079056 | SKF | Winergy
Forward | 57 | 840079057 | Timken | Winergy
Forward | 58 | 840079058 | Timken | Winergy
Forward | 59A | 840079059 | SKF | Winergy
Forward | 60A | 840079060 |  | Winergy
Forward | 61 | 840079061 | SKF | Winergy
Forward | 62 | 840079062 | SKF | Moventas
Forward | 63A | 840079063 |  | Winergy
Forward | 65 | 840079065 | SKF | Moventas
Forward | 66 | 840079066 | FAG | Winergy
Forward | 70 | 840079070 | Timken | Winergy
Forward | 71A | 840079071 | Timken | Winergy
Forward | 72A | 840079072 |  | Winergy
Forward | 73 | 840079073 | NTN | Moventas
Forward | 74A | 840079074 | Timken | Winergy
Forward | 75B | 840079075 | SKF | Winergy
Forward | 81 | 840079081 | Timken | Winergy
Forward | 82 | 840079082 | NTN | Winergy
Forward | 83 | 840079083 | SKF | Winergy
Forward | 84 | 840079084 | SKF | Moventas
Forward | 85 | 840079085 | Timken | Winergy
Forward | 86 | 840079086 | NTN | Winergy
Forward | 87 | 840079087 | SKF | Winergy
Forward | 89 | 840079089 | SKF | Winergy
Forward | 90 | 840079090 | SKF | Winergy
Forward | 95 | 840079095 | Timken | Winergy
Forward | 96 | 840079096 | Timken | Winergy
Forward | 97 | 840079097 | SKF | Winergy
Forward | 98 | 840079098 | SKF | Winergy
Forward | 107 | 840079107 | SKF | Winergy
Forward | 203 | 840079203 | Timken | Winergy
Forward | 204 | 840079204 |  | Winergy
Forward | 205 | 840079205 | SKF | Winergy
Forward | 210A | 840079210 | SKF | Winergy
Forward | 211A | 840079211 | SKF | Winergy
Forward | 212 | 840079212 | Timken | Winergy
Camp Springs II | 101 | 840083001 | SKF | Moventas
Camp Springs II | 102 | 840083002 | SKF | Winergy
Camp Springs II | 103 | 840083003 | Koyo | Winergy
Camp Springs II | 104 | 840083004 | SKF | Winergy
Camp Springs II | 105 | 840083005 | SKF | Winergy
Camp Springs II | 106 | 840083006 | SKF | GETS
Camp Springs II | 107 | 840083007 | FAG | Winergy
Camp Springs II | 108 | 840083008 | SKF | Rexroth
Camp Springs II | 109 | 840083009 | SKF | Winergy
Camp Springs II | 110 | 840083010 | FAG | Replacement Pending
Camp Springs II | 111 | 840083011 | FAG | GETS
Camp Springs II | 112 | 840083012 | FAG | Winergy
Camp Springs II | 113 | 840083013 | Timken | GETS
Camp Springs II | 114 | 840083014 | FAG | Winergy
Camp Springs II | 115 | 840083015 | SKF | Winergy
Camp Springs II | 116 | 840083016 | SKF | Winergy
Camp Springs II | 117 | 840083017 | Replacement Pending | Winergy
Camp Springs II | 118 | 840083018 | FAG | Winergy
Camp Springs II | 119 | 840083019 | FAG | Winergy
Camp Springs II | 120 | 840083020 | Timken | Winergy
Camp Springs II | 121 | 840083021 | SKF | Rexroth
Camp Springs II | 122 | 840083022 | FAG | Winergy
Camp Springs II | 123 | 840083023 | Replacement Pending | Moventas
Camp Springs II | 124 | 840083024 | SKF | Winergy
Camp Springs II | 125 | 840083025 | Koyo | Winergy
Camp Springs II | 126 | 840083026 | Koyo | Winergy
Camp Springs II | 127 | 840083027 | FAG | Winergy
Camp Springs II | 128 | 840083028 | FAG | Winergy
Camp Springs II | 129 | 840083029 | SKF | Winergy
Camp Springs II | 130 | 840083030 | Koyo | Moventas
Camp Springs II | 131 | 840083031 | SKF | Winergy
Camp Springs II | 132 | 840083032 | Timken | Replacement Pending
Camp Springs II | 133 | 840083033 | SKF | Rexroth
Camp Springs II | 134 | 840083034 | NTN | Replacement Pending
Camp Springs II | 135 | 840083035 | NTN
Camp Springs II | 136 | 840083036 | NTN | Winergy
Camp Springs II | 137 | 840083037 | SKF | Winergy
Camp Springs II | 138 | 840083038 | SKF | Rexroth
Camp Springs II | 139 | 840083039 | SKF | Winergy
Camp Springs II | 140 | 840083040 |  | Winergy
Camp Springs II | 141 | 840083041 | Koyo | Rexroth
Camp Springs II | 142 | 840083042 | Koyo | Winergy
Camp Springs II | 143 | 840083043 |  | Winergy
Camp Springs II | 144 | 840083044 | SKF | Winergy
Camp Springs II | 145 | 840083045 | Timken | Moventas
Camp Springs II | 146 | 840083046 | Koyo | Moventas
Camp Springs II | 147 | 840083047 | Replacement Pending | Winergy
Camp Springs II | 148 | 840083048 | Replacement Pending | Winergy
Camp Springs II | 149 | 840083049 | FAG | GETS
Camp Springs II | 150 | 840083050 | Koyo | GETS
Camp Springs II | 151 | 840083051 | FAG | Replacement Pending
Camp Springs II | 152 | 840083052 | FAG | Winergy
Camp Springs II | 153 | 840083053 | FAG | Winergy
Camp Springs II | 154 | 840083054 | NTN | Moventas
Camp Springs II | 155 | 840083055 | SKF | Moventas
Camp Springs II | 156 | 840083056 | Replacement Pending | Moventas
Camp Springs II | 157 | 840083057 | Replacement Pending | Winergy
Camp Springs II | 158 | 840083058 | Timken | Winergy
Camp Springs II | 159 | 840083059 | FAG | Winergy
Camp Springs II | 160 | 840083060 | Koyo | Moventas
Camp Springs II | 161 | 840083061 | NTN | Moventas
Camp Springs II | 162 | 840083062 | NTN | Moventas
Camp Springs II | 163 | 840083063 | FAG | Winergy
Camp Springs II | 164 | 840083064 | Replacement Pending | Winergy
Camp Springs II | 165 | 840083065 | Timken | Rexroth
Camp Springs II | 166 | 840083066 | FAG | Winergy
Camp Springs II | 167 | 840083067 | Pending Repair Report | Winergy
Camp Springs II | 168 | 840083068 | FAG | Winergy
Camp Springs II | 169 | 840083069 | SKF | Winergy
Camp Springs II | 170 | 840083070 | FAG | Winergy
Camp Springs II | 171 | 840083071 | FAG | Winergy
Camp Springs II | 172 | 840083072 | FAG | Winergy
Camp Springs II | 173 | 840083073 | FAG | Winergy
Camp Springs II | 174 | 840083074 | FAG | Winergy
Camp Springs II | 175 | 840083075 | SKF | Winergy
Camp Springs II | 176 | 840083076 | NTN | Moventas
Camp Springs II | 177 | 840083077 | Timken | Winergy
Camp Springs II | 178 | 840083078 | SKF | Winergy
Camp Springs II | 179 | 840083079 | FAG | Winergy
Camp Springs II | 180 | 840083080 | FAG | Winergy
McAdoo | 1 | 840084001 | Pending Repair Report | Moventas
McAdoo | 2 | 840084002 | Timken | Winergy
McAdoo | 3 | 840084003 | NTN | Winergy
McAdoo | 4 | 840084004 | NTN | Moventas
McAdoo | 5 | 840084005 | NTN | Winergy
McAdoo | 6 | 840084006 | Timken | Winergy
McAdoo | 7 | 840084007 | Timken | GETS
McAdoo | 8 | 840084008 | SKF
McAdoo | 9 | 840084009 | SKF | GETS
McAdoo | 10 | 840084010 | Timken | Pending Repair Report
McAdoo | 11 | 840084011 | NTN | Winergy
McAdoo | 12 | 840084012 | SKF | Rexroth
McAdoo | 13 | 840084013 | SKF | Rexroth
McAdoo | 14 | 840084014 | NTN | ZF
McAdoo | 15 | 840084015 | SKF | Moventas
McAdoo | 16 | 840084016 | SKF | Rexroth
McAdoo | 17 | 840084017 | SKF | Pending Repair Report
McAdoo | 18 | 840084018 | SKF | Rexroth
McAdoo | 19 | 840084019 | Replacement Pending | Winergy
McAdoo | 20 | 840084020 | NTN | Moventas
McAdoo | 21 | 840084021 | SKF | GETS
McAdoo | 22 | 840084022 | SKF | GETS
McAdoo | 23 | 840084023 | Koyo | Moventas
McAdoo | 24 | 840084024 | NTN | Winergy
McAdoo | 25 | 840084025 | SKF | Replacement Pending
McAdoo | 26 | 840084026 | SKF | Winergy
McAdoo | 27 | 840084027 | SKF
McAdoo | 28 | 840084028 | Koyo | Moventas
McAdoo | 29 | 840084029 | NTN | Winergy
McAdoo | 30 | 840084030 | Timken | Winergy
McAdoo | 31 | 840084031 | SKF | Winergy
McAdoo | 32 | 840084032 | SKF | GETS
McAdoo | 33 | 840084033 | SKF | GETS
McAdoo | 34 | 840084034 | NTN | Winergy
McAdoo | 35 | 840084035 | NTN | Winergy
McAdoo | 36 | 840084036 | NTN | Winergy
McAdoo | 37 | 840084037 | NTN | Winergy
McAdoo | 38 | 840084038 | Pending Repair Report | Winergy
McAdoo | 39 | 840084039 | Koyo | Moventas
McAdoo | 40 | 840084040 | SKF | Rexroth
McAdoo | 41 | 840084041 | SKF | Winergy
McAdoo | 42 | 840084042 | Timken | Pending Repair Report
McAdoo | 43 | 840084043 | SKF | Winergy
McAdoo | 44 | 840084044 | SKF | GETS
McAdoo | 45 | 840084045 | SKF | Winergy
McAdoo | 46 | 840084046 | Timken | Winergy
McAdoo | 47 | 840084047 | Timken | Rexroth
McAdoo | 48 | 840084048 | Timken | Winergy
McAdoo | 49 | 840084049 | SKF | Rexroth
McAdoo | 50 | 840084050 | SKF | Rexroth
McAdoo | 51 | 840084051 | SKF | Rexroth
McAdoo | 52 | 840084052 | SKF | Rexroth
McAdoo | 53 | 840084053 | SKF | Winergy
McAdoo | 54 | 840084054 | Pending Repair Report | Rexroth
McAdoo | 55 | 840084055 | SKF | Winergy
McAdoo | 56 | 840084056 | NTN | Moventas
McAdoo | 57 | 840084057 |  | Rexroth
McAdoo | 58 | 840084058 | SKF | GETS
McAdoo | 59 | 840084059 | SKF | Winergy
McAdoo | 60 | 840084060 | SKF | Rexroth
McAdoo | 61 | 840084061 | NTN | Moventas
McAdoo | 62 | 840084062 | SKF | GETS
McAdoo | 63 | 840084063 | Timken | Winergy
McAdoo | 64 | 840084064 | SKF | Winergy
McAdoo | 65 | 840084065 | Koyo | Winergy
McAdoo | 66 | 840084066 | Koyo | Winergy
McAdoo | 67 | 840084067 | NTN | Moventas
McAdoo | 68 | 840084068 | NTN | Winergy
McAdoo | 69 | 840084069 | NTN | GETS
McAdoo | 70 | 840084070 | Koyo | Winergy
McAdoo | 71 | 840084071 | SKF | Nanjing
McAdoo | 72 | 840084072 | SKF | GETS
McAdoo | 73 | 840084073 | SKF | Winergy
McAdoo | 74 | 840084074 | SKF | Nanjing
McAdoo | 75 | 840084075 | SKF | GETS
McAdoo | 76 | 840084076 | Timken | GETS
McAdoo | 77 | 840084077 | Pending Repair Report | Winergy
McAdoo | 78 | 840084078 | SKF | Winergy
McAdoo | 79 | 840084079 | Koyo | Winergy
McAdoo | 80 | 840084080 | SKF | Winergy
McAdoo | 81 | 840084081 | SKF | Winergy
McAdoo | 82 | 840084082 | Koyo | Winergy
McAdoo | 83 | 840084083 | Koyo | Winergy
McAdoo | 84 | 840084084 | Koyo | Winergy
McAdoo | 85 | 840084085 | Pending Repair Report | Winergy
McAdoo | 86 | 840084086 | Koyo | Winergy
McAdoo | 87 | 840084087 | Koyo | Replacement Pending
McAdoo | 88 | 840084088 | SKF | GETS
McAdoo | 89 | 840084089 | SKF | Rexroth
McAdoo | 90 | 840084090 | SKF | GETS
McAdoo | 91 | 840084091 | SKF | Nanjing
McAdoo | 92 | 840084092 | Koyo | Winergy
McAdoo | 93 | 840084093 | Koyo | Winergy
McAdoo | 94 | 840084094 | SKF | Winergy
McAdoo | 95 | 840084095 | Koyo | Winergy
McAdoo | 96 | 840084096 | Koyo | Moventas
McAdoo | 97 | 840084097 | Timken | Winergy
McAdoo | 98 | 840084098 | NTN | Rexroth
McAdoo | 99 | 840084099 | SKF | GETS
McAdoo | 100 | 840084100 | SKF | Moventas
Willow Creek | 1 | 840094001 | Koyo | Winergy
Willow Creek | 2 | 840094002 | Koyo | Winergy
Willow Creek | 3 | 840094003 | NTN | Winergy
Willow Creek | 4 | 840094004 | NTN | Winergy
Willow Creek | 5 | 840094005 | NTN | Winergy
Willow Creek | 6 | 840094006 | Timken
Willow Creek | 7 | 840094007 | Koyo | Winergy
Willow Creek | 8 | 840094008 | FAG | Moventas
Willow Creek | 9 | 840094009 | FAG | Moventas
Willow Creek | 10 | 840094010 | Koyo | Moventas
Willow Creek | 11 | 840094011 | FAG | Moventas
Willow Creek | 12 | 840094012 | Koyo | Moventas
Willow Creek | 13 | 840094013 | NTN | Moventas
Willow Creek | 14 | 840094014 | NTN | Moventas
Willow Creek | 15 | 840094015 | Koyo | Moventas
Willow Creek | 16 | 840094016 | NTN | Moventas
Willow Creek | 17 | 840094017 | NTN | Moventas
Willow Creek | 18 | 840094018 | Koyo | Winergy
Willow Creek | 19 | 840094019 | NTN | Moventas
Willow Creek | 20 | 840094020 | NTN | Moventas
Willow Creek | 21 | 840094021 | NTN | Winergy
Willow Creek | 22 | 840094022 | NTN | Rexroth
Willow Creek | 23 | 840094023 | NTN | Nanjing
Willow Creek | 24 | 840094024 | NTN | Moventas
Willow Creek | 25 | 840094025 | NTN | Winergy
Willow Creek | 26 | 840094026 | NTN | Winergy
Willow Creek | 27 | 840094027 | NTN | Moventas
Willow Creek | 28 | 840094028 | NTN | Moventas
Willow Creek | 29 | 840094029 | Timken | Moventas
Willow Creek | 30 | 840094030 | NTN | Moventas
Willow Creek | 31 | 840094031 | Koyo | Winergy
Willow Creek | 32 | 840094032 | Koyo | Winergy
Willow Creek | 33 | 840094033 | Koyo | Winergy
Willow Creek | 34 | 840094034 | NTN | Winergy
Willow Creek | 35 | 840094035 | Koyo | Winergy
Willow Creek | 36 | 840094036 | Koyo | Moventas
Willow Creek | 37 | 840094037 | Koyo | Winergy
Willow Creek | 38 | 840094038 | Koyo | Winergy
Willow Creek | 39 | 840094039 | SKF | GETS
Willow Creek | 40 | 840094040 | NTN | Rexroth
Willow Creek | 41 | 840094041 | SKF | Winergy
Willow Creek | 42 | 840094042 | NTN | Rexroth
Willow Creek | 43 | 840094043 | SKF
Willow Creek | 44 | 840094044 | SKF | Winergy
Willow Creek | 45 | 840094045 | NTN | Rexroth
Willow Creek | 46 | 840094046 | NTN | Winergy
Willow Creek | 47 | 840094047 | Timken | Winergy
Willow Creek | 48 | 840094048 | SKF | Winergy
Grand Ridge I | 1 | 840095001 | SKF | Winergy
Grand Ridge I | 2 | 840095002 | Koyo | Winergy
Grand Ridge I | 3 | 840095003 | Timken | Winergy
Grand Ridge I | 4 | 840095004 | Koyo | Winergy
Grand Ridge I | 5 | 840095005 | Koyo | Winergy
Grand Ridge I | 6 | 840095006 | SKF | Winergy
Grand Ridge I | 7 | 840095007 | Koyo | Winergy
Grand Ridge I | 8 | 840095008 | Timken | Winergy
Grand Ridge I | 9 | 840095009 | FAG | Winergy
Grand Ridge I | 10 | 840095010 | Timken | Winergy
Grand Ridge I | 11 | 840095011 | Koyo | Rexroth
Grand Ridge I | 12 | 840095012 | SKF | Winergy
Grand Ridge I | 13 | 840095013 | Timken | Nanjing
Grand Ridge I | 14 | 840095014 | Timken | Moventas
Grand Ridge I | 15 | 840095015 | Timken | Winergy
Grand Ridge I | 16 | 840095016 |  | Winergy
Grand Ridge I | 17 | 840095017 |  | Moventas
Grand Ridge I | 18 | 840095018 | SKF | Moventas
Grand Ridge I | 19 | 840095019 | SKF | Winergy
Grand Ridge I | 20 | 840095020 | Timken | Nanjing
Grand Ridge I | 21 | 840095021 |  | Moventas
Grand Ridge II | 22 | 840095022 |  | Moventas
Grand Ridge II | 23 | 840095023 |  | GETS
Grand Ridge I | 24 | 840095024 | SKF | Winergy
Grand Ridge I | 25 | 840095025 | SKF | Moventas
Grand Ridge I | 26 | 840095026 | Koyo | Winergy
Grand Ridge I | 27 | 840095027 | Koyo | Nanjing
Grand Ridge I | 28 | 840095028 | Koyo | Winergy
Grand Ridge I | 29 | 840095029 |  | Rexroth
Grand Ridge I | 30 | 840095030 | SKF | Winergy
Grand Ridge I | 31 | 840095031 | SKF | Moventas
Grand Ridge I | 32 | 840095032 | Koyo | Rexroth
Grand Ridge I | 33 | 840095033 | Koyo | Winergy
Grand Ridge I | 34 | 840095034 | Koyo | Rexroth
Grand Ridge I | 35 | 840095035 | SKF | Winergy
Grand Ridge I | 36 | 840095036 |  | Moventas
Grand Ridge I | 37 | 840095037 | SKF | Rexroth
Grand Ridge I | 38 | 840095038 | SKF | Winergy
Grand Ridge I | 39 | 840095039 | Koyo | Winergy
Grand Ridge I | 40 | 840095040 | Koyo | Rexroth
Grand Ridge I | 41 | 840095041 | NTN | Winergy
Grand Ridge I | 42 | 840095042 | SKF | Winergy
Grand Ridge I | 43 | 840095043 | SKF
Grand Ridge I | 44 | 840095044 | Timken | Winergy
Grand Ridge I | 45 | 840095045 | SKF | Winergy
Grand Ridge I | 46 | 840095046 |  | Winergy
Grand Ridge I | 47 | 840095047 | SKF | Winergy
Grand Ridge I | 48 | 840095048 | NTN | Winergy
Grand Ridge I | 49 | 840095049 | SKF | Winergy
Grand Ridge I | 50 | 840095050 | SKF | Winergy
Grand Ridge I | 51 | 840095051 | Koyo | Winergy
Grand Ridge I | 52 | 840095052 | Koyo | Rexroth
Grand Ridge I | 53 | 840095053 | SKF | Rexroth
Grand Ridge I | 54 | 840095054 | Koyo | Winergy
Grand Ridge I | 55 | 840095055 | Koyo
Grand Ridge I | 56 | 840095056 | Timken | Winergy
Grand Ridge I | 57 | 840095057 | Koyo | Rexroth
Grand Ridge I | 58 | 840095058 | Koyo | Winergy
Grand Ridge I | 59 | 840095059 | Koyo | Rexroth
Grand Ridge I | 60 | 840095060 | Koyo | Winergy
Grand Ridge I | 61 | 840095061 | Timken | Nanjing
Grand Ridge I | 62 | 840095062 | SKF | Winergy
Grand Ridge I | 63 | 840095063 | SKF | Winergy
Grand Ridge I | 64 | 840095064 | Timken | Winergy
Grand Ridge I | 65 | 840095065 | SKF | Moventas
Grand Ridge I | 66 | 840095066 | FAG | Winergy
Grand Ridge I | 67 | 840095067 | SKF | Winergy
Grand Ridge I | 68 | 840095068 | Koyo | Winergy
Grand Ridge II | 69 | 840095069 |  | Winergy
Grand Ridge II | 70 | 840095070 | FAG | GETS
Grand Ridge II | 71 | 840095071 | FAG | GETS
Grand Ridge II | 72 | 840095072 | SKF | Winergy
Grand Ridge II | 73 | 840095073 |  | Winergy
Grand Ridge II | 74 | 840095074 | SKF | Winergy
Grand Ridge II | 75 | 840095075 |  | Winergy
Grand Ridge II | 76 | 840095076 |  | Nanjing
Grand Ridge II | 77 | 840095077 |  | Winergy
Grand Ridge II | 78 | 840095078 | SKF | Winergy
Grand Ridge II | 79 | 840095079 | Pending Repair Report | Winergy
Grand Ridge II | 80 | 840095080 |  | Winergy
Grand Ridge II | 81 | 840095081 |  | Winergy
Grand Ridge II | 82 | 840095082 | Timken | Winergy
Grand Ridge II | 83 | 840095083 | Timken | Winergy
Grand Ridge II | 84 | 840095084 | Timken | Nanjing
Grand Ridge II | 85 | 840095085 | Timken | GETS
Grand Ridge II | 86 | 840095086 |  | Winergy
Grand Ridge II | 87 | 840095087 | FAG | GETS
Grand Ridge II | 88 | 840095088 |  | Winergy
Grand Ridge II | 89 | 840095089 |  | Winergy
Grand Ridge II | 90 | 840095090 |  | GETS
Grand Ridge II | 91 | 840095091 |  | Winergy
Grand Ridge II | 92 | 840095092 |  | Winergy
Grand Ridge II | 93 | 840095093 |  | Winergy
Grand Ridge II | 94 | 840095094 |  | Winergy
Grand Ridge II | 95 | 840095095 |  | Winergy
Grand Ridge II | 96 | 840095096 | Timken | GETS
Grand Ridge II | 97 | 840095097 |  | Winergy
Grand Ridge II | 98 | 840095098 | Timken | Winergy
Grand Ridge II | 99 | 840095099 |  | Winergy
Grand Ridge II | 100 | 840095100 |  | Winergy
Grand Ridge III | 101 | 840095101 |  | Winergy
Grand Ridge III | 102 | 840095102 |  | Winergy
Grand Ridge III | 103 | 840095103 |  | Winergy
Grand Ridge III | 104 | 840095104 | Timken | Winergy
Grand Ridge III | 105 | 840095105 |  | Winergy
Grand Ridge III | 106 | 840095106 |  | GETS
Grand Ridge III | 107 | 840095107 |  | GETS
Grand Ridge III | 108 | 840095108 |  | Winergy
Grand Ridge III | 109 | 840095109 | Timken | Winergy
Grand Ridge III | 110 | 840095110 |  | Winergy
Grand Ridge III | 111 | 840095111 |  | GETS
Grand Ridge III | 112 | 840095112 | Timken | GETS
Grand Ridge III | 113 | 840095113 |  | Winergy
Grand Ridge III | 114 | 840095114 |  | Replacement Pending
Grand Ridge III | 115 | 840095115 |  | Winergy
Grand Ridge III | 116 | 840095116 | Timken | GETS
Grand Ridge III | 117 | 840095117 |  | Winergy
Grand Ridge III | 118 | 840095118 |  | GETS
Grand Ridge III | 119 | 840095119 |  | Nanjing
Grand Ridge III | 120 | 840095120 |  | Winergy
Grand Ridge III | 121 | 840095121 | FAG | Winergy
Grand Ridge III | 122 | 840095122 |  | Winergy
Grand Ridge III | 123 | 840095123 |  | Winergy
Grand Ridge III | 124 | 840095124 |  | Winergy
Grand Ridge III | 125 | 840095125 |  | NGC
Grand Ridge III | 126 | 840095126 |  | Winergy
Grand Ridge III | 127 | 840095127 |  | Winergy
Grand Ridge III | 128 | 840095128 |  | Winergy
Grand Ridge III | 129 | 840095129 | Timken | Winergy
Grand Ridge III | 130 | 840095130 |  | Winergy
Grand Ridge III | 131 | 840095131 |  | Winergy
Grand Ridge III | 132 | 840095132 | Timken | GETS
Grand Ridge III | 133 | 840095133 |  | Winergy
Grand Ridge IV | 134 | 840095134 | Timken | Winergy
Grand Ridge IV | 135 | 840095135 |  | Winergy
Grand Ridge IV | 136 | 840095136 |  | Winergy
Grand Ridge IV | 137 | 840095137 | SKF | Winergy
Grand Ridge IV | 138 | 840095138 |  | Winergy
Grand Ridge IV | 139 | 840095139 | Timken | Winergy
Grand Ridge IV | 140 | 840095140 | Timken | Winergy
Turkey Track | 1 | 840098001 | Timken | Winergy
Turkey Track | 2 | 840098002 | Timken | Winergy
Turkey Track | 3 | 840098003 | SKF | Winergy
Turkey Track | 4 | 840098004 | SKF | Winergy
Turkey Track | 5 | 840098005 |  | Winergy
Turkey Track | 6 | 840098006 | SKF | Winergy
Turkey Track | 7 | 840098007 | SKF | Moventas
Turkey Track | 8 | 840098008 | SKF | Winergy
Turkey Track | 9 | 840098009 | SKF | Moventas
Turkey Track | 10 | 840098010 | SKF | Winergy
Turkey Track | 11 | 840098011 | SKF | GETS
Turkey Track | 12 | 840098012 | Timken | Moventas
Turkey Track | 13 | 840098013 | SKF | Moventas
Turkey Track | 14 | 840098014 | SKF | Moventas
Turkey Track | 15 | 840098015 | SKF | Moventas
Turkey Track | 16 | 840098016 | SKF | Moventas
Turkey Track | 17 | 840098017 | SKF | Moventas
Turkey Track | 18 | 840098018 | SKF | Moventas
Turkey Track | 19 | 840098019 | SKF | Moventas
Turkey Track | 20 | 840098020 | SKF | Winergy
Turkey Track | 21 | 840098021 | SKF | Moventas
Turkey Track | 22 | 840098022 | SKF | Moventas
Turkey Track | 23 | 840098023 | Timken | GETS
Turkey Track | 24 | 840098024 | Timken | Winergy
Turkey Track | 25 | 840098025 | SKF | Winergy
Turkey Track | 26 | 840098026 | SKF | Moventas
Turkey Track | 27 | 840098027 | SKF | Moventas
Turkey Track | 28 | 840098028 | NTN | Rexroth
Turkey Track | 29 | 840098029 | SKF | Winergy
Turkey Track | 30 | 840098030 | Koyo | Moventas
Turkey Track | 31 | 840098031 | SKF | Moventas
Turkey Track | 32 | 840098032 | FAG | Moventas
Turkey Track | 33 | 840098033 |  | Moventas
Turkey Track | 34 | 840098034 | Koyo | Moventas
Turkey Track | 35 | 840098035 | SKF | Moventas
Turkey Track | 36 | 840098036 | Koyo | Moventas
Turkey Track | 37 | 840098037 | SKF | Moventas
Turkey Track | 38 | 840098038 | SKF | Moventas
Turkey Track | 39 | 840098039 | SKF | Moventas
Turkey Track | 40 | 840098040 | SKF | Moventas
Turkey Track | 41 | 840098041 | Timken | Moventas
Turkey Track | 42 | 840098042 | SKF | Moventas
Turkey Track | 43 | 840098043 | SKF | Moventas
Turkey Track | 44 | 840098044 | Timken | GETS
Turkey Track | 45 | 840098045 | SKF | Moventas
Turkey Track | 46 | 840098046 | Timken | GETS
Turkey Track | 47 | 840098047 | SKF | Moventas
Turkey Track | 48 | 840098048 | Timken | GETS
Turkey Track | 49 | 840098049 | SKF | Moventas
Turkey Track | 50 | 840098050 | FAG | Winergy
Turkey Track | 51 | 840098051 | SKF | Moventas
Turkey Track | 52 | 840098052 | SKF | Winergy
Turkey Track | 53 | 840098053 | SKF | Winergy
Turkey Track | 54 | 840098054 | SKF | Moventas
Turkey Track | 55 | 840098055 | FAG | Winergy
Turkey Track | 56 | 840098056 | Timken | GETS
Turkey Track | 57 | 840098057 | SKF | Replacement Pending
Turkey Track | 58 | 840098058 | SKF | Winergy
Turkey Track | 59 | 840098059 | SKF | Winergy
Turkey Track | 60 | 840098060 | SKF | Winergy
Turkey Track | 61 | 840098061 | SKF | Winergy
Turkey Track | 62 | 840098062 | SKF | Winergy
Turkey Track | 63 | 840098063 | Timken | Moventas
Turkey Track | 64 | 840098064 | SKF | Moventas
Turkey Track | 65 | 840098065 | SKF | Moventas
Turkey Track | 66 | 840098066 | SKF | Winergy
Turkey Track | 67 | 840098067 | SKF | Winergy
Turkey Track | 68 | 840098068 | Koyo
Turkey Track | 69 | 840098069 | Koyo | Moventas
Turkey Track | 70 | 840098070 | SKF | Moventas
Turkey Track | 71 | 840098071 | Replacement Pending | Winergy
Turkey Track | 72 | 840098072 |  | Moventas
Turkey Track | 73 | 840098073 | SKF | Moventas
Turkey Track | 74 | 840098074 | Koyo | Moventas
Turkey Track | 75 | 840098075 | SKF | Moventas
Turkey Track | 76 | 840098076 | SKF | Moventas
Turkey Track | 77 | 840098077 | SKF | Moventas
Turkey Track | 78 | 840098078 | SKF | Nanjing
Turkey Track | 79 | 840098079 | Koyo | Moventas
Turkey Track | 80 | 840098080 |  | Moventas
Turkey Track | 81 | 840098081 | Koyo | Moventas
Turkey Track | 82 | 840098082 | Koyo | Moventas
Turkey Track | 83 | 840098083 | SKF | Winergy
Turkey Track | 84 | 840098084 | Replacement Pending | Nanjing
Turkey Track | 85 | 840098085 | SKF | Winergy
Turkey Track | 86 | 840098086 | Koyo | Moventas
Turkey Track | 87 | 840098087 | Timken | GETS
Turkey Track | 88 | 840098088 | SKF | Winergy
Turkey Track | 89 | 840098089 | SKF | Moventas
Turkey Track | 90 | 840098090 | SKF | Moventas
Turkey Track | 91 | 840098091 | Replacement Pending | Pending Repair Report
Turkey Track | 92 | 840098092 | Timken | Winergy
Turkey Track | 93 | 840098093 | SKF | Winergy
Turkey Track | 94 | 840098094 | Timken | Winergy
Turkey Track | 95 | 840098095 | Timken | GETS
Turkey Track | 96 | 840098096 | Timken | Moventas
Turkey Track | 97 | 840098097 | SKF | GETS
Turkey Track | 98 | 840098098 | SKF | Winergy
Turkey Track | 99 | 840098099 | Timken | GETS
Turkey Track | 100 | 840098100 | Timken | Nanjing
Turkey Track | 101 | 840098101 | SKF | GETS
Turkey Track | 102 | 840098102 | SKF | Nanjing
Turkey Track | 103 | 840098103 | Timken | GETS
Turkey Track | 104 | 840098104 | SKF | Moventas
Turkey Track | 105 | 840098105 | SKF | Moventas
Turkey Track | 106 | 840098106 | SKF | Moventas
Turkey Track | 107 | 840098107 | Timken | GETS
Turkey Track | 108 | 840098108 | Timken | GETS
Turkey Track | 109 | 840098109 | Timken | Nanjing
Turkey Track | 110 | 840098110 | SKF | Nanjing
Turkey Track | 111 | 840098111 | FAG | Winergy
Turkey Track | 112 | 840098112 | FAG | GETS
Turkey Track | 113 | 840098113 | Koyo | Moventas

## ALL_CMS_WOs
Priority | Equipment | Work Order | Description | Date Created | Status | Problem Code | Standard WO | Organization | Created By | Duration | Date Completed
1 | WTG-0059-0000 | 1657997 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2017-01-12 07:30 | Closed | GBXOIL | GBXOILCOOL | BETHEL | DWOOD |  | 2017-01-15 16:12
5 | WTG-0004-N000-0000 | 1825317 | Secondary filter cut-out contactor installation | 2018-01-15 15:50 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | JUDITHGAP |  | 2018-02-27 08:29
1 | WTG-0042-0000 | 1345287 | Change gearbox inlet hose | 2016-07-15 11:18 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | JLAPPIN |  | 2016-08-04 15:06
1 | WTG-0023-NDGP-0000 | 1273269 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-05-19 14:51 | Closed | GBXOIL | GBXOILCOOL | SPRING CANYON | STAYLOR |  | 2016-05-20 15:40
1 | WTG-0062-NDGP-0000 | 1622604 | GEARBOX OIL, Fix oil leak | 2016-12-05 12:59 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MIAMI |  | 2016-12-19 07:21
1 | WTG-0061-0000 | 1250401 | No Errors | 2016-03-03 13:57 | Closed | GBXOIL | GBXOILSAMP | JUDITH GAP | TBRISCOE |  | 2016-03-04 06:11
2 | WTG-0084-NDGP-0000 | 1241708 | GEARBOX OIL, Particle counter installation | 2016-02-10 15:31 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2016-02-11 11:41
1 | WTG-0012-0000 | 1344039 | Install secondary filtration system on gearbox oil | 2016-07-12 09:37 | Closed | GBXOIL | GBXFILTINS | WOLVERINE CREEK | DSTEO | 1 | 2016-07-19 09:03
5 | WTG-0036-NDG0-0000 | 1249178 | Oil filter housing replacement | 2016-03-01 13:43 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CRWADE |  | 2016-03-04 10:34
1 | WTG-0020-NDG0-0000 | 1255635 | GEARBOX OIL, Particle counter installation (Troubleshoot) | 2016-03-29 09:57 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | TURKEY TRACK |  | 2016-03-30 15:38
2 | WTG-0025-NDGP-0000 | 1280063 | Oil Pump Inversion | 2016-06-03 12:29 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | AMARTORANA |  | 2016-06-03 14:01
4 | WTG-0022-NDGP-0000 | 1591668 | Gear oil pump replacement | 2016-10-21 10:04 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-10-24 15:26
5 | WTG-0050-0000 | 1270519 | GEARBOX OIL, Oil Sample | 2016-05-10 10:49 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-03 15:07
5 | WTG-0061-0000 | 1270520 | GEARBOX OIL, Oil Sample | 2016-05-10 10:50 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-28 08:35
2 | WTG-0005-NDGP-0000 | 1270424 | Oil Pump Motor Inversion | 2016-05-09 14:03 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | DSTEO |  | 2016-05-13 09:26
2 | WTG-0072-0000 | 1586267 | GEARBOX OIL, Fix oil leak | 2016-10-12 12:50 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | BUCKEYE |  | 2016-11-10 17:01
1 | WTG-0128-NDGP-0000 | 1359217 | EM: Gearbox oil pessure too low | 2016-08-03 15:17 | Closed | GBXOIL | EM52 | WAKE 1 | JDEWEESE |  | 2016-08-12 14:29
1 | WTG-0065-NDG0-0000 | 1359218 | GEARBOX OIL, Fix oil leak | 2016-08-03 14:33 | Closed | GBXOIL | GBXOILLEAK | MCADOO | DHALE |  | 2016-08-04 08:32
4.2 | WTG-0009-0000 | 1401332 | gearbox oil sample and Post oil change Oil sample | 2016-08-12 14:24 | Cancelled | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-17 16:21
4.2 | WTG-0010-0000 | 1401333 | gearbox oil sample and Post oil change Oil sample | 2016-08-12 14:24 | Cancelled | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-17 16:22
4.2 | WTG-0012-0000 | 1401341 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:26 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-30 17:02
4.2 | WTG-0013-0000 | 1401342 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:26 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-30 17:01
4.2 | WTG-0022-0000 | 1401353 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:28 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:54
4.2 | WTG-0024-0000 | 1401355 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:29 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:53
4.2 | WTG-0028-0000 | 1401359 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:29 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-27 18:59
4.2 | WTG-0023-0000 | 1401354 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:28 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:53
4.2 | WTG-0029-0000 | 1401360 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:30 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-27 18:58
4.2 | WTG-0046-0000 | 1401395 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:35 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:33
4.2 | WTG-0065-0000 | 1401433 | gearbox oil change and post oil change Oil sample | 2016-08-12 14:39 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:21
4.2 | WTG-0031-0000 | 1401362 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:30 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:50
4.2 | WTG-0051-0000 | 1401405 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:35 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:25
4.2 | WTG-0052-0000 | 1401406 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:36 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:41
1 | WTG-0101-NDGP-0000 | 1425610 | WTG 0101 gearbox radiator has leak | 2016-09-08 10:10 | Closed | GBXOIL | GBXOILCOOL | TURKEY TRACK | MGROTJAN |  | 2016-12-09 13:26
2 | WTG-0118-NDG0-0000 | 1599482 | GEARBOX OIL, Particle counter installation | 2016-11-03 10:17 | Closed | GBXOIL | GBXPARTINS | GREXP | SCLARK |  | 2016-11-29 07:14
9 | WTG-0066-0000 | 1188550 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 08:46 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
9 | WTG-0068-0000 | 1188552 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 08:50 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
9 | WTG-0090-0000 | 1188553 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 08:52 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
9 | WTG-0100-0000 | 1188555 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 08:56 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
9 | WTG-0105-0000 | 1188556 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 08:58 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
9 | WTG-0078-0000 | 1188558 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:02 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
9 | WTG-0085-0000 | 1188561 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:09 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
9 | WTG-0086-0000 | 1188562 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:11 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
1 | WTG-0051-0000 | 1112659 | GEARBOX OIL, Fix oil leak | 2015-03-26 09:59 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2015-06-25 07:18
1 | GBX-000039 | 1137052 | Pall Filter Housing Leak | 2015-05-07 17:03 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CHADDIX |  | 2015-05-14 13:17
2 | WTG-0061-NDGP-0000 | 1158968 | GEARBOX OIL, Fix oil leak (Radiator) | 2015-07-06 08:18 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | JBRILEY |  | 2015-07-07 11:57
1 | WTG-0014-0000 | 1193837 | Gearbox Inspection | 2015-10-27 10:38 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | RWALL |  | 2018-01-09 12:39
2 | WTG-0107-NDG0-0000 | 1601765 | GEARBOX OIL, Fix oil leak | 2016-11-11 10:43 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | JBRILEY |  | 2016-12-22 11:50
2 | WTG-0109-NDG0-0000 | 1601766 | GEARBOX OIL, Fix oil leak (Follow up) | 2016-11-11 10:46 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | JBRILEY |  | 2016-12-22 11:51
1 | WTG-0054-NDGP-0000 | 1602413 | GEARBOX OIL, Replace oil cooler hose | 2016-11-16 08:54 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | JFREEMAN |  | 2016-12-29 07:17
4.2 | WTG-0010-NDG0-0000 | 1668757 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:20 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-16 08:00
4.2 | WTG-0006-NDG0-0000 | 1668751 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:19 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-01 08:19
9 | WTG-0075-0000 | 1663560 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2017-01-26 08:53 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ | 30 | 2017-01-27 16:12
9 | WTG-0085-0000 | 1663561 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2017-01-26 08:53 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ | 30 | 2017-01-27 16:12
1 | TTEC-WTG-062 | 1253941 | EM: Gearbox oil level too low | 2016-03-23 18:37 | Closed | GBXOIL | EM51 | TURKEY TRACK | SREYNOLDS |  | 2016-03-24 08:10
1 | MIA1 | 1595420 | GEARBOX OIL, Fix oil leak | 2016-10-28 17:35 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2016-10-31 07:31
1 | WTG-0137-NDG0-0000 | 1595392 | EM: Shaft bearing overtemperature | 2016-10-28 16:11 | Closed | GBXOIL | EM81 | WAKE 1 | IMORALES |  | 2016-11-07 16:16
5 | WTG-0014-NDGP-0000 | 1602564 | GEARBOX OIL, Secondary filter system element change | 2016-11-16 14:35 | Closed | GBXOIL | GBXFILTELEM | WOLVERINE CREEK | AMARTORANA |  | 2016-11-18 14:38
2 | WTG-0002C-NDGP-0000 | 1259849 | GEARBOX OIL, Replace oil cooler fan motor | 2016-04-05 17:01 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2016-04-13 14:07
1 | WTG-0076-NDGP-0000 | 1267388 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:35 | Closed | GBXOIL | GBXFILTELEM | GREXP | MSNOW |  | 2016-12-22 08:53
1 | WTG-0085-NDGP-0000 | 1267389 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:35 | Closed | GBXOIL | GBXFILTELEM | GREXP | MSNOW |  | 2016-05-24 07:18
1 | WTG-0102-NDGP-0000 | 1267390 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:35 | Closed | GBXOIL | GBXFILTELEM | GREXP | MSNOW |  | 2016-10-13 08:30
1 | WTG-0111-NDGP-0000 | 1267391 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:36 | Closed | GBXOIL | GBXFILTELEM | GREXP | MSNOW |  | 2017-12-14 16:42
1 | WTG-0004-NDGP-0000 | 1267393 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 08:37 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | MSNOW |  | 2016-06-02 06:24
1 | WTG-0040-NDGP-0000 | 1267376 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:32 | Closed | GBXOIL | GBXFILTELEM | GRAND RIDGE | MSNOW |  | 2017-04-28 11:53
1 | WTG-0043-NDGP-0000 | 1267377 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:33 | Closed | GBXOIL | GBXFILTELEM | GRAND RIDGE | MSNOW |  | 2017-11-09 07:52
1 | WTG-0093-0000 | 1269881 | GEARBOX OIL, Fix oil leak | 2016-05-05 10:59 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MIAMI |  | 2016-05-09 07:16
5 | WTG-0063-0000 | 1270521 | GEARBOX OIL, Oil Sample | 2016-05-10 10:50 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-28 08:35
5 | WTG-0070-0000 | 1270524 | GEARBOX OIL, Oil Sample | 2016-05-10 10:54 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-28 08:35
4.2 | WTG-0021-NDG0-0000 | 1669004 | GEARBOX OIL, Add/Top-Off | 2017-02-03 09:02 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-31 12:09
4.2 | WTG-0022-NDG0-0000 | 1669005 | GEARBOX OIL, Add/Top-Off | 2017-02-03 09:02 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-04-04 15:07
4.2 | WTG-0028-NDG0-0000 | 1669006 | GEARBOX OIL, Add/Top-Off | 2017-02-03 09:03 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-04-14 08:15
4.2 | WTG-0030-NDG0-0000 | 1669007 | GEARBOX OIL, Add/Top-Off | 2017-02-03 09:03 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-04-19 13:14
4.2 | WTG-0035-NDG0-0000 | 1669008 | GEARBOX OIL, Add/Top-Off | 2017-02-03 09:04 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-05-04 10:58
4.2 | WTG-0032-NDG0-0000 | 1669009 | GEARBOX OIL, Add/Top-Off | 2017-02-03 09:06 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-04-21 21:49
2 | WTG-0022-NDG0-0000 | 1281570 | GEARBOX OIL, Fix oil leak | 2016-06-10 14:48 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | JCUMMINGS |  | 2017-04-30 19:47
1 | WTG-0010-NDG0-0000 | 1118675 | Jensen Filter Verification | 2015-04-07 19:01 | Closed | GBXOIL | GBXOILSAMP | PRAIRIE BREEZE | CROLAND |  | 2015-04-13 17:01
4 | WTG-0049-NDG0-0000 | 1588660 | GEARBOX OIL, Add/Top-Off | 2016-10-18 17:26 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2016-10-19 14:43
1 | WTG-0024-0000 | 1354272 | Replace oil pump to motor coupler | 2016-07-29 09:02 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | JDWILLIAMS |  | 2016-08-30 09:36
1 | WTG-0122-0000 | 1337977 | GEARBOX OIL, Fix oil leak | 2016-06-30 11:42 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | JLAPPIN |  | 2018-01-09 13:08
1 | WTG-0149-0000 | 1646233 | GEARBOX OIL, Replace oil cooler hose | 2016-12-22 16:02 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MIAMI |  | 2016-12-23 11:06
2 | WTG-0026-NDGP-0000 | 1586683 | GEARBOX OIL, Fix oil leak-Replace drain valve | 2016-10-14 06:24 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2016-10-24 15:29
1 | WTG-0046-NDG0-0000 | 1586687 | GEARBOX OIL, Fix oil leak | 2016-10-14 08:34 | Closed | GBXOIL | GBXOILLEAK | GUNSIGHT | CHUBBARD |  | 2016-10-17 08:49
4 | WTG-0026-NDG0-0000 | 1586637 | GEARBOX OIL, Add/Top-Off (Needed 5 gal.) | 2016-10-13 15:22 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2016-10-18 14:12
5 | WTG-0049-0000 | 1270518 | GEARBOX OIL, Oil Sample | 2016-05-10 10:48 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-28 08:35
1 | WTG-0113-NDGP-0000 | 1272474 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS II | RJOHNSON |  | 2017-08-03 15:18
1 | WTG-0160-NDGP-0000 | 1272475 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS II | RJOHNSON |  | 2017-08-07 16:31
1 | WTG-0165-NDGP-0000 | 1272476 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS II | RJOHNSON |  | 2017-08-03 15:15
1 | WTG-0125-NDGP-0000 | 1272477 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS II | RJOHNSON |  | 2017-08-03 15:12
1 | WTG-0105-NDGP-0000 | 1272509 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | TURKEY TRACK | RJOHNSON |  | 2016-06-30 21:56
1 | WTG-0113-NDGP-0000 | 1272510 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | TURKEY TRACK | RJOHNSON |  | 2016-06-30 21:58
1 | WTG-0062-NDGP-0000 | 1272511 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 12:51 | Closed | GBXOIL | GBXFILTELEM | VANTAGE | RJOHNSON |  | 2018-11-19 16:33
1 | WTG-0056-NDGP-0000 | 1272512 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 12:51 | Closed | GBXOIL | GBXFILTELEM | VANTAGE | RJOHNSON |  | 2016-11-11 10:54
1 | WTG-0036-NDGP-0000 | 1272514 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 12:51 | Closed | GBXOIL | GBXFILTELEM | VANTAGE | RJOHNSON |  | 2018-04-12 12:10
1 | WTG-0049-NDGP-0000 | 1272515 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 12:51 | Closed | GBXOIL | GBXFILTELEM | VANTAGE | RJOHNSON |  | 2016-11-02 09:44
1 | WTG-0016-NDGP-0000 | 1272516 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 12:51 | Closed | GBXOIL | GBXFILTELEM | WILLOW CREEK | RJOHNSON |  | 2016-09-09 14:01
1 | WTG-0013-NDGP-0000 | 1272519 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 12:51 | Closed | GBXOIL | GBXFILTELEM | WILLOW CREEK | RJOHNSON |  | 2016-09-08 10:03
1 | WTG-0034-NDGP-0000 | 1272520 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 13:51 | Closed | GBXOIL | GBXFILTELEM | WOLVERINE CREEK | RJOHNSON |  | 2016-07-19 09:11
1 | WTG-0039-NDGP-0000 | 1272521 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 13:51 | Closed | GBXOIL | GBXFILTELEM | WOLVERINE CREEK | RJOHNSON |  | 2016-08-15 17:09
1 | WTG-0014-NDGP-0000 | 1272522 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 13:51 | Closed | GBXOIL | GBXFILTELEM | WOLVERINE CREEK | RJOHNSON |  | 2016-07-25 12:31
1 | WTG-0045-NDGP-0000 | 1272517 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 12:51 | Closed | GBXOIL | GBXFILTELEM | WILLOW CREEK | RJOHNSON |  | 2016-11-02 06:36
1 | WTG-0041-NDGP-0000 | 1272518 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 12:51 | Closed | GBXOIL | GBXFILTELEM | WILLOW CREEK | RJOHNSON |  | 2017-10-20 14:51
1 | WTG-0045-NDGP-0000 | 1272463 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS I | RJOHNSON |  | 2017-08-03 15:34
1 | WTG-0029-NDGP-0000 | 1272506 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | STANTON | RJOHNSON |  | 2016-11-04 14:29
1 | WTG-0012-NDGP-0000 | 1272507 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | STANTON | RJOHNSON |  | 2017-10-16 12:05
1 | WTG-0090-NDGP-0000 | 1272508 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | TURKEY TRACK | RJOHNSON |  | 2016-06-30 21:56
1 | WTG-0019-NDGP-0000 | 1272464 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS I | RJOHNSON |  | 2017-08-03 15:34
1 | WTG-0023-NDGP-0000 | 1272465 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS I | RJOHNSON |  | 2017-08-03 15:33
1 | WTG-0016-NDGP-0000 | 1272466 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS I | RJOHNSON |  | 2017-08-03 15:32
1 | WTG-0014-NDGP-0000 | 1272467 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS I | RJOHNSON |  | 2017-08-03 15:30
1 | WTG-0011-NDGP-0000 | 1272468 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS I | RJOHNSON |  | 2017-08-03 15:28
1 | WTG-0005-NDGP-0000 | 1272505 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | STANTON | RJOHNSON |  | 2017-10-16 12:05
1 | WTG-0006-NDGP-0000 | 1272502 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | STANTON | RJOHNSON |  | 2016-11-08 15:10
1 | WTG-0033-NDGP-0000 | 1272503 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | STANTON | RJOHNSON |  | 2016-12-13 15:43
1 | WTG-0053-NDGP-0000 | 1272504 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | STANTON | RJOHNSON |  | 2017-10-16 12:07
1 | WTG-0080-0000 | 1124412 | GEARBOX OIL, Fix oil leak | 2015-04-17 08:15 | Closed | GBXOIL | GBXOILLEAK | MCADOO | JZARATE |  | 2015-04-21 07:36
1 | WTG-0031-0000 | 1273506 | Pall filter housing leak | 2016-05-21 14:05 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MIAMI |  | 2016-08-15 15:46
1 | WTG-0175-NDGP-0000 | 1245776 | 72hr oil sample | 2016-02-26 11:01 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS II | JPOTTER |  | 2016-02-29 08:19
1 | WTG-0142-NDG0-0000 | 1600871 | GEARBOX OIL, Replace oil cooler hose | 2016-11-07 14:00 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2016-12-29 07:19
1 | WTG-0151-NDG0-0000 | 1600872 | Fix leaks on Nanjing gearboxes | 2016-11-07 14:00 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 07:48
1 | WTG-0152-NDG0-0000 | 1600873 | Fix leaks on Nanjing gearboxes | 2016-11-07 14:00 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 07:49
1 | WTG-0006-NDGP-0000 | 1402665 | GEARBOX OIL, Oil Sample | 2016-08-18 16:43 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS I | MSNOW |  | 2016-08-22 07:09
1 | WTG-0009-NDGP-0000 | 1402666 | GEARBOX OIL, Oil Sample | 2016-08-18 16:43 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS I | MSNOW |  | 2016-08-22 07:10
1 | WTG-0093-NDG0-0000 | 1403922 | GEARBOX OIL, Oil Sample | 2016-08-23 12:22 | Closed | GBXOIL | GBXOILSAMP | PRAIRIE BREEZE | LHINKLE |  | 2016-08-30 08:56
2 | WTG-0085-NDGP-0000 | 1404009 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-08-23 16:03 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-01-04 11:31
1 | WTG-0056-0000 | 1655212 | GEARBOX OIL, Replace oil cooler hose | 2017-01-04 13:37 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-03-28 07:48
4.2 | WTG-0039-NDGP-0000 | 1601301 | replace oil cooler motor | 2016-11-09 15:20 | Cancelled | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2019-04-18 09:22
4 | WTG-0040A-NDGP-0000 | 1601372 | GEARBOX OIL, Replace pump | 2016-11-10 09:20 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-11-15 09:22
3 | WTG-0025-NDGP-0000 | 1595779 | Install Winergy oil pump inversion kit | 2016-10-31 10:04 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2016-11-07 09:18
2 | WTG-0118-0000 | 1657949 | GEARBOX OIL, Fix oil leak | 2017-01-11 18:00 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2018-05-15 16:17
1 | WTG-0003-0000 | 1657945 | GEARBOX OIL, Fix oil leak | 2017-01-11 17:24 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MIAMI |  | 2017-01-13 07:39
5 | WTG-0096-NDGP-0000 | 1477793 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-09-14 08:15 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-09-19 13:52
1 | WTG-0108-0000 | 1563671 | GEARBOX OIL, Oil Sample | 2016-09-26 14:21 | Closed | GBXOIL | GBXOILSAMP | CAL RIDGE | BDAILY |  | 2016-09-26 14:48
1 | WTG-0088-NDGP-0000 | 1229069 | EM: Gearbox oil pessure too low | 2016-01-06 10:27 | Closed | GBXOIL | EM52 | MCADOO | MGIVENS |  | 2016-01-06 15:20
5 | WTG-0204A-NDGP-0000 | 1229131 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-01-06 15:21 | Closed | GBXOIL | GBXOILCOOL | FORWARD | ACASPER |  | 2016-01-21 10:21
1 | WTG-0103-0000 | 1518136 | GEARBOX OIL, Fix oil leak | 2016-09-15 16:04 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | BDAILY |  | 2016-09-19 07:51
9 | WTG-0045-0000 | 1613901 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-11-30 15:46 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | KIRBY | 30 | 2017-01-27 16:11
1 | WTG-0144-0000 | 1570303 | GEARBOX OIL, Replace oil cooler hose | 2016-09-29 09:23 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2016-09-30 07:35
2 | WTG-0120-NDG0-0000 | 1600178 | GEARBOX OIL, Add/Top-Off | 2016-11-04 16:06 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JFREEMAN |  | 2016-11-07 10:03
1 | WTG-0066-NDGP-0000 | 1600170 | GEARBOX OIL, Fix oil leak | 2016-11-04 15:55 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JFREEMAN |  | 2016-11-04 16:10
1 | WTG-0059-0000 | 1649605 | GEARBOX OIL, Replace oil cooler hose | 2016-12-28 13:55 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-03-22 07:44
1 | WTG-0093-NDGP-0000 | 1178484 | pump inversion | 2015-09-02 15:42 | Closed | GBXOIL | GBXOILCOOL | GREXP | NSCHAEFER |  | 2018-01-06 10:19
1 | WTG-0090-NDGP-0000 | 1180040 | EM: Gearbox oil pessure too low | 2015-09-08 12:23 | Closed | GBXOIL | EM52 | MCADOO | IMORALES |  | 2015-11-25 09:29
5 | WTG-0026-0000 | 1189874 | Install Filter Mag | 2015-10-08 13:43 | Closed | GBXOIL | GBXFILTINS | SPRING CANYON | ASCHRIMPSCHER |  | 2015-11-19 19:39
2 | WTG-0053-0000 | 1191850 | GEARBOX OIL, Fix oil leak | 2015-10-19 09:08 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CWADE |  | 2016-01-08 11:44
2 | WTG-0104-0000 | 1231193 | GEARBOX OIL, Fix oil leak | 2016-01-14 18:12 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CWADE |  | 2016-12-06 17:04
1 | WTG-0030-NDG0-0000 | 1038346 | Gearbox Oil Sample (Special) | 2014-09-02 14:20 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | MCONWELL |  | 2015-03-16 12:33
1 | WTG-0028-NDG0-0000 | 1038337 | Gearbox Oil Sample (Special) | 2014-09-02 14:20 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | MCONWELL |  | 2015-03-02 09:13
2 | WTG-0096-NDG0-0000 | 1163641 | GEARBOX OIL, Oil Sample | 2015-07-29 10:49 | Closed | GBXOIL | GBXOILSAMP | TURKEY TRACK | MSNOW |  | 2015-07-31 13:05
1 | WTG-0122-NDGP-0000 | 1238772 | GEARBOX OIL, Replace oil cooler ( radiator) winergy | 2016-02-03 17:11 | Closed | GBXOIL | GBXOILCOOL | GREXP | NSCHAEFER |  | 2016-06-30 13:53
2 | WTG-0E13-0000 | 1091864 | GEARBOX OIL, Oil Sample | 2015-02-06 09:23 | Closed | GBXOIL | GBXOILSAMP | BEECH RIDGE | SLANGLEY |  | 2015-02-06 12:30
9 | WTG-0039-0000 | 1617115 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-12-02 13:54 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ | 30 | 2016-12-29 14:44
2 | WTG-0006-NDGP-0000 | 1611025 | GEARBOX OIL, Particle counter troubleshooting | 2016-11-28 09:44 | Closed | GBXOIL | GBXPARTINS | JUDITH GAP | MSNOW |  | 2016-11-29 16:12
9 | WTG-0007-0000 | 1239429 | GEARBOX OIL, Secondary filter system installation | 2016-02-05 08:26 | Closed | GBXOIL | GBXFILTINS | RATTLESNAKE 1 | JGASTON |  | 2016-02-16 07:53
1 | WTG-0A02-0000 | 1640648 | Post Gear Box Oil Sample CT 320 | 2016-12-12 07:03 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2016-12-12 07:57
1 | WTG-0B01-0000 | 1640649 | Post Gear Box Oil Sample CT 320 | 2016-12-12 07:05 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2016-12-12 07:55
1 | WTG-0C03-0000 | 1640650 | Post Gear Box Oil Sample CT 320 | 2016-12-12 07:06 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2016-12-12 07:53
1 | WTG-0F03-0000 | 1640651 | Post Gear Box Oil Sample CT 320 | 2016-12-12 07:06 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2016-12-12 07:52
1 | WTG-0F06-0000 | 1640652 | Post Gear Box Oil Sample CT 320 | 2016-12-12 07:07 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2016-12-12 07:49
2 | WTG-0043-NDGP-0000 | 1241525 | GEARBOX OIL, Replace oil cooler | 2016-02-09 17:13 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2017-08-14 12:05
2 | WTG-0033-0000 | 1245564 | Gearbox Oil Leak | 2016-02-25 14:23 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CSIPE |  | 2016-05-31 17:07
1 | WTG-0021-NDGP-0000 | 1110240 | T-21Needs new Radiator uptower. (Leaking) | 2015-03-19 14:51 | Closed | GBXOIL | GBXOILCOOL | GRAND RIDGE | JLANDRUM |  | 2015-10-12 14:19
1 | WTG-0079-NDG0-0000 | 1134682 | GEARBOX OIL, Oil Sample | 2015-05-01 10:06 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS I | LBENAVIDES |  | 2015-05-05 08:11
1 | WTG-0110-NDG0-0000 | 1346769 | GEARBOX OIL, Oil Sample | 2016-07-20 14:14 | Closed | GBXOIL | GBXOILSAMP | SCEXP | ASCHRIMPSCHER |  | 2016-07-26 10:37
1 | WTG-0106-NDG0-0000 | 1346770 | GEARBOX OIL, Oil Sample | 2016-07-20 14:15 | Closed | GBXOIL | GBXOILSAMP | SCEXP | ASCHRIMPSCHER |  | 2016-07-26 10:36
1 | WTG-0062-0000 | 1147715 | GEARBOX OIL, Oil Sample | 2015-06-05 14:24 | Closed | GBXOIL | GBXOILSAMP | MIAMI 1 | ZMCCASLAND |  | 2015-06-05 15:47
2 | WTG-0044-NDGP-0000 | 1346133 | GEARBOX OIL, Fix oil leak | 2016-07-15 14:17 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2016-07-18 09:09
2 | WTG-0076-NDGP-0000 | 1401755 | GEARBOX OIL, Particle counter installation | 2016-08-15 09:56 | Closed | GBXOIL | GBXPARTINS | GREXP | MSNOW |  | 2016-09-09 15:26
1 | WTG-0029-0000 | 1182947 | GEARBOX OIL, Fix oil leak | 2015-09-27 20:27 | Closed | GBXOIL | GBXOILLEAK | CAMP SPRINGS I | FMORALES |  | 2015-09-28 08:01
1 | WTG-0040-NDG0-0000 | 1194618 | GEARBOX OIL, Oil Sample | 2015-10-29 08:30 | Closed | GBXOIL | GBXOILSAMP | WOLVERINE CREEK | MSNOW |  | 2015-11-06 09:26
4 | WTG-0020-NDGP-0000 | 1593220 | GEARBOX OIL, Fix oil leak- Replace O-Ring on filter housing | 2016-10-26 06:08 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2016-10-28 15:33
2 | WTG-0046-NDGP-0000 | 1211184 | GEARBOX OIL, Particle counter troubleshooting | 2015-11-30 10:22 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2015-12-02 12:58
1 | WTG-0040-0000 | 1605982 | Replace radiator | 2016-11-17 16:07 | Closed | GBXOIL | GBXOILCOOL | GRAND RIDGE | JDISS |  | 2017-03-06 07:53
5 | WTG-0031-NDGP-0000 | 1606043 | GEARBOX OIL, Clean Cooler Radiator | 2016-11-18 06:54 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | JFREEMAN |  | 2017-12-07 07:41
1 | WTG-0083-0000 | 1660946 | GEARBOX OIL, Fix oil leak | 2017-01-20 12:27 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JUDITHGAP |  | 2017-01-20 14:13
1 | WTG-0063-0000 | 1240027 | GEARBOX OIL, Fix oil leak | 2016-02-08 11:12 | Closed | GBXOIL | GBXOILLEAK | STANTON | THUBBARD |  | 2016-02-08 17:01
9 | WTG-0070-0000 | 1280880 | Tower clean up due to oi leak - Oil Cooler | 2016-06-08 08:34 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | KIRBY |  | 2016-07-15 09:50
1 | WTG-0097-NDG0-0000 | 1600857 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:56 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 09:14
1 | WTG-0100-NDG0-0000 | 1600858 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:56 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 09:15
1 | WTG-0107-NDG0-0000 | 1600859 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:57 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 09:15
2 | WTG-0032-0000 | 1594807 | GEARBOX OIL, Replace oil pump coupler | 2016-10-27 17:24 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | BSMITH |  | 2016-12-12 11:20
1 | WTG-0024-0000 | 1557377 | GEARBOX OIL, Fix oil leak | 2016-09-23 11:27 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | RWALL |  | 2016-09-23 12:08
5 | WTG-0118-NDG0-0000 | 1656828 | GEARBOX OIL, Fix oil leak | 2017-01-09 11:16 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | CAL RIDGE |  | 2017-02-23 10:12
5 | WTG-0119-NDG0-0000 | 1656829 | GEARBOX OIL, Fix oil leak | 2017-01-09 11:18 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | CAL RIDGE |  | 2017-02-13 18:12
1 | GBX-000010 | 1656851 | Gearbox inlet hose replacement | 2017-01-09 13:13 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | RWALL |  | 2017-04-03 13:59
1 | GBX-000010 | 1656852 | Oil sample | 2017-01-09 13:17 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | RWALL |  | 2017-01-12 07:05
3 | WTG-0023-NDGP-0000 | 1613840 | Winergy Oil Pump Inversion Kit | 2016-11-30 11:48 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2017-05-01 17:32
3 | WTG-0026-NDGP-0000 | 1613850 | Winergy Oil Pump Inversion Kit | 2016-11-30 11:50 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2017-05-01 12:31
3 | WTG-0031-NDGP-0000 | 1613851 | Winergy Oil Pump Inversion Kit | 2016-11-30 11:52 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2017-05-03 17:33
3 | WTG-0032-NDGP-0000 | 1613853 | Winergy Oil Pump Inversion Kit | 2016-11-30 11:54 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2017-04-14 13:44
3 | WTG-0033-NDGP-0000 | 1613854 | Winergy Oil Pump Inversion Kit | 2016-11-30 11:55 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2017-05-03 17:33
3 | WTG-0036-NDGP-0000 | 1613855 | Winergy Oil Pump Inversion Kit | 2016-11-30 11:57 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2016-12-15 12:20
3 | WTG-0038-NDGP-0000 | 1613856 | Winergy Oil Pump Inversion Kit | 2016-11-30 11:59 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2017-05-01 12:30
4.2 | WTG-0124-NDG0-0000 | 1001402 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GREXP | R5 |  | 2015-02-10 15:03
4.2 | WTG-0125-NDG0-0000 | 1001403 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GREXP | R5 |  | 2015-02-11 16:11
4.2 | WTG-0128-NDG0-0000 | 1001405 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GREXP | R5 |  | 2015-02-12 15:15
4.2 | WTG-0129-NDG0-0000 | 1051648 | 3 Year Gearbox Borescope Inspection | 2014-10-03 08:24 | Closed | GBXOIL |  | GREXP | JURSUA |  | 2017-04-28 11:54
1 | WTG-0112-NDG0-0000 | 1096094 | GEARBOX OIL, Fix oil leak | 2015-02-21 20:08 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | BDOZLER |  | 2015-03-23 12:28
2 | WTG-0059-0000 | 1110856 | GEARBOX OIL, Fix oil leak | 2015-03-20 15:14 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | JBRILEY |  | 2015-09-21 09:16
1 | WTG-0156-NDGP-0000 | 1093049 | Offline Filter Installation | 2015-02-11 09:03 | Cancelled | GBXOIL | GBXFILTINS | MIAMI 1 | LPORTER |  | 2015-02-13 16:20
1 | WTG-0088-NDG0-0000 | 1129047 | GEARBOX OIL, Fix oil leak | 2015-04-22 08:30 | Closed | GBXOIL | GBXOILLEAK | MCADOO | DHALE |  | 2015-04-23 10:21
1 | WTG-0027-NLS0-0000 | 1130618 | GEARBOX OIL, Fix oil leak | 2015-04-28 10:44 | Closed | GBXOIL | GBXOILLEAK | MCADOO | BMARSHALL |  | 2015-04-30 13:55
1 | WTG-0080-0000 | 1686352 | Changed leaking oil pump | 2017-03-24 13:48 | Closed | GBXOIL | GBXOILCOOL | MCADOO | AHILL2 |  | 2017-03-29 10:23
5 | WTG-0082-NDG0-0000 | 1696227 | Install pail under front of gearbox | 2017-04-17 14:12 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2017-06-14 11:03
4.2 | SITE-VWEC | 1710233 | Built CJC secondary filter pumps | 2017-05-24 16:40 | Closed | GBXOIL | GBXFILTINS | VANTAGE | VANTAGE |  | 2017-07-07 17:22
2 | WTG-0008-NDGP-0000 | 1734390 | GEARBOX OIL, Particle counter removal | 2017-06-08 10:19 | Closed | GBXOIL | GBXPARTINS | JUDITH GAP | MSNOW |  | 2017-06-19 08:28
5 | WTG-0057-0000 | 1161771 | change leaking rad | 2015-07-20 10:12 | Cancelled | GBXOIL | GBXOILCOOL | RALEIGH | KNOLAN |  | 2020-01-28 18:42
1 | WTG-0035-NDG0-0000 | 1342368 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-07-06 11:52 | Closed | GBXOIL | GBXOILCOOL | MCADOO | DHALE |  | 2016-07-11 10:08
1 | WTG-0041-NDG0-0000 | 1152286 | GEARBOX OIL, Oil Sample | 2015-06-22 12:27 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | RIRVING |  | 2015-07-13 13:17
1 | GBX-000079 | 1152355 | EM: Gearbox oil overtemperature | 2015-06-22 20:13 | Closed | GBXOIL | EM77 | PRAIRIE BREEZE | AMITCHELL |  | 2015-06-26 10:31
5 | WTG-0026-0000 | 1189919 | Install Filter Mag | 2015-10-08 14:03 | Cancelled | GBXOIL | GBXFILTINS | SPRING CANYON | ASCHRIMPSCHER |  | 2015-10-21 15:18
9 | WTG-0008-0000 | 1177657 | Install AMSOIL Labels on DTA & Gearbox of Turbines that have been converted | 2015-09-01 11:28 | Closed | GBXOIL | GBXOILCHG | GOLDTHWAITE | DDIAZ |  | 2015-09-18 01:43
9 | WTG-0075-0000 | 1188572 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:31 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
1 | WTG-0017-NDGP-0000 | 1199903 | EM: Gearbox oil level too low | 2015-11-09 08:12 | Closed | GBXOIL | EM51 | MCADOO | DHALE |  | 2015-11-10 09:55
1 | WTG-0073-NDGP-0000 | 1107318 | WTG #73_Replace Leaking Moventas Hose | 2015-03-12 07:48 | Closed | GBXOIL | GBXOILLEAK | FORWARD | NZIRBEL |  | 2015-03-21 08:51
2 | WTG-0061-NDG0-0000 | 1183855 | GEARBOX OIL, Fix oil leak | 2015-09-29 07:41 | Cancelled | GBXOIL | GBXOILLEAK | FORWARD | ACASPER |  | 2015-09-29 07:58
2 | WTG-0061-NDG0-0000 | 1183856 | Oil hose from oil cooler to gearbox is leaking. Needs to be replaced. | 2015-09-29 07:51 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ACASPER |  | 2015-10-09 08:30
1 | WTG-0092-0000 | 1210018 | Replace Oil Filter Canister Breather Hose | 2015-11-25 12:28 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CWADE |  | 2016-02-15 11:42
1 | WTG-0029-NDG0-0000 | 1209989 | GEARBOX OIL, Fix oil leak | 2015-11-25 08:44 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | JGILLILAN |  | 2015-12-15 16:18
1 | WTG-0033-HC00-0000 | 1199011 | GEARBOX OIL, Fix oil leak | 2015-11-05 14:49 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ACARR |  | 2015-11-10 09:39
5 | WTG-0003A-NDGP-0000 | 1208959 | GEARBOX OIL, Fix oil leak - Slow Leak Nacelle Wall Hose | 2015-11-20 07:42 | Closed | GBXOIL | GBXOILLEAK | FORWARD | NZIRBEL |  | 2015-12-15 12:54
1 | WTG-0036-0000 | 1218685 | Oil Leak | 2015-12-07 17:56 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2015-12-07 18:00
1 | WTG-0070-0000 | 1222445 | GEARBOX OIL, Oil Sample | 2015-12-22 07:11 | Closed | GBXOIL | GBXOILSAMP | GREXP | NSCHAEFER |  | 2016-02-17 10:00
1 | WTG-0071-0000 | 1222446 | GEARBOX OIL, Oil Sample | 2015-12-22 07:12 | Closed | GBXOIL | GBXOILSAMP | GREXP | NSCHAEFER |  | 2016-05-06 07:24
1 | WTG-0075-0000 | 1222447 | GEARBOX OIL, Oil Sample | 2015-12-22 07:13 | Closed | GBXOIL | GBXOILSAMP | GREXP | NSCHAEFER |  | 2016-03-07 06:50
1 | WTG-0033-0000 | 1230621 | Gearbox Oil Work/Issue | 2016-01-12 12:39 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | NSCHMEIDLER |  | 2016-01-18 10:58
5 | WTG-0061-0000 | 1160560 | GEARBOX OIL, Fix oil leak | 2015-07-10 10:10 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2015-11-24 07:27
2 | WTG-0061-NDGP-0000 | 1162082 | GEARBOX OIL, Fix oil leak | 2015-07-21 08:03 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ACASPER |  | 2015-07-21 14:45
1 | WTG-0012-0000 | 1171805 | inspection port leak | 2015-08-14 17:00 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS |  | 2015-08-15 10:41
3 | WTG-0032-NDGP-0000 | 1192151 | GEARBOX OIL, Replace oil pump | 2015-10-20 17:14 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2015-10-28 08:30
1 | WTG-0001-NDGP-0000 | 1228393 | Install Winergy oil pump inversion kit | 2016-01-04 14:32 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2016-01-06 11:18
2 | WTG-0050-NDGP-0000 | 1581257 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-10-06 06:51 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2018-03-27 12:11
1 | WTG-0016-0000 | 1101802 | Pall Housing Change | 2015-03-02 15:09 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KYARNOLD |  | 2015-03-03 13:37
1 | WTG-0113-NDG0-0000 | 1038483 | Gearbox Oil Sample (Special) | 2014-09-02 14:20 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | MCONWELL |  | 2015-03-03 09:06
4.2 | WTG-0004-NDGP-0000 | 1174792 | Leaky oil pump | 2015-08-26 13:00 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | PMASAKI |  | 2015-09-03 07:20
1 | WTG-0103-0000 | 1182645 | GEARBOX OIL, Oil Sample | 2015-09-24 12:59 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | KCOOPER |  | 2015-09-30 14:54
1 | WTG-0044-0000 | 1182649 | GEARBOX OIL, Oil Sample | 2015-09-24 13:06 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | SEVANS |  | 2015-09-30 14:54
1 | WTG-0118-0000 | 1182648 | GEARBOX OIL, Oil Sample | 2015-09-24 13:06 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | KCOOPER |  | 2015-09-30 14:54
1 | WTG-0L01-0000 | 1199088 | Oil Cooler Replacment | 2015-11-06 06:28 | Closed | GBXOIL | GBXOILCOOL | HIGH SHELDON | BEUSCHER |  | 2016-05-12 16:17
1 | WTG-0053-0000 | 1209096 | GEARBOX OIL, Oil Sample | 2015-11-20 13:55 | Closed | GBXOIL | GBXOILSAMP | TURKEY TRACK | MRHODES |  | 2015-11-25 06:53
1 | GBX-000005 | 1230488 | EM: Gearbox oil pessure too low | 2016-01-11 12:59 | Closed | GBXOIL | EM52 | JUDITH GAP | LHATVELDT |  | 2016-01-12 10:43
4.2 | WTG-0057-NDGP-0000 | 1261311 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-04-13 13:54 | Closed | GBXOIL | GBXOILCOOL | FORWARD | RSOBER |  | 2016-04-19 15:34
1 | WTG-0020-NDGP-0000 | 1114918 | GEARBOX OIL, Fix oil leak | 2015-03-31 15:24 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ACARR |  | 2015-03-31 17:07
1 | BMEC-DT-003 | 1151125 | WTG003: Low Oil Level | 2015-06-17 07:53 | Closed | GBXOIL |  | BUFFALO MOUNT | CPARKS |  | 2015-07-02 11:25
1 | GBX-000098 | 1159863 | Pall Filter Housing Leak | 2015-07-07 19:16 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CHADDIX |  | 2015-07-08 17:23
1 | WTG-0011-0000 | 1182640 | GEARBOX OIL, Oil Sample | 2015-09-24 11:45 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS I | JSULLIVAN |  | 2015-09-24 12:06
1 | WTG-0047-0000 | 1182677 | GEARBOX OIL, Oil Sample | 2015-09-24 14:47 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | MBELCHER |  | 2015-09-30 14:54
1 | WTG-0045-0000 | 1182646 | GEARBOX OIL, Oil Sample | 2015-09-24 12:58 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | SEVANS |  | 2015-09-30 14:54
1 | WTG-0004-0000 | 1219416 | GEARBOX OIL, Fix oil leak | 2015-12-10 10:59 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2015-12-11 16:04
4 | WTG-0038-NDG0-0000 | 1597865 | Gearbox Oil Hose Leaks and Needs Replacement | 2016-11-01 07:33 | Closed | GBXOIL |  | FORWARD | FORWARD |  | 2016-11-15 09:34
1 | WTG-0034-NDGP-0000 | 1242032 | Winergy Gearbox Oil Pump and Motor Inversion Kit | 2016-02-11 06:25 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MMCCABE |  | 2016-04-15 07:41
1 | GBX-000073 | 1242335 | Pall Filter Housing Leak | 2016-02-12 11:33 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | JFERRIS |  | 2016-02-24 17:52
1 | WTG-0037-NDGP-0000 | 1250018 | Winenergy Gearbox Oil Pump and Motor Flip Kit | 2016-03-02 12:50 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MMCCABE |  | 2016-03-08 13:58
1 | WTG-0046-NDGP-0000 | 1251711 | Winergy Gearbox Oil Pump and Motor Inversion Kit | 2016-03-09 06:11 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MMCCABE |  | 2016-03-14 07:34
3 | WTG-0065-NDGP-0000 | 1674103 | GEARBOX OIL, Replace oil pump | 2017-02-21 14:16 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2018-10-15 09:06
1 | WTG-0009-NDGP-0000 | 1684145 | Inversion | 2017-03-14 13:31 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | AMARTORANA |  | 2017-03-16 08:02
1 | SCEXP | 1676797 | dispose of parts | 2017-02-27 14:31 | Cancelled | GBXOIL | GBXOILLEAK | SPRING CANYON | CMUSTAIN |  | 2017-02-27 14:40
9 | WTG-0I09-NDG0-0000 | 1677268 | Gearbox Oil Change | 2017-02-28 13:08 | Closed | GBXOIL | GBXOILCHG | HIGH SHELDON | RTRITES |  | 2017-03-02 11:16
1 | WTG-0037-0000 | 1680495 | Leaking gearbox | 2017-03-02 09:49 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BDIAZ |  | 2017-06-29 15:51
1 | WTG-0037-0000 | 1680494 | Pall filter housing leak | 2017-03-02 09:47 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BDIAZ |  | 2017-06-29 15:51
4 | WTG-0029A-NDGP-0000 | 1681073 | GEARBOX OIL, Add/Top-Off | 2017-03-02 13:08 | Closed | GBXOIL | GBXOILADD | FORWARD | CMITCHELL |  | 2017-03-10 09:10
1 | WTG-0015-NDG0-0000 | 1681709 | GEARBOX OIL, Fix oil leak | 2017-03-03 20:49 | Closed | GBXOIL | GBXOILLEAK | BISHOP HILL | BISHOP HILL |  | 2017-03-15 14:51
1 | WTG-0052-0000 | 1681745 | GEARBOX OIL, Fix oil leak | 2017-03-04 12:28 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CHADDIX |  | 2017-03-06 15:00
4 | WTG-0058-NDG0-0000 | 1684686 | GEARBOX OIL, Add/Top-Off (5 gallons) | 2017-03-17 10:29 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2017-03-20 09:59
1 | WTG-0006-NDG0-0000 | 1685437 | leaking cooling hose on gearbox | 2017-03-21 15:12 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | LHATVELDT |  | 2017-03-23 14:49
1 | WTG-0117-0000 | 1685509 | GEARBOX OIL, Oil Sample | 2017-03-21 07:42 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | RATTLESNAKE |  | 2017-03-29 11:44
1 | WTG-0038-NDGP-0000 | 1687246 | GEARBOX OIL, Oil Sample | 2017-03-28 08:15 | Closed | GBXOIL | GBXOILSAMP | GRAND RIDGE | MSNOW |  | 2017-04-28 11:54
9 | WTG-0011-0000 | 1689485 | WTG011 - GEARBOX, Oil Change | 2017-04-03 07:19 | Closed | GBXOIL | GBXOILCHG | BUFFALO MOUNT | CRO EAST |  | 2020-10-15 12:16
1 | WTG-0301-0000 | 1689408 | GEARBOX OIL, Fix oil leak | 2017-04-01 18:28 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | NHEITHOFF |  | 2017-12-05 15:59
3 | WTG-0042-NDGP-0000 | 1693061 | GEARBOX OIL, Replace oil pump | 2017-04-05 14:52 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2018-08-03 11:32
1 | WTG-0062-0000 | 1694564 | Replace thermobypass | 2017-04-11 12:18 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | LPORTER |  | 2017-07-07 09:02
1 | WTG-0032-0000 | 1696705 | GBX hose sweating | 2017-04-20 08:37 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS |  | 2017-05-01 10:06
1 | WTG-0092-NDGP-0000 | 1703732 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:27 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | DSLITTLE |  | 2017-05-22 11:09
1 | WTG-0082-0000 | 1703718 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:19 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | IAREBALO |  | 2017-05-22 11:09
5 | WTG-0063-0000 | 1703719 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:18 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDKEY |  | 2017-09-07 12:14
5 | WTG-0027-0000 | 1705064 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2017-05-04 07:58 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH | 30 | 2017-05-05 09:34
3 | WTG-0005-NDGP-0000 | 1705734 | Install secondary filtration system on gearbox oil | 2017-05-04 17:12 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-08-15 15:29
1 | WTG-0095-NDG0-0000 | 1705735 | GEARBOX OIL, Fix oil leak | 2017-05-04 17:13 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | IMORALES |  | 2017-05-22 11:09
1 | WTG-0102-NDG0-0000 | 1705845 | GEARBOX OIL, Fix oil leak | 2017-05-05 08:54 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | IAREBALO |  | 2017-05-22 11:09
1 | WTG-0117-0000 | 1705855 | GEARBOX OIL, Fix oil leak | 2017-05-05 09:05 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | IAREBALO |  | 2017-05-22 11:09
1 | WTG-0145-NDGP-0000 | 1705849 | GEARBOX OIL, Fix oil leak | 2017-05-05 08:56 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | BWHEELER |  | 2017-05-22 11:09
1 | WTG-0080-NDGP-0000 | 1705996 | Gearbox Oil Work/Issue | 2017-05-05 11:38 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | DSLITTLE |  | 2017-05-22 11:09
1 | WTG-0150-NDGP-0000 | 1705850 | GEARBOX OIL, Fix oil leak | 2017-05-05 08:58 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | BWHEELER |  | 2017-05-22 11:09
3 | WTG-0099-NDGP-0000 | 1706763 | GEARBOX OIL, Replace oil pump | 2017-05-09 08:16 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2017-08-14 16:15
1 | WTG-0211-0000 | 1707583 | GEARBOX OIL, Fix oil leak | 2017-05-12 18:14 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2019-02-08 18:13
1 | WTG-0011-NDGP-0000 | 1707158 | GEARBOX OIL, Oil Sample | 2017-05-10 15:16 | Closed | GBXOIL | GBXOILSAMP | BETHEL | MSNOW |  | 2017-05-18 11:28
1 | WTG-0012-NDGP-0000 | 1707159 | GEARBOX OIL, Oil Sample | 2017-05-10 15:17 | Closed | GBXOIL | GBXOILSAMP | BETHEL | MSNOW |  | 2017-05-18 11:28
1 | WTG-0085-NDG0-0000 | 1707163 | EM: Gearbox oil pessure too low | 2017-05-10 15:22 | Closed | GBXOIL | EM52 | RONCEVAUX | SCLARK |  | 2017-05-31 14:24
1 | WTG-0240-NDG0-0000 | 1707004 | GEARBOX OIL, Fix oil leak on t joint for bypass | 2017-05-09 17:37 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE |  | 2020-11-12 15:35
2 | WTG-0042-NDGP-0000 | 1707468 | GEARBOX OIL, Inversion | 2017-05-12 10:39 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | AMARTORANA |  | 2018-04-20 15:25
1 | WTG-0043-0000 | 1707490 | GEARBOX OIL, Fix oil leak | 2017-05-11 12:38 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | RATTLESNAKE |  | 2017-05-22 10:33
3 | WTG-0024-NDGP-0000 | 1708649 | Install secondary filtration system on gearbox oil | 2017-05-17 15:53 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-10-04 14:10
3 | WTG-0006-NDGP-0000 | 1708650 | Install new Secondary oil filtration/ Sample valve and low oil cut out | 2017-05-17 15:55 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-09-25 16:56
3 | WTG-0016-NDGP-0000 | 1708666 | Install low oil cut out/ Oil Sample Valve | 2017-05-17 16:53 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-09-25 09:37
3 | WTG-0013-NDGP-0000 | 1708665 | Install low oil cut out | 2017-05-17 16:51 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-09-20 16:50
3 | WTG-0018-NDGP-0000 | 1708668 | Install low oil cut out/ Oil Sample Valve | 2017-05-17 16:54 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-09-26 16:55
3 | WTG-0019-NDGP-0000 | 1708669 | Install low oil cut out/ Oil Sample Valve | 2017-05-17 16:56 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-09-26 16:55
3 | WTG-0045-NDGP-0000 | 1709675 | Install low oil cut out/ Oil Sample Valve | 2017-05-22 14:13 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-10-20 14:57
2 | WTG-0053-0000 | 1711042 | Fix oil cooler leak | 2017-05-25 12:33 | Closed | GBXOIL | GBXOILCOOL | FORWARD | ACASPER |  | 2022-03-07 12:01
5 | WTG-0033-0000 | 1711888 | Oil cooler hose replacement gen side NGC | 2017-05-30 08:21 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2018-05-08 14:12
1 | WTG-0084-0000 | 1716146 | GEARBOX OIL, Oil Sample | 2017-06-02 15:36 | Closed | GBXOIL | GBXOILSAMP | BETHEL | AGALARZA |  | 2017-07-19 08:03
2 | WTG-0006-NDGP-0000 | 1734389 | GEARBOX OIL, Particle counter removal | 2017-06-08 10:17 | Closed | GBXOIL | GBXPARTINS | JUDITH GAP | MSNOW |  | 2017-06-19 08:28
2 | WTG-0004-NDGP-0000 | 1734398 | GEARBOX OIL, Particle counter removal | 2017-06-08 10:41 | Closed | GBXOIL | GBXPARTREM | MCADOO | MSNOW |  | 2017-06-21 10:55
1 | WTG-0001-NDGP-0000 | 1734402 | GEARBOX OIL, Particle counter removal | 2017-06-08 10:47 | Closed | GBXOIL | GBXPARTREM | SPRING CANYON | MSNOW |  | 2017-12-05 12:12
1 | WTG-0026-NDGP-0000 | 1734403 | GEARBOX OIL, Particle counter removal | 2017-06-08 10:48 | Closed | GBXOIL | GBXPARTREM | SPRING CANYON | MSNOW |  | 2019-03-22 10:39
1 | WTG-0317-NDGP-0000 | 1748373 | GEARBOX OIL, Fix oil leak | 2017-07-15 10:23 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | JSTAHLECKER |  | 2017-08-14 15:15
4 | WTG-0075B-0000 | 1774413 | Fix oil leak from plantetary / O'Hain Oil Bucket Installed | 2017-09-14 14:36 | In Progress | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE
1 | WTG-0048-0000 | 1823875 | GEARBOX OIL, Fix oil leak (NGC repair) | 2018-01-12 15:55 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | JLAPPIN |  | 2018-01-22 18:07
2 | WTG-0156-0000 | 1799199 | GEARBOX OIL, Add/Top-Off | 2017-11-07 12:30 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JFREEMAN |  | 2017-11-08 14:59
1 | WTG-0048-0000 | 1807541 | Gearbox Oil Work/Issue | 2017-12-04 13:09 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TMORRIS |  | 2018-07-20 12:00
4 | WTG-0074A-NDG0-0000 | 1809958 | GEARBOX OIL, Add/Top-Off 5 gals | 2017-12-11 16:03 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2017-12-13 09:32
2 | WTG-0052-0000 | 1826153 | missing gearbox cooler boot | 2018-01-17 15:32 | Closed | GBXOIL | BLANK | JUDITH GAP | JUDITHGAP |  | 2019-04-26 12:50
1 | WTG-0020-NDGP-0000 | 1840461 | Replace Oil Pump | 2018-02-16 09:06 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2018-05-15 11:43
4 | WTG-0024-NDG0-0000 | 1846926 | GEARBOX OIL, Add/Top-Off 5 gal | 2018-03-01 13:39 | Cancelled | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2018-06-13 15:16
2 | WTG-0G10-NDG0-0000 | 1850837 | GEARBOX OIL, Particle counter troubleshooting | 2018-03-08 11:08 | Closed | GBXOIL | GBXPARTINS | BEECH RIDGE | SCLARK |  | 2018-04-03 08:26
4.2 | WCEC | 1851227 | Oil Samples to be sent off for testing | 2018-03-09 16:32 | Closed | GBXOIL | GBXOILSAMP | WOLVERINE CREEK | WOLVERINECREEK |  | 2018-03-09 16:43
1 | WTG-0016-0000 | 1852917 | GBX hose leak | 2018-03-19 15:23 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CRWADE |  | 2018-05-24 16:06
1 | WTG-0107-0000 | 1852595 | GEARBOX OIL, Fix oil leak | 2018-03-15 12:33 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | CJERNIGAN |  | 2018-12-11 22:57
1 | WTG-0104-NDGP-0000 | 1853446 | GEARBOX OIL, Fix oil leak | 2018-03-20 17:42 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2020-11-20 10:53
2 | WTG-0071-NDGP-0000 | 1734399 | GEARBOX OIL, Particle counter installation | 2017-06-08 10:43 | Closed | GBXOIL | GBXPARTINS | MCADOO | MSNOW |  | 2017-06-21 10:56
2 | WTG-0110-NDGP-0000 | 1734406 | GEARBOX OIL, Particle counter installation | 2017-06-08 10:57 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2017-06-16 16:18
1 | WTG-0035-NDGP-0000 | 1734520 | Thermobypass | 2017-06-08 15:00 | Closed | GBXOIL | EM77 | BUCKEYE | DJACOBS |  | 2017-07-27 15:37
1 | WTG-0107-0000 | 1734703 | GEARBOX OIL, Fix oil leak | 2017-06-09 14:37 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CSIPE |  | 2017-10-26 15:20
5 | WTG-0109-NDG0-0000 | 1737460 | Check Secondary Oil Filtration Filter | 2017-06-20 11:32 | Closed | GBXOIL | BLANK | RONCEVAUX | SCLARK |  | 2017-09-22 16:54
1 | WTG-0050-0000 | 1737510 | Bypass to cooler hose replacment | 2017-06-20 15:26 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | KIRBY |  | 2017-06-27 09:54
2 | WTG-0043-NDG0-0000 | 1745118 | GEARBOX oil pump leaking | 2017-07-06 08:00 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-07-14 16:48
1 | WTG-0083-NDGP-0000 | 1746619 | GEARBOX OIL, Replace oil pump | 2017-07-07 15:49 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2017-07-31 10:24
1 | GBX-000065 | 1747900 | EM: Gearbox oil overtemperature | 2017-07-12 17:44 | Closed | GBXOIL | EM77 | PRAIRIE BREEZE | JFERRIS |  | 2017-07-19 18:39
2 | WTG-0063-0000 | 1749001 | GEARBOX OIL, Secondary filter system element change | 2017-07-17 14:04 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | SMAYER |  | 2017-07-18 07:03
2 | WTG-0064-0000 | 1749005 | GEARBOX OIL, Secondary filter system element change | 2017-07-17 14:39 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | SMAYER |  | 2017-07-18 07:03
1 | WTG-0042-NDGP-0000 | 1749100 | GEARBOX OIL, Replace oil cooler hose | 2017-07-18 08:51 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | JHAVENS |  | 2017-07-25 07:29
1 | WTG-0049-NDGP-0000 | 1749101 | GEARBOX OIL, Replace oil cooler hose | 2017-07-18 08:53 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | JHAVENS |  | 2017-07-19 07:26
2 | WTG-0009-NDG0-0000 | 1749987 | Gearbox Oil Work/Issue | 2017-07-20 16:55 | Closed | GBXOIL | EM245 | GUNSIGHT | GUNSIGHT |  | 2017-09-07 20:19
2 | WTG-0065-0000 | 1749948 | GEARBOX OIL, Secondary filter system element change | 2017-07-20 14:54 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-07-21 07:02
2 | WTG-0071-0000 | 1750282 | GEARBOX OIL, Secondary filter system element change | 2017-07-21 15:12 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-07-24 07:00
2 | WTG-0072-0000 | 1750283 | GEARBOX OIL, Secondary filter system element change | 2017-07-21 15:13 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-07-24 07:00
1 | WTG-0061-NDGP-0000 | 1750289 | GEARBOX OIL, Oil Sample | 2017-07-21 15:59 | Closed | GBXOIL | GBXOILSAMP | BUCKEYE | MSNOW | 1 | 2017-07-27 11:17
1 | WTG-0209-0000 | 1751320 | GEARBOX OIL, Oil Sample | 2017-07-24 15:49 | Closed | GBXOIL | GBXOILSAMP | SCEXP | SPRINGCANYON |  | 2017-09-08 12:20
1 | WTG-0210-0000 | 1751321 | GEARBOX OIL, Oil Sample | 2017-07-24 15:51 | Closed | GBXOIL | GBXOILSAMP | SCEXP | SPRINGCANYON |  | 2017-09-08 12:20
4 | WTG-0070-NDGP-0000 | 1825354 | Need push valve for secondary pump | 2018-01-15 16:31 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2018-04-17 16:53
2 | WTG-0075-0000 | 1759622 | GEARBOX OIL, Secondary filter system element change | 2017-08-09 14:59 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-08-10 06:56
2 | WTG-0034-0000 | 1763062 | Oil cooler fan motor has worn bearings. | 2017-08-16 16:43 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2019-06-28 09:14
2 | WTG-0079-0000 | 1763847 | GEARBOX OIL, Secondary filter system element change | 2017-08-18 11:52 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-08-21 07:17
1 | WTG-0072-0000 | 1763862 | GEARBOX OIL, Fix oil leak | 2017-08-18 14:24 | Closed | GBXOIL | GBXOILLEAK | BISHOP HILL | GPETERSON |  | 2017-09-28 09:35
1 | WTG-0023-NDGP-0000 | 1768094 | Replace oil cooler Plenum | 2017-08-31 16:56 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | MSTONER |  | 2017-10-04 14:10
2 | WTG-0082-0000 | 1770596 | GEARBOX OIL, Secondary filter system element change | 2017-09-05 14:06 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-09-06 15:12
2 | WTG-0080-NDG0-0000 | 1771078 | Replace secondary filtration system filter on gearbox oil | 2017-09-06 15:18 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GBOTT | 1 | 2017-09-07 06:56
1 | WTG-0013-0000 | 1772953 | GEARBOX OIL, Fix oil leak | 2017-09-08 19:27 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | BUCKEYE |  | 2017-09-20 09:01
1 | WTG-0018-0000 | 1774038 | GEARBOX, Uptower Gearbox Leak Repair | 2017-09-13 13:15 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | SELLISON |  | 2017-09-25 14:08
1 | WTG-0014-0000 | 1774883 | GEARBOX OIL, Oil Sample | 2017-09-15 10:58 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | BISHOP HILL |  | 2017-09-28 09:32
9 | WTG-0055-0000 | 1775937 | TERP GBX Oil Change | 2017-09-19 14:49 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE | MSNOW | 1 | 2017-10-31 16:57
1 | WTG-0041-NDGP-0000 | 1776706 | Leaking pall filter housing | 2017-09-20 15:46 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CHADDIX |  | 2018-03-30 12:14
1 | WTG-0043-0000 | 1783693 | GEARBOX OIL, Fix oil leak | 2017-10-03 18:57 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CWERNER |  | 2018-11-27 16:49
1 | WTG-0116-0000 | 1783502 | Gearbox oil pressure low | 2017-10-03 15:11 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | DLANGDON |  | 2017-10-09 14:02
5 | WTG-0132-0000 | 1784180 | GEARBOX OIL, Particle counter installation | 2017-10-05 11:23 | Closed | GBXOIL | GBXPARTINS | CAMP SPRINGS II | AMAXWELL |  | 2018-09-06 16:44
5 | WTG-0149-0000 | 1784181 | GEARBOX OIL, Particle counter installation | 2017-10-05 11:23 | Closed | GBXOIL | GBXPARTINS | CAMP SPRINGS II | AMAXWELL |  | 2019-03-19 17:05
5 | WTG-0178-0000 | 1784182 | GEARBOX OIL, Particle counter installation | 2017-10-05 11:23 | Cancelled | GBXOIL | GBXPARTINS | CAMP SPRINGS II | AMAXWELL |  | 2021-08-18 17:21
1 | WTG-0J07-NDG0-0000 | 1784177 | GEARBOX OIL, Particle counter installation | 2017-10-05 11:16 | Closed | GBXOIL | GBXPARTINS | BEECH RIDGE | SCLARK |  | 2017-12-15 11:10
5 | WTG-0039-0000 | 1784178 | GEARBOX OIL, Particle counter installation | 2017-10-05 11:21 | Cancelled | GBXOIL | GBXPARTINS | CAMP SPRINGS I | AMAXWELL |  | 2017-10-09 16:44
2 | WTG-0005-0000 | 1785694 | GEARBOX OIL, Oil Sample | 2017-10-10 11:43 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | ZSEABLOOM |  | 2017-10-12 13:22
2 | WTG-0092-0000 | 1788296 | GEARBOX OIL, Secondary filter system element change | 2017-10-18 10:42 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | JCAPEN |  | 2017-10-20 07:40
2 | WTG-0093-0000 | 1788297 | GEARBOX OIL, Secondary filter system element change | 2017-10-18 10:43 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | JCAPEN |  | 2017-10-20 07:40
9 | WTG-0032-0000 | 1789817 | Pre oil change detergent | 2017-10-25 09:16 | Closed | GBXOIL | GBXOILCHG | CAL RIDGE | JLAPPIN |  | 2017-10-26 11:28
1 | WTG-0017-0000 | 1790294 | Replaced oil filter housing | 2017-10-25 14:36 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2017-10-26 11:08
2 | WTG-0129-0000 | 1799202 | GEARBOX OIL, Add/Top-Off | 2017-11-07 16:19 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JFREEMAN |  | 2017-11-08 15:00
2 | WTG-0153-0000 | 1799201 | GEARBOX OIL, Add/Top-Off | 2017-11-07 13:39 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JFREEMAN |  | 2017-11-08 15:00
2 | WTG-0140-0000 | 1799204 | GEARBOX OIL, Add/Top-Off | 2017-11-07 17:58 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JFREEMAN |  | 2017-11-08 15:01
1 | WTG-0042-NDG0-0000 | 1800844 | GEARBOX OIL, Fix oil leak,GBX Warranty | 2017-11-13 09:50 | Closed | GBXOIL | GBXOILLEAK | MCADOO | RROBERTS |  | 2018-08-02 13:56
4 | WTG-0009-NDG0-0000 | 1801588 | GEARBOX OIL, Add/Top-Off | 2017-11-16 15:22 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2017-11-17 14:21
1 | WTG-0063-0000 | 1803983 | GBX oil filter leaking from base. | 2017-11-28 08:26 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CRWADE |  | 2018-05-14 15:43
2 | WTG-0011-0000 | 1804624 | Oil cooler Leak found | 2017-11-29 13:12 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | GOLDTHWAITE |  | 2021-10-12 07:48
2 | WTG-0011-0000 | 1804625 | Oil filter housing leak found | 2017-11-29 13:14 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | GOLDTHWAITE |  | 2018-05-31 20:25
2 | WTG-0070-0000 | 1808895 | GEARBOX OIL, Add/Top-Off | 2017-12-06 14:05 | Closed | GBXOIL | GBXOILADD | TURKEY TRACK | CJERNIGAN |  | 2018-01-12 12:32
2 | WTG-0019-0000 | 1809648 | Add Oil to Gearbox | 2017-12-09 08:30 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NSCHMEIDLER |  | 2018-01-09 12:56
2 | WTG-0035-0000 | 1809713 | Add Oil to Gearbox | 2017-12-10 07:03 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NSCHMEIDLER |  | 2018-01-09 12:56
2 | WTG-0025-0000 | 1814044 | Add Oil to Gearbox | 2017-12-19 15:38 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 09:53
2 | WTG-0042-0000 | 1814047 | Add Oil to Gearbox | 2017-12-12 15:38 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 09:39
2 | WTG-0057-0000 | 1814056 | Add Oil to Gearbox | 2017-12-14 15:48 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 09:32
1 | WTG-0034-0000 | 1819305 | GEARBOX OIL, Fix oil leak - outlet hose fitting | 2018-01-02 14:53 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | AHOFFMANN
1 | WTG-0097-0000 | 1819312 | GEARBOX OIL, Fix oil leak | 2017-12-28 15:22 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KMCLELAND |  | 2018-01-03 07:37
2 | WTG-0082-NDG0-0000 | 1819170 | GEARBOX OIL, Oil Sample | 2018-01-02 13:52 | Closed | GBXOIL | GBXOILSAMP | GRATIOT | SCLARK |  | 2018-01-16 07:16
2 | WTG-0099-NDG0-0000 | 1819172 | GEARBOX OIL, Oil Sample | 2018-01-02 13:55 | Closed | GBXOIL | GBXOILSAMP | GRATIOT | SCLARK |  | 2018-01-16 07:16
1 | GREXP | 1821237 | GEARBOX OIL, Oil Sample | 2018-01-05 13:12 | Closed | GBXOIL | GBXOILSAMP | GREXP | GRAND RIDGE |  | 2018-01-05 13:17
1 | GREC | 1821269 | GR oil samples | 2018-01-05 15:19 | Closed | GBXOIL | GBXOILSAMP | GRAND RIDGE | GRAND RIDGE |  | 2018-01-05 15:25
2 | WTG-0066-0000 | 1821736 | Add Oil to Gearbox | 2018-01-08 16:18 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:08
2 | WTG-0067-0000 | 1821739 | Add Oil to Gearbox | 2018-01-08 16:20 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:07
1 | WTG-0014-0000 | 1827093 | PALL Filter Housing Leak | 2018-01-22 11:23 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2020-01-23 14:38
1 | WTG-0090-0000 | 1830342 | GEARBOX OIL, Fix oil leak | 2018-01-23 15:49 | Cancelled | GBXOIL | GBXOILLEAK | CAL RIDGE | RWALL
1 | WTG-0021-0000 | 1831648 | GEARBOX OIL, Sweating Hose | 2018-01-26 13:23 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | CPRUIT |  | 2018-04-25 13:41
1 | WTG-0318-0000 | 1833591 | GEARBOX OIL, Replace oil cooler fan shroud | 2018-01-30 17:48 | Closed | GBXOIL | GBXOILCOOL | PRAIRIE BREEZE3 | PRAIRIE BREEZE |  | 2018-02-26 11:05
4 | WTG-0028-NDG0-0000 | 1833584 | GEARBOX OIL, Add/Top-Off | 2018-01-30 17:35 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2018-02-02 11:54
2 | WTG-0B05-NDGP-0000 | 1837992 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:16 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-04-10 07:51
2 | WTG-0E02-NDGP-0000 | 1837995 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:22 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-04-26 14:43
2 | WTG-0G08-NDGP-0000 | 1837999 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:26 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-04-26 08:27
2 | WTG-0G14-NDGP-0000 | 1838000 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:28 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-06-21 14:46
2 | WTG-0H10-NDGP-0000 | 1838004 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:31 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-03-21 10:36
1 | WTG-0006-0000 | 1838730 | GEARBOX OIL, Replace oil cooler system | 2018-02-08 06:57 | Closed | GBXOIL | GBXOILCOOL | BISHOP HILL | BISHOP HILL |  | 2018-03-05 10:20
4.2 | WTG-0089-NDGP-0000 | 1840580 | Replace Gearbox Heat Exchanger | 2018-02-16 15:21 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2018-03-26 07:00
4.2 | WTG-0101-NDGP-0000 | 1841073 | Replace Gearbox Heat Exchanger | 2018-02-20 07:05 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2018-04-02 06:56
5 | WTG-0024-NDGP-0000 | 1846927 | GEARBOX OIL, Secondary filter system broken fitting. | 2018-03-01 13:41 | Closed | GBXOIL | GBXFILTINS | FORWARD | GOTKIN |  | 2018-05-11 14:14
1 | WTG-0061-0000 | 1847071 | GEARBOX OIL, Fix oil leak-Replace Pall Filter Housing | 2018-03-01 15:48 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | NHEITHOFF |  | 2018-06-20 16:05
2 | WTG-0034-0000 | 1848549 | Replace Lube Pump Motor | 2018-03-04 16:32 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2018-03-09 16:31
1 | WTG-0002-NDG0-0000 | 1849692 | EM: Gearbox oil pessure too low | 2018-03-05 17:04 | Closed | GBXOIL | EM52 | BUCKEYE | BUCKEYE |  | 2018-06-06 07:48
2 | WTG-0033-NDGP-0000 | 1851724 | Replace Oil Cooler, and Add 5 Gal | 2018-03-14 07:57 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2018-07-06 07:46
1 | WTG-0117-NDG0-0000 | 1853447 | GEARBOX OIL, Fix oil leak | 2018-03-20 17:44 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2018-12-02 11:13
1 | WTG-0008-NDGP-0000 | 1853180 | GEARBOX OIL COOLER LEAKING | 2018-03-20 16:15 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | GRAND RIDGE |  | 2018-03-27 10:16
1 | GBX-000087 | 2186956 | Love joy | 2020-02-11 10:39 | Closed | GBXOIL | EM52 | CAMP SPRINGS I | CMORRIS |  | 2020-02-12 10:49
1 | WTG-0115-0000 | 1862989 | Gearbox Oil Work/Issue | 2018-04-11 15:48 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2018-07-20 12:40
2 | WTG-0019-ND00-0000 | 1863069 | Gearbox Oil Work/Issue | 2018-04-13 08:09 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TMORRIS |  | 2018-07-20 11:53
1 | WTG-0117-0000 | 1862988 | Gearbox Oil Work/Issue | 2018-04-12 15:47 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2018-07-20 12:42
1 | WTG-0055-0000 | 1862987 | Gearbox Oil Work/Issue | 2018-04-12 15:45 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2018-07-20 12:01
4.2 | WTG-0078-NDGP-0000 | 1863372 | Replace Gearbox Heat Exchanger | 2018-04-13 14:17 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2018-07-11 06:46
1 | WTG-0076-0000 | 1863022 | GEARBOX OIL, Fix oil leak | 2018-04-12 16:43 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BDIAZ |  | 2018-09-06 16:22
1 | WTG-0118-NDG0-0000 | 1862818 | Gearbox Oil Work/Issue | 2018-04-11 15:13 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | FHUBBARD |  | 2018-07-20 12:42
1 | WTG-0047-0000 | 1862825 | Gearbox Oil Work/Issue | 2018-04-11 15:34 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2018-07-20 11:59
5 | WTG-0213-NDG0-0000 | 1864814 | GEARBOX OIL, Add 5 Gallons | 2018-04-19 15:18 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2018-05-11 14:21
4 | WTG-0203B-NDGP-0000 | 1867053 | GEARBOX OIL, Replace oil pump | 2018-04-26 10:38 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2018-05-02 10:30
4 | WTG-0203B-NDGP-0000 | 1867054 | GEARBOX OIL, Replace oil pump | 2018-04-26 10:38 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2018-05-02 10:29
4 | WTG-0204A-NDG0-0000 | 1868575 | GEARBOX OIL, Add/Top-Off | 2018-04-30 15:31 | Closed | GBXOIL | GBXOILADD | FORWARD | CMITCHELL |  | 2018-05-02 10:46
2 | WTG-0063A-NDGP-0000 | 1873670 | GEARBOX OIL, Replace oil cooler | 2018-05-10 15:39 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2021-08-26 06:54
1 | WTG-0047-0000 | 1877671 | rFSA Claim- Pitch Tube Seals | 2018-05-25 14:47 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2018-06-28 17:33
1 | WTG-0028-0000 | 1877672 | rFSA Claim- Pitch Tube Seals | 2018-05-25 14:48 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2018-06-28 17:28
2 | WTG-0028-0000 | 2032448 | GEARBOX OIL, Fix oil leak | 2019-02-05 13:45 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | UPSTREAM |  | 2019-10-10 16:56
1 | WTG-0021-0000 | 1916197 | rFSA Claim for leaking Pitch Tube Seals | 2018-06-26 16:25 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | RBABIK |  | 2018-06-28 17:32
2 | WTG-0119-0000 | 3347673 | CMS Gearbox Borescope | 2024-05-07 13:36 | Closed | CMS | CMSGBXBORE | BETHEL | ABARNDT |  | 2024-05-09 14:47
1 | WTG-0093-0000 | 1925889 | GEARBOX OIL, Fix oil leak | 2018-07-18 18:43 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE3 |  | 2018-10-19 15:50
2 | WTG-0G03-NDG0-0000 | 1925992 | GEARBOX OIL, Particle counter installation | 2018-07-19 12:04 | Closed | GBXOIL | GBXPARTINS | HIGH SHELDON | SCLARK |  | 2018-09-21 10:02
4 | GBX-FDMD-4155 | 1926854 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000999 | 1926743 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000005476 | 1926744 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000669 | 1926802 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
1 | WTG-0059-0000 | 1855844 | GEARBOX OIL, Fix oil leak | 2018-03-27 14:50 | Closed | GBXOIL | GBXOILLEAK | MCADOO | MCADOO |  | 2018-03-28 16:10
1 | WTG-0044-0000 | 1856740 | GEARBOX OIL, Fix oil leak | 2018-03-28 15:45 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CWERNER |  | 2018-04-23 14:42
1 | WTG-0053-0000 | 1860904 | Follow Up Oil Sample | 2018-04-05 16:05 | Closed | GBXOIL | GBXOILSAMP | TURKEY TRACK | MSNOW | 30 | 2018-05-14 14:51
1 | WTG-0070-ND00-0000 | 1862284 | Gearbox Oil Work/Issue | 2018-04-09 14:23 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | FHUBBARD |  | 2018-07-20 12:21
1 | WTG-0053-0000 | 1862299 | Leaking Oil Pump | 2018-04-09 15:25 | Closed | GBXOIL | GBXOILLEAK | VANTAGE | VANTAGE |  | 2018-04-10 16:28
1 | WTG-0065-ND00-0000 | 1862388 | Gearbox Oil Work/Issue | 2018-04-09 17:10 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 12:20
1 | WTG-0027-ND00-0000 | 1862392 | Gearbox Oil Work/Issue | 2018-04-09 17:12 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 11:55
1 | WTG-0046-ND00-0000 | 1862377 | Gearbox Oil Work/Issue | 2018-04-09 17:04 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 11:59
1 | WTG-0045-ND00-0000 | 1862378 | Gearbox Oil Work/Issue | 2018-04-09 17:04 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 11:58
1 | WTG-0043-ND00-0000 | 1862379 | Gearbox Oil Work/Issue | 2018-04-09 17:06 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 11:58
1 | WTG-0042-ND00-0000 | 1862380 | Gearbox Oil Work/Issue | 2018-04-09 17:06 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 11:57
1 | WTG-0063-ND00-0000 | 1862387 | Gearbox Oil Work/Issue | 2018-04-09 17:10 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 12:14
1 | WTG-0082-ND00-0000 | 1862656 | Gearbox Oil Work/Issue | 2018-04-10 17:23 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TCARD |  | 2018-07-20 12:31
1 | WTG-0005-0000 | 1862991 | Gearbox Oil Work/Issue | 2018-04-12 15:54 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2018-07-20 11:47
1 | WTG-0114-NDG0-0000 | 1862829 | Gearbox Inspection | 2018-04-11 15:48 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | FHUBBARD |  | 2018-04-11 15:54
1 | WTG-0309-0000 | 1863252 | GEARBOX OIL, Fix oil leak | 2018-04-13 11:07 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | CBORER |  | 2018-04-23 14:43
1 | WTG-0090-NDG0-0000 | 1863544 | Gearbox Oil Work/Issue | 2018-04-14 14:08 | Closed | GBXOIL | EM225 | BUCKEYE | BUCKEYE |  | 2018-09-12 15:48
1 | WTG-0079-0000 | 1864832 | GEARBOX OIL, Fix oil leak | 2018-04-19 18:38 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | WBAUGUS |  | 2018-04-23 09:07
4 | WTG-0057-NY00-0000 | 1864821 | Yaw drive oil top off | 2018-04-19 16:55 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2018-08-15 16:51
2 | WTG-0057-NDD0-0000 | 1864677 | Replace generator cooling fan top box side | 2018-04-19 07:33 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2018-05-30 10:00
1 | WTG-0117-0000 | 1866512 | GEARBOX OIL, Fix oil leak | 2018-04-25 15:42 | Closed | GBXOIL | GBXOILLEAK | BETHEL | ACHAVIRA |  | 2018-04-26 17:42
5 | WTG-0058-NDG0-0000 | 1867261 | GEARBOX OIL, Add/Top-Off | 2018-04-27 07:57 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2018-05-02 10:42
1 | WTG-0037-NDG0-0000 | 1867060 | GEARBOX OIL, Particle counter removal | 2018-04-26 11:52 | Closed | GBXOIL | GBXPARTREM | FORWARD | SCLARK |  | 2018-10-05 10:32
1 | WTG-0003-NDGP-0000 | 1868511 | Oil Pump Replacement | 2018-04-30 11:49 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | SENGLAND |  | 2018-05-01 15:46
4 | WTG-0066-NDG0-0000 | 1870555 | GEARBOX OIL, Add/Top-Off 5 gallons | 2018-05-02 16:46 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2018-05-11 14:45
2 | WTG-0024-NDG0-0000 | 1871442 | GEARBOX OIL, Oil Sample | 2018-05-03 17:22 | Closed | GBXOIL | GBXOILSAMP | CAL RIDGE | SCLARK |  | 2018-08-22 13:51
1 | WTG-0012-NDGP-0000 | 1871443 | Oil Pump Replacement | 2018-05-03 17:30 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2018-05-04 11:53
5 | WTG-0082-NDG0-0000 | 1886993 | GEARBOX OIL, Add/Top-Off 10 gals | 2018-06-04 15:32 | Closed | GBXOIL | GBXOILADD | FORWARD | MPEARSON |  | 2018-07-17 16:49
4 | WTG-0044-NDGP-0000 | 1887436 | GEARBOX OIL, Replace oil spigot on filter pot | 2018-06-05 14:25 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2018-06-12 11:17
1 | WTG-0010-0000 | 1894804 | rFSA Claim for Pitch Tube Leak and UEA replacement | 2018-01-28 12:15 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | RBABIK |  | 2018-06-28 17:15
1 | WTG-0041-NDGP-0000 | 1895215 | EM: Dirty gearing oil filter (switching off) | 2018-06-22 12:26 | Closed | GBXOIL | EM71 | MCADOO | MCADOO |  | 2018-06-29 08:17
4 | WTG-0048-0000 | 1910347 | GEARBOX OIL, Add 5 Gallons Amsoil | 2018-06-25 17:21 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2018-10-05 09:29
1 | WTG-0056-0000 | 1916199 | rFSA Claim- Pitch Tube Seals | 2018-06-26 16:30 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | RBABIK |  | 2018-06-28 17:16
1 | WTG-0G01-NDG0-0000 | 1919991 | GEARBOX OIL, Particle counter installation | 2018-07-02 16:51 | Cancelled | GBXOIL | GBXPARTINS | HIGH SHELDON | SCLARK |  | 2019-03-12 13:24
2 | WTG-0025-NDG0-0000 | 1925216 | GEARBOX OIL, Particle counter troubleshooting | 2018-07-16 12:53 | Closed | GBXOIL | GBXPARTTS | MCADOO | MSNOW |  | 2018-08-29 14:44
4 | GBX-JKD-W-0000816 | 1926745 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004062 | 1926746 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000875 | 1926747 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000895 | 1926748 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000709 | 1926749 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004030 | 1926750 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004027 | 1926751 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000932 | 1926752 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004118 | 1926753 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000770 | 1926754 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004086 | 1926780 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004042 | 1926781 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000786 | 1926782 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000785 | 1926783 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004079 | 1926784 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000787 | 1926785 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000003966 | 1926786 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000836 | 1926787 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000685 | 1926788 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000822 | 1926789 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004020 | 1926790 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000708 | 1926791 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004063 | 1926792 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004053 | 1926793 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004009 | 1926794 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000830 | 1926795 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004029 | 1926796 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000949 | 1926797 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004019 | 1926798 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004043 | 1926799 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004081 | 1926800 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000704 | 1926801 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004070 | 1926803 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000748 | 1926804 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004007 | 1926805 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000809 | 1926806 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004114 | 1926810 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000707 | 1926807 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004106 | 1926808 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004072 | 1926809 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000844 | 1926811 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000767 | 1926812 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000721 | 1926813 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000691 | 1926814 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000692 | 1926815 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000672 | 1926816 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000003964 | 1926820 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004075 | 1926817 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004105 | 1926818 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000838 | 1926819 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | SYS-WTG-BUCK | 1926742 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL | GBXOILSAMP | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000723 | 1926821 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000818 | 1926822 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000003947 | 1926823 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004052 | 1926824 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004073 | 1926828 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004041 | 1926825 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000690 | 1926826 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004036 | 1926827 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004033 | 1926829 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000670 | 1926830 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004044 | 1926831 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004058 | 1926832 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004078 | 1926833 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004071 | 1926834 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000710 | 1926838 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-FDMD-4021 | 1926835 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000702 | 1926836 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000768 | 1926837 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-FDMD-4054 | 1926839 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000751 | 1926840 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004038 | 1926841 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004002 | 1926842 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000722 | 1926843 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000699 | 1926844 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004119 | 1926848 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-FDMD-4112 | 1926845 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004103 | 1926846 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004047 | 1926847 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000866 | 1926849 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004061 | 1926850 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004077 | 1926851 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000003942 | 1926852 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000817 | 1926853 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
1 | WTG-0065-NDGP-0000 | 1934541 | Install secondary filtration system on gearbox oil | 2018-08-08 12:23 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-02-26 07:49
1 | WTG-0072-NDGP-0000 | 1934549 | Install secondary filtration system on gearbox oil | 2018-08-08 12:27 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2018-09-13 17:20
2 | WTG-0H09-NDG0-0000 | 1933817 | GEARBOX OIL, Particle counter removal | 2018-08-06 10:59 | Closed | GBXOIL | GBXPARTREM | BEECH RIDGE | MSNOW |  | 2018-09-24 08:27
1 | WTG-0064-NDGP-0000 | 1934540 | Install secondary filtration system on gearbox oil | 2018-08-08 12:21 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-03-01 09:43
1 | WTG-0067-NDGP-0000 | 1934543 | Install secondary filtration system on gearbox oil | 2018-08-08 12:24 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-02-13 11:08
1 | WTG-0067-NDGP-0000 | 1934544 | Install secondary filtration system on gearbox oil | 2018-08-08 12:24 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-02-13 11:08
1 | WTG-0061-NDGP-0000 | 1934537 | Install secondary filtration system on gearbox oil | 2018-08-08 12:16 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-02-28 11:23
1 | WTG-0062-NDGP-0000 | 1934538 | Install secondary filtration system on gearbox oil | 2018-08-08 12:19 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-03-04 14:08
1 | WTG-0066-NDGP-0000 | 1934542 | Install secondary filtration system on gearbox oil | 2018-08-08 12:24 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2018-08-13 17:05
1 | WTG-0073-NDGP-0000 | 1934553 | Install secondary filtration system on gearbox oil | 2018-08-08 12:28 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-02-01 15:05
1 | WTG-0075-NDGP-0000 | 1934555 | Install secondary filtration system on gearbox oil | 2018-08-08 12:28 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-01-30 07:47
1 | WTG-0076-NDGP-0000 | 1934556 | Install secondary filtration system on gearbox oil | 2018-08-08 12:29 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2020-08-12 07:51
1 | WTG-0077-NDGP-0000 | 1934557 | Install secondary filtration system on gearbox oil | 2018-08-08 12:29 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2018-08-16 18:38
1 | WTG-0078-NDGP-0000 | 1934558 | Install secondary filtration system on gearbox oil | 2018-08-08 12:29 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2018-08-14 17:21
1 | WTG-0029-0000 | 1935209 | GEARBOX OIL, Fix oil leak | 2018-08-09 09:59 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | MCALVERT
1 | WTG-0038-0000 | 1940294 | GEARBOX OIL, Fix oil leak - outlet hose fitting | 2018-08-22 18:31 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE
4 | WTG-0021-NDG0-0000 | 1959790 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2018-10-10 17:07 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2018-10-12 13:05
5 | WTG-0027-NDG0-0000 | 1960216 | Add 5 gal oil | 2018-10-12 07:49 | Closed | GBXOIL | GBXOILADD | FORWARD | CMITCHELL |  | 2019-02-12 14:28
1 | WTG-0051-0000 | 1961112 | Replaced Cooler to thermal bypass manifold hose | 2018-10-17 09:36 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2019-04-09 16:12
1 | WTG-0107-0000 | 1969229 | GEARBOX OIL, Fix oil leak | 2018-11-02 13:00 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2018-11-14 07:25
3 | WTG-0032-NDG0-0000 | 1983475 | Gearbox oil sample | 2018-11-14 10:55 | Closed | GBXOIL | GBXOILSAMP | FORWARD | KLEFFELMAN |  | 2018-11-16 14:33
4 | GBX-737000004010 | 2011817 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
1 | GBX-000137 | 1992283 | GEARBOX OIL, Fix oil leak | 2018-12-04 16:09 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | LPIERCE |  | 2019-03-27 10:07
1 | WTG-0087-0000 | 1993030 | GEARBOX OIL, Fix oil leak | 2018-12-06 17:32 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE
4 | WTG-0096-NDG0-0000 | 2003052 | GEARBOX OIL, Top-Off about 2-3 Gallons of Amsoil | 2018-12-18 15:39 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-04-05 14:54
1 | WTG-0098-0000 | 1935790 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2018-08-09 08:37 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | KMCLELAND |  | 2018-08-20 13:53
1 | WTG-0083-0000 | 1935789 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2018-08-07 07:24 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | KMCLELAND |  | 2018-08-20 13:53
1 | WTG-0070-NDGP-0000 | 1935739 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2018-08-11 18:52 | Closed | GBXOIL | GBXOILCOOL | CAMP SPRINGS I | AMELIN |  | 2018-08-15 09:17
4 | WTG-0082-NDGP-0000 | 1940217 | GEARBOX OIL, Secondary filter system element change | 2018-08-22 10:40 | Closed | GBXOIL | GBXFILTELEM | FORWARD | KLEFFELMAN |  | 2018-12-18 13:21
1 | GBX-000130 | 1941609 | EM: Gearbox oil pessure too low | 2018-08-27 17:51 | Closed | GBXOIL | EM52 | BISHOP HILL | KCOOPER |  | 2018-10-10 08:56
4 | WTG-0046-NDG0-0000 | 1953859 | GEARBOX OIL, Add/Top-Off5 gals | 2018-09-27 11:21 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2019-01-24 10:04
5 | WTG-0087-NDG0-0000 | 1954555 | GEARBOX OIL, Add/Top-Off 5 gal of gear oil | 2018-09-28 19:24 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2019-02-05 09:11
4 | WTG-0020-NDGP-0000 | 1957179 | Gearbox Pump to filter flange is leaking | 2018-10-03 07:36 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2018-10-05 09:44
4 | WTG-0020-NDGP-0000 | 1957180 | Oil cooler vent tube fell off. | 2018-10-03 07:41 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2018-10-05 09:44
1 | WTG-0006-0000 | 1957535 | GEARBOX OIL, Clean oil out of belly | 2018-10-03 16:33 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TCARD
4 | WTG-0107-NDG0-0000 | 1958764 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2018-10-08 08:54 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-01-02 09:42
2 | WTG-0101-0000 | 1966315 | Radiator Needed | 2018-10-30 17:19 | Closed | GBXOIL | GBXOILADD | CAMP SPRINGS II | CAMP SPRINGS |  | 2018-11-15 17:02
1 | WTG-0001-0000 | 1969437 | GEARBOX OIL, Add/Top-Off | 2018-11-02 18:52 | Closed | GBXOIL | GBXOILADD | BUFFALO MOUNT | CRO EAST |  | 2019-01-07 13:33
1 | GBX-000041 | 1982262 | EM: Gearbox oil pessure too low | 2018-11-08 07:47 | Closed | GBXOIL | EM52 | ORANGEVILLE | NSPINK |  | 2018-11-09 09:27
2 | WTG-0081-0000 | 1982855 | GEARBOX OIL, Add/Top-Off | 2018-11-09 22:01 | Cancelled | GBXOIL | GBXOILADD | CAL RIDGE | RWALL
5 | WTG-0032-0000 | 1983105 | Filter housing clamps needed | 2018-11-12 16:27 | Closed | GBXOIL | GBXFILTINS | GOLDTHWAITE | GOLDTHWAITE |  | 2019-06-06 17:16
4 | GBX-737000003999 | 2011812 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004002 | 2011813 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004005 | 2011814 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004007 | 2011815 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004009 | 2011816 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
5 | WTG-0011-NDGP-0000 | 1992564 | Oil Pump Replacement | 2018-12-05 16:12 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2018-12-10 13:42
4 | WTG-0073-NDGP-0000 | 1993070 | GEARBOX OIL, Add/Top-Off | 2018-12-07 07:38 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2019-04-10 12:41
1 | WTG-0090-0000 | 1994962 | GEARBOX OIL, Secondary filter system installation | 2018-12-11 16:29 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | BUCKEYE |  | 2022-06-29 16:30
2 | WTG-0041A-NDGP-0000 | 2159233 | Replace gear oil coupling | 2019-12-04 08:47 | Closed | GBXOIL | GBXOILCOOL | FORWARD | MPEARSON |  | 2020-01-06 16:21
5 | WTG-0089-NDGP-0000 | 2000573 | TADS, Gearbox Cooling System - Mechanical Issue | 2018-12-16 08:42 | Closed | GBXOIL | GBXOILCOOL | GREXP | GRAND RIDGE |  | 2019-01-03 12:46
1 | WTG-0132-NDG0-0000 | 2003282 | GEARBOX OIL, Particle counter installation | 2018-12-19 17:35 | Cancelled | GBXOIL | GBXPARTINS | CAMP SPRINGS II | JSULLIVAN |  | 2019-09-17 09:19
4 | WTG-0203B-NDGP-0000 | 2015901 | Oil Cooler Filter Needed | 2019-01-08 15:58 | Closed | GBXOIL | GBXFILTELEM | FORWARD | FORWARD |  | 2019-05-03 10:25
4 | WTG-0056-NDG0-0000 | 2019554 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
2 | WTG-0009-0000 | 2003517 | GEARBOX OIL, Oil Sample | 2018-12-20 13:43 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS I | CMORALES |  | 2019-03-05 19:50
1 | WTG-0067-0000 | 2004654 | GEARBOX OIL, Replace hoses. | 2018-12-21 16:06 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TMORRIS
4 | WTG-0096-NDG0-0000 | 2016069 | GEARBOX OIL, Secondary filter system element change | 2019-01-09 10:31 | Closed | GBXOIL | GBXFILTELEM | FORWARD | SCLARK |  | 2019-04-05 15:22
4 | WTG-0050-NDG0-0000 | 2019548 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0051-NDG0-0000 | 2019549 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0052-NDG0-0000 | 2019550 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0053-NDG0-0000 | 2019551 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0054-NDG0-0000 | 2019552 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0055-NDG0-0000 | 2019553 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0057-NDG0-0000 | 2019555 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0061-NDG0-0000 | 2019559 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0058-NDG0-0000 | 2019556 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0059-NDG0-0000 | 2019557 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0060-NDG0-0000 | 2019558 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0062-NDG0-0000 | 2019560 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0063-NDG0-0000 | 2019561 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0064-NDG0-0000 | 2019562 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0065-NDG0-0000 | 2019563 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0066-NDG0-0000 | 2019564 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0067-NDG0-0000 | 2019565 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0068-NDG0-0000 | 2019566 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0072-NDG0-0000 | 2019570 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0069-NDG0-0000 | 2019567 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0070-NDG0-0000 | 2019568 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0071-NDG0-0000 | 2019569 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0073-NDG0-0000 | 2019571 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0077-NDG0-0000 | 2019575 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0074-NDG0-0000 | 2019572 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0075-NDG0-0000 | 2019573 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0076-NDG0-0000 | 2019574 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0078-NDG0-0000 | 2019576 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0079-NDG0-0000 | 2019577 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0080-NDG0-0000 | 2019578 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0081-NDG0-0000 | 2019579 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0025-NDG0-0000 | 2019523 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0022-NDG0-0000 | 2019520 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0023-NDG0-0000 | 2019521 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0024-NDG0-0000 | 2019522 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0026-NDG0-0000 | 2019524 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0029-NDG0-0000 | 2019527 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | SYS-WTG-BETH | 2019498 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL | GBXOILSAMP | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0027-NDG0-0000 | 2019525 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0028-NDG0-0000 | 2019526 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
5 | WTG-0047-NDGP-0000 | 2024501 | Replace gearbox oil pump | 2019-01-22 07:57 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2019-04-05 15:37
1 | WTG-0036-0000 | 2027507 | GEARBOX OIL, Replace Leaking Hoses | 2019-01-29 21:56 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | CPRUIT
2 | WTG-0089-NDGP-0000 | 2030561 | GEARBOX OIL, Oil Sample | 2019-02-04 09:04 | Closed | GBXOIL | GBXOILSAMP | FORWARD | GOTKIN |  | 2019-02-05 09:33
1 | WTG-0098-0000 | 2047599 | Oil leak | 2019-03-01 07:00 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | CDEVOLL |  | 2019-03-06 07:37
1 | WTG-0085-0000 | 2053097 | GEARBOX OIL, Fix oil leak | 2019-03-19 16:56 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CHORN |  | 2021-06-07 08:12
2 | WTG-0030-NDG0-0000 | 2620591 | Bring 1 gal pail to empty gear oil catch bucket. | 2021-10-20 06:48 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2021-11-02 06:23
1 | WTG-0013-0000 | 2055892 | 2019 Padmount Oil Sample | 2019-03-27 15:34 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-04-18 13:38
3 | WTG-0006-NDG0-0000 | 2058345 | Gearbox running too hot | 2019-04-01 09:02 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-07-10 08:18
1 | WTG-0312-0000 | 2064134 | GEARBOX OIL, Oil Sample | 2019-04-09 14:05 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL III | KCOOPER |  | 2019-06-13 07:58
1 | WTG-0010-0000 | 2067597 | Oil Inlet hose rubbing on flooring frame | 2019-04-22 15:57 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | SOSTERLOH |  | 2021-09-06 22:26
1 | WTG-0071-0000 | 2069371 | GEARBOX OIL, Fix oil leak | 2019-04-26 16:01 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CWERNER
4.2 | WTG-0097-NDGP-0000 | 2075689 | Replace Gearbox Heat Exchanger | 2019-05-09 08:43 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2019-07-15 06:56
1 | WTG-0216-0000 | 2092492 | GEARBOX OIL, Fix oil leak | 2019-06-12 17:52 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SCEXP |  | 2020-01-10 11:15
4.2 | WTG-0096-NDGP-0000 | 2094160 | Replace Gearbox Heat Exchanger | 2019-06-20 07:31 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2019-07-11 09:17
1 | WTG-0078-0000 | 2094200 | GEARBOX OIL, Fix oil leak | 2019-06-20 13:11 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | TURKEY TRACK |  | 2020-04-30 11:31
5 | WTG-0020-NDG0-0000 | 2096470 | GEARBOX, gasket/sealant needed | 2019-06-26 14:14 | Closed | GBXOIL | GBXOILLEAK | FORWARD | MPEARSON |  | 2020-09-30 12:01
1 | GBX-000113 | 2104089 | GEARBOX OIL, Fix oil leak | 2019-07-17 13:40 | Cancelled | GBXOIL | GBXOILLEAK | GRAND RIDGE | GRAND RIDGE |  | 2023-06-29 13:16
4 | WTG-0050-NDG0-0000 | 2105388 | 5 gallons oil needed | 2019-07-23 15:47 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2019-09-25 11:12
1 | WTG-0305-0000 | 2105402 | GEARBOX OIL, Fix oil leak | 2019-07-23 16:46 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | PRAIRIE BREEZE3 |  | 2019-12-10 16:26
5 | WTG-0050-NDG0-0000 | 2105386 | Pump to oil cooler inlet hose leaking at plastic block | 2019-07-23 11:48 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2020-02-12 16:17
1 | BMEC-WTG-006 | 2105329 | WTG006 - Thermoerror Nacelle Fan F313 | 2019-07-23 09:58 | Closed | GBXOIL |  | BUFFALO MOUNT | CPARKS |  | 2019-09-30 08:50
1 | WTG-0016-0000 | 2113618 | GEARBOX OIL, Fix oil leak | 2019-08-12 11:14 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | NSCHMEIDLER |  | 2021-02-02 10:59
2 | WTG-0037-0000 | 2114331 | Secondary filter system element change | 2019-08-14 09:04 | Closed | GBXOIL | GBXFILTELEM | WOLVERINE CREEK | WOLVERINECREEK |  | 2019-12-09 15:46
4 | WTG-0065-NDGP-0000 | 2114905 | Install grommets on the oil pump motor. | 2019-08-16 11:32 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2020-09-30 12:02
1 | WTG-0211-NDG0-0000 | 2114788 | GEARBOX OIL, Fix oil leak | 2019-08-15 16:59 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | AHOFFMANN |  | 2021-08-30 15:12
1 | WTG-0099-0000 | 2116274 | GEARBOX OIL, Fix oil leak | 2019-08-21 14:43 | Closed | GBXOIL | GBXOILLEAK | MCADOO | MCADOO |  | 2019-08-21 14:55
1 | WTG-0003-0000 | 2116315 | Replace Leaking GBX Oil Hose | 2019-08-21 16:10 | Closed | GBXOIL | GBXOILLEAK | SANTA RITA EAST | AVILLARREAL |  | 2019-08-23 10:52
4 | WTG-0211A-NDG0-0000 | 2117767 | 5 gallons oil needed | 2019-08-26 10:55 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2020-01-06 16:12
4 | WTG-0211A-NDGP-0000 | 2117768 | Gbx oil pump leaking | 2019-08-26 10:56 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2020-01-06 16:12
1 | WTG-0007-NDG0-0000 | 2119780 | GEARBOX OIL, Particle counter troubleshooting | 2019-08-29 18:02 | Closed | GBXOIL | GBXPARTTS | GUNSIGHT | RPPATEL |  | 2019-08-30 16:46
2 | WTG-0104-NDG0-0000 | 2127449 | Rewitec additive by GE rFSA | 2019-09-18 14:13 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JHAVENS |  | 2019-09-18 14:15
2 | WTG-0135-NDG0-0000 | 2127450 | Rewitec additive by GE rFSA | 2019-09-18 14:13 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JHAVENS |  | 2019-09-18 14:15
2 | WTG-0113-NDG0-0000 | 2127448 | Rewitec additive by GE rFSA | 2019-09-18 14:10 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JHAVENS |  | 2019-09-18 14:15
5 | WTG-0053-0000 | 2128286 | Oil cooler filter needs magnets | 2019-09-23 14:22 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2020-01-17 10:10
1 | WTG-0125-NDGP-0000 | 2022800 | Needs pump inversion ( leaking ) | 2019-01-16 15:43 | Closed | GBXOIL | GBXOILCOOL | GREXP | GRAND RIDGE |  | 2019-02-21 14:32
1 | WTG-0055-0000 | 2036079 | GEARBOX OIL, Fix oil leak | 2019-02-13 17:13 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | AHOFFMANN |  | 2019-02-22 17:21
2 | WTG-0022-NDGP-0000 | 2038822 | GEARBOX OIL, Fix oil leak | 2019-02-19 17:22 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | WILLOWCREEK |  | 2019-08-09 09:31
5 | WTG-0002C-NDG0-0000 | 2052406 | GEARBOX OIL, Add/Top-Off 5 gallons of Amsoil | 2019-03-14 13:16 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2019-04-22 12:40
1 | WTG-0008-0000 | 2052372 | GEARBOX OIL, Fix oil leak | 2019-03-14 11:44 | Closed | GBXOIL | GBXOILLEAK | BETHEL | BETHEL |  | 2019-04-04 17:48
4 | WTG-0042-NDGP-0000 | 2053337 | GEARBOX OIL, replace hose from filter housing to oil cooler | 2019-03-20 15:47 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2019-08-16 13:59
4 | WTG-0042-NDGP-0000 | 2053341 | GEARBOX OIL, Add/Top-Off | 2019-03-20 18:20 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2019-07-05 08:38
1 | WTG-0057-0000 | 2053798 | GEARBOX OIL, Fix oil leak | 2019-03-21 15:57 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE
1 | WTG-0043-0000 | 2054633 | GEARBOX OIL, Particle counter troubleshooting | 2019-03-25 11:07 | Closed | GBXOIL | GBXPARTTS | GUNSIGHT | CMORALES |  | 2019-08-20 15:19
1 | WTG-0048-0000 | 2054634 | GEARBOX OIL, Particle counter troubleshooting | 2019-03-25 11:09 | Closed | GBXOIL | GBXPARTTS | GUNSIGHT | CMORALES |  | 2019-08-20 16:43
1 | WTG-0010-0000 | 2055366 | GEARBOX OIL, Fix oil leak | 2019-03-26 07:48 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2019-04-02 07:26
1 | WTG-0042-0000 | 2057256 | GEARBOX OIL, Fix oil leak | 2019-03-29 16:34 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CWERNER
2 | WTG-0039-NDGP-0000 | 2065425 | GEARBOX OIL, Replace oil pump and motor | 2019-04-16 09:53 | Closed | GBXOIL | GBXOILCOOL | FORWARD | MPEARSON |  | 2019-04-18 10:51
1 | GBX-000016 | 2067611 | EM: Gearbox oil pessure too low | 2019-04-22 17:42 | Closed | GBXOIL | EM52 | SPRING CANYON | SPRINGCANYON |  | 2019-04-24 15:10
4.2 | WTG-0077-NDGP-0000 | 2069908 | Replace Gearbox Heat Exchanger | 2019-04-29 10:41 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2019-06-26 06:31
1 | WTG-0003-0000 | 2080996 | Replace Oil Cooler outlet to GBX hose | 2019-05-30 10:41 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH |  | 2019-07-09 16:02
1 | WTG-0069-0000 | 2110806 | GEARBOX OIL, Fix oil leak | 2019-08-02 08:06 | Closed | GBXOIL | GBXOILLEAK | MCADOO | MCADOO |  | 2019-08-06 13:20
1 | WTG-0005-0000 | 2111466 | GEARBOX OIL, Fix oil leak | 2019-08-06 09:15 | Closed | GBXOIL | GBXOILLEAK | MCADOO | MCADOO |  | 2019-08-07 09:01
5 | WTG-0093-0000 | 2114371 | GEARBOX OIL, Particle counter troubleshooting | 2019-08-14 10:58 | Cancelled | GBXOIL | GBXPARTTS | GRATIOT | NFALASZ |  | 2019-08-27 08:41
8 | WTG-0013-NDG0-0000 | 2117325 | Add oil additive to main gearbox | 2019-08-26 08:45 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-09-30 14:48
1 | WTG-0086-0000 | 2125402 | GEARBOX OIL, Fix oil leak | 2019-09-07 07:45 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KMCLELAND |  | 2019-09-10 07:39
2 | WTG-0310-0000 | 2130168 | GEARBOX OIL, Fix oil leak | 2019-09-26 17:56 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | AHOFFMANN |  | 2022-10-28 16:25
1 | WTG-0312-0000 | 2130133 | GEARBOX OIL, Oil Sample | 2019-09-26 15:05 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL III | BISHOP HILL |  | 2019-09-27 11:59
1 | WTG-0113-0000 | 2136253 | Bypass hose is seeping pump to gbx | 2019-10-09 09:14 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2022-05-23 16:55
2 | WTG-0006-NDG0-0000 | 2136043 | gearbox running too hot | 2019-10-08 09:03 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-10-10 09:26
2 | WTG-0099-0000 | 2141903 | GEARBOX OIL, verification of oil level. | 2019-10-25 16:15 | Closed | GBXOIL | GBXOILADD | TURKEY TRACK | JBRILEY |  | 2019-10-25 16:20
4 | WTG-0F06-NDGP-0000 | 2145578 | GEARBOX OIL, Oil Sample | 2019-11-01 11:55 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | MSNOW |  | 2020-06-05 13:33
4 | WTG-0K01-NDGP-0000 | 2145581 | GEARBOX OIL, Oil Sample | 2019-11-01 11:56 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | MSNOW |  | 2020-07-07 06:53
9 | WTG-0240-0000 | 2225085 | GEARBOX, Oil Change | 2020-05-19 15:26 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:41
1 | WTG-0222-0000 | 2153427 | GEARBOX OIL, Fix oil leak | 2019-11-20 07:49 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NHEITHOFF |  | 2019-12-23 15:42
1 | WTG-0043-NDGP-0000 | 2155501 | GEARBOX OIL, Fix oil leak | 2019-11-25 15:01 | Closed | GBXOIL | GBXOILLEAK | VANTAGE | VANTAGE |  | 2020-10-27 09:53
1 | WTG-0001-NDG0-0000 | 2228590 | Add Gearbox oil | 2020-05-29 13:14 | Cancelled | GBXOIL | BLANK | GORDON BUTTE | JUDITHGAP |  | 2020-08-24 16:04
1 | WTG-0317-0000 | 2164168 | GEARBOX OIL, Fix oil leak | 2019-12-20 13:26 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | JSTAHLECKER |  | 2020-02-17 14:53
2 | WTG-0024-NDGP-0000 | 2172315 | GEARBOX OIL, Replace oil pump | 2020-01-09 16:31 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2020-04-01 14:24
1 | WTG-0014-0000 | 2174474 | rFSA Claim: Leaking pitch tube seals | 2020-01-17 15:16 | Cancelled | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-17 13:29
5 | WTG-0081-NDGP-0000 | 2175715 | GEARBOX OIL, Add 5gals | 2020-01-24 11:18 | Closed | GBXOIL | GBXOILADD | FORWARD | MPEARSON |  | 2020-02-05 14:18
1 | WTG-0014-0000 | 2183532 | GEARBOX OIL, Fix oil leak | 2020-02-05 05:46 | Closed | GBXOIL | GBXOILLEAK | BUFFALO MOUNT | SBAY |  | 2020-05-21 13:47
1 | GBX-000151 | 2185418 | GEARBOX OIL, Fix oil leak | 2020-02-07 08:56 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MMEADOWS |  | 2020-02-10 07:41
3 | WTG-0205-NDG0-0000 | 2185293 | GEARBOX OIL, Particle counter installation | 2020-02-06 16:03 | Closed | GBXOIL | GBXPARTINS | PRAIRIE BREEZE2 | RPPATEL |  | 2020-11-12 15:34
2 | WTG-0113-NDG0-0000 | 2186110 | Rewitec filter change, Borescope by GE rFSA | 2020-02-07 16:06 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JHAVENS |  | 2020-02-07 16:11
2 | WTG-0135-NDG0-0000 | 2186111 | Rewitec filter change, Borescope by GE rFSA | 2020-02-07 16:06 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JHAVENS |  | 2020-02-07 16:13
2 | WTG-0321-NDG0-0000 | 2198217 | GEARBOX OIL, Add/Top-Off | 2020-03-12 09:08 | Closed | GBXOIL | GBXOILADD | BISHOP HILL III | MBUCK |  | 2020-03-12 15:33
2 | WTG-0015-0000 | 2198389 | GEARBOX OIL, Fix oil leak WC# 3617254 | 2020-03-12 14:52 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | NHEITHOFF |  | 2021-01-13 21:55
4 | WTG-0055A-NDG0-0000 | 2198413 | Replace Gearbox Hose (Filter to Cooler) | 2020-03-12 11:57 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2020-10-09 07:21
1 | WTG-0218-0000 | 2199216 | GEARBOX OIL, Fix oil leak | 2020-03-17 13:25 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | JFERRIS |  | 2020-10-13 13:39
1 | WTG-039E-0000 | 2199063 | Replace filter housing /Fix oil leak, | 2020-03-16 14:22 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | ABRADSHAW |  | 2021-03-09 13:15
4 | WTG-0095-NDG0-0000 | 2257941 | Return oil cooler hose replacement | 2020-08-12 06:41 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2021-03-01 14:38
2 | WTG-0221-NDG0-0000 | 2222933 | All 3 oil hoses are sweating nanjing | 2020-05-14 13:18 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | JFERRIS |  | 2020-06-11 16:29
1 | WTG-0215-HPA2-G000 | 2222934 | GEARBOX OIL, Fix oil leak | 2020-05-14 13:51 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | JFERRIS |  | 2020-07-30 14:40
2 | WTG-0032-NDG0-0000 | 2223092 | replace cooler to gearbox hose | 2020-05-15 13:11 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JUDITHGAP |  | 2020-06-08 08:17
9 | WTG-0210-0000 | 2225071 | GEARBOX, Oil Change | 2020-05-19 15:21 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:40
9 | WTG-0234-0000 | 2225079 | GEARBOX, Oil Change | 2020-05-19 15:24 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:40
9 | WTG-0235-0000 | 2225080 | GEARBOX, Oil Change | 2020-05-19 15:25 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:41
9 | WTG-0236-0000 | 2225081 | GEARBOX, Oil Change | 2020-05-19 15:25 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:41
9 | WTG-0237-0000 | 2225083 | GEARBOX, Oil Change | 2020-05-19 15:25 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:41
9 | WTG-0238-0000 | 2225084 | GEARBOX, Oil Change | 2020-05-19 15:26 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:41
9 | WTG-0305-0000 | 2225089 | GEARBOX, Oil Change | 2020-05-19 15:28 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE3 | MCASPER |  | 2020-07-30 14:41
9 | WTG-0310-0000 | 2225092 | GEARBOX, Oil Change | 2020-05-19 15:28 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE3 | MCASPER |  | 2020-07-30 14:41
9 | WTG-0318-0000 | 2225093 | GEARBOX, Oil Change | 2020-05-19 15:29 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE3 | MCASPER |  | 2020-07-30 14:41
9 | WTG-0206-0000 | 2225070 | GEARBOX, Oil Change | 2020-05-19 15:20 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:40
9 | WTG-0212-0000 | 2225072 | GEARBOX, Oil Change | 2020-05-19 15:21 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:40
9 | WTG-0213-0000 | 2225074 | GEARBOX, Oil Change | 2020-05-19 15:22 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:40
9 | WTG-0230-0000 | 2225078 | GEARBOX, Oil Change | 2020-05-19 15:24 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:40
9 | WTG-0241-0000 | 2225086 | GEARBOX, Oil Change | 2020-05-19 15:26 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:41
9 | WTG-0302-0000 | 2225087 | GEARBOX, Oil Change | 2020-05-19 15:27 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE3 | MCASPER |  | 2020-07-30 14:41
9 | WTG-0304-0000 | 2225088 | GEARBOX, Oil Change | 2020-05-19 15:27 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE3 | MCASPER |  | 2020-07-30 14:41
9 | WTG-0309-0000 | 2225090 | GEARBOX, Oil Change | 2020-05-19 15:28 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE3 | MCASPER |  | 2020-07-30 14:41
1 | WTG-0048-0000 | 2233635 | GEARBOX OIL, Fix oil leak/finish hub maintenance | 2020-06-05 11:15 | Closed | GBXOIL | GBXOILLEAK | BETHEL | HFLORESGONZALEZ |  | 2020-06-05 16:02
1 | WTG-0J04-NDG0-0000 | 2236970 | GEARBOX OIL, Particle counter installation | 2020-06-19 12:44 | Closed | GBXOIL | GBXPARTINS | HIGH SHELDON | NFALASZ |  | 2024-02-21 09:16
4 | WTG-0012-0000 | 2242391 | GEARBOX OIL, Add/Top-Off | 2020-07-01 12:52 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-07-06 14:28
1 | WTG-0031-0000 | 2255575 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2020-08-05 11:14 | Closed | GBXOIL | GBXOILCOOL | ORANGEVILLE | ECOPELAND |  | 2020-08-06 06:54
1 | WTG-0039-0000 | 2246193 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2020-07-13 17:11 | Closed | GBXOIL | GBXOILCOOL | BUCKEYE | BUCKEYE |  | 2020-07-27 15:23
1 | WTG-0103-0000 | 2247003 | GEARBOX OIL, Fix oil leak | 2020-07-15 14:28 | Closed | GBXOIL | GBXOILLEAK | BETHEL | BCRUTCHFIELD |  | 2020-12-14 15:31
2 | WTG-0301-0000 | 2252353 | GEARBOX OIL, Fix oil leak - Replace all 3 cooler hoses | 2020-07-31 09:19 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | NHEITHOFF |  | 2021-11-17 17:20
2 | WTG-0227-0000 | 2252946 | GEARBOX OIL, Fix oil leak - Cooler Hose | 2020-07-31 16:57 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NHEITHOFF |  | 2020-10-13 13:39
4 | WTG-0210A-0000 | 2258316 | Mount for secondary filter pump needs to be tightened | 2020-08-12 15:27 | Closed | GBXOIL | GBXFILTINS | FORWARD | JLAWRENCE |  | 2021-03-01 14:39
4.1 | WTG-0211A-0000 | 2258318 | Gearbox oil leak from the front (O'Hain Oil Bucket) | 2020-08-12 20:27 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE
3 | WTG-0005-NDG0-0000 | 2258696 | GBX oil pump inversion | 2020-08-14 11:21 | Closed | GBXOIL | GBXOILCOOL | GORDON BUTTE | JUDITHGAP |  | 2021-04-28 09:36
1 | WTG-0J02-0000 | 2273462 | GEARBOX OIL, Secondary filter system installation | 2020-08-25 07:21 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2022-09-08 09:25
1 | WTG-0054-N000-0000 | 2282054 | GEARBOX OIL, Fix oil leak | 2020-09-02 15:52 | Closed | GBXOIL | GBXOILLEAK | MCADOO | MCADOO |  | 2020-09-03 07:58
5 | WTG-0074A-0000 | 2282847 | GEARBOX OIL, Add about 5 gallons | 2020-09-04 12:52 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-10-29 10:50
3 | WTG-0019-0000 | 2283603 | GEARBOX OIL, Fix oil leak | 2020-09-09 13:34 | Closed | GBXOIL | GBXOILLEAK | BETHEL | BCRUTCHFIELD |  | 2021-02-26 15:25
4 | WTG-0003A-NDG0-0000 | 2131657 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2019-09-30 22:15 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-12-13 11:28
1 | WTG-0070-0000 | 2136935 | GEARBOX OIL, Fix oil leak | 2019-10-11 17:52 | Closed | GBXOIL | GBXOILLEAK | SANTA RITA EAST | HGARCIA |  | 2019-12-17 08:43
1 | WTG-0308-0000 | 2136940 | Belly full of oil | 2019-10-11 19:40 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | AHOFFMANN |  | 2019-10-18 09:01
1 | BMEC-DT-006 | 2137204 | WTG006 - Low Oil Pressure | 2019-10-14 15:17 | Closed | GBXOIL |  | BUFFALO MOUNT | CPARKS |  | 2019-12-10 08:49
2 | WTG-0086-NDG0-0000 | 2141801 | gearbox running too hot | 2019-10-25 09:14 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-10-29 09:45
2 | WTG-0007-NDG0-0000 | 2141840 | gearbox running too hot | 2019-10-25 09:15 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-11-20 14:52
2 | WTG-0011-NDG0-0000 | 2141841 | gearbox running too hot | 2019-10-25 09:16 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-11-20 16:56
2 | WTG-0119-N000-0000 | 2141843 | GEARBOX OIL, Add/Top-Off | 2019-10-25 09:14 | Closed | GBXOIL | GBXOILADD | CAMP SPRINGS II | CAMP SPRINGS |  | 2019-11-26 15:53
4 | WTG-0G05-NDGP-0000 | 2145580 | GEARBOX OIL, Oil Sample | 2019-11-01 11:56 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | MSNOW |  | 2020-06-11 07:34
4 | WTG-0G04-NDGP-0000 | 2145579 | GEARBOX OIL, Oil Sample | 2019-11-01 11:55 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | MSNOW |  | 2020-06-11 07:34
4 | WTG-0K04-NDGP-0000 | 2145582 | GEARBOX OIL, Oil Sample | 2019-11-01 11:57 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | MSNOW |  | 2020-07-09 08:37
2 | WTG-0109-0000 | 2148132 | GEARBOX OIL, Oil Sample | 2019-11-08 10:16 | Closed | GBXOIL | GBXOILSAMP | SANTA RITA EAST | JGASTON |  | 2019-12-02 11:02
1 | GBX-000002 | 2155875 | EM: Gearbox oil level too low | 2019-11-26 10:42 | Closed | GBXOIL | EM51 | CAMP SPRINGS II | CAMP SPRINGS |  | 2019-11-27 15:30
1 | WTG-0313-0000 | 2162154 | GEARBOX OIL, Oil Sample | 2019-12-12 09:01 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL III | KCOOPER |  | 2020-01-02 08:21
5 | WTG-0229-0000 | 2163678 | GEARBOX OIL, Fix oil leak | 2019-12-19 08:50 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | RKUDERA |  | 2024-03-22 16:34
2 | WTG-0127-NDGP-0000 | 2174226 | GEARBOX OIL, Secondary filter system element change | 2020-01-16 15:22 | Cancelled | GBXOIL | GBXFILTELEM | GREXP | GRAND RIDGE |  | 2023-06-29 09:04
1 | GBX-000101 | 2177808 | GEARBOX OIL, Fix oil leak | 2020-01-27 09:55 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2020-11-02 14:57
2 | WTG-0104-NDG0-0000 | 2186105 | Rewitec filter change, Borescope by GE rFSA | 2020-02-07 16:05 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JHAVENS |  | 2020-02-10 07:40
1 | WTG-0337-0000 | 2187790 | GEARBOX OIL, Fix oil leak | 2020-02-14 09:13 | Closed | GBXOIL | GBXOILLEAK | BISHOP HILL III | BISHOP HILL |  | 2020-03-10 12:45
1 | WTG-0339-0000 | 2187791 | GEARBOX OIL, Fix oil leak | 2020-02-14 09:21 | Closed | GBXOIL | GBXOILLEAK | BISHOP HILL III | BISHOP HILL |  | 2023-03-21 08:13
1 | WTG-0340-0000 | 2187792 | GEARBOX OIL, Fix oil leak | 2020-02-14 09:23 | Closed | GBXOIL | GBXOILLEAK | BISHOP HILL III | BISHOP HILL |  | 2020-08-06 13:48
1 | WTG-0303-0000 | 2187794 | GEARBOX OIL, Fix oil leak | 2020-02-14 09:24 | Closed | GBXOIL | GBXOILLEAK | BISHOP HILL III | BISHOP HILL |  | 2020-05-20 08:37
4 | WTG-0012-NDG0-0000 | 2192519 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0013-NDG0-0000 | 2192520 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0014-NDG0-0000 | 2192521 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0045-NDG0-0000 | 2192552 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0046-NDG0-0000 | 2192553 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0047-NDG0-0000 | 2192554 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0048-NDG0-0000 | 2192555 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0072A-NDGP-0000 | 2198847 | Replace red spider in gear oil pump | 2020-03-15 12:56 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2020-08-07 10:18
4 | WTG-0023A-0000 | 2202338 | 5 gallon oil add | 2020-03-28 10:46 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2020-05-19 11:04
4 | WTG-0019-NDGP-0000 | 2207553 | GEARBOX OIL, Particle counter troubleshooting | 2020-04-10 09:18 | Closed | GBXOIL | GBXPARTTS | WILLOW CREEK | MSNOW |  | 2020-06-01 10:43
1 | WTG-0083-0000 | 2210463 | GEARBOX OIL, Fix oil leak | 2020-04-25 14:53 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDEWEESE |  | 2020-04-28 08:27
9 | WTG-0222-0000 | 2225077 | GEARBOX, Oil Change | 2020-05-19 15:23 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:40
2 | WTG-0034-0000 | 2229211 | GEARBOX OIL, Add/Top-Off/Clean up | 2020-05-31 14:14 | Closed | GBXOIL | GBXOILADD | BETHEL | HFLORESGONZALEZ |  | 2020-09-30 13:49
2 | WTG-0037-NDG0-0000 | 2236302 | GEARBOX OIL, Add/Top-Off | 2020-06-15 16:00 | Closed | GBXOIL | GBXOILADD | VANTAGE | VANTAGE |  | 2020-06-17 17:20
1 | WTG-0318-0000 | 2239645 | GEARBOX OIL, Fix oil leak | 2020-06-29 15:58 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2020-08-25 11:17
5 | WTG-0085-0000 | 2248942 | GEARBOX OIL, Add/Top-Off about 5 Gallons | 2020-07-23 14:07 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-11-04 07:00
1 | WTG-0310-NDG0-0000 | 2254336 | GEARBOX OIL, Fix oil leak | 2020-08-03 17:25 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | JFERRIS |  | 2020-11-13 15:21
1 | WTG-0236-0000 | 2283440 | GEARBOX OIL, Fix oil leak | 2020-09-09 10:20 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | DGORDON |  | 2020-10-13 13:39
1 | WTG-0096-NDGP-0000 | 2284035 | GEARBOX OIL, Replace oil cooler motor | 2020-09-10 13:40 | Cancelled | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-05-05 12:20
4 | WTG-0047-NDGP-0000 | 2284039 | Oil filter housing needs new drain valve | 2020-09-10 13:58 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2022-02-11 07:08
2 | WTG-0203-0000 | 2285360 | GEARBOX OIL, Fix oil leak - Cooler Outlet Hose | 2020-09-17 16:32 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NHEITHOFF |  | 2020-10-06 16:28
5 | WTG-0053-0000 | 2285952 | Secondary filtration assembly is leaking | 2020-09-22 10:06 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2022-07-22 07:58
1 | WTG-0036-0000 | 2285787 | GEARBOX OIL, Fix oil leak | 2020-09-21 12:27 | Closed | GBXOIL | GBXOILLEAK | BETHEL | HFLORESGONZALEZ |  | 2020-09-23 11:08
1 | WTG-0004-0000 | 2291212 | GEARBOX OIL, Fix oil leak | 2020-10-03 20:22 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | TURKEY TRACK |  | 2020-10-09 12:49
4 | WTG-0031-0000 | 2291813 | Replace O-Ring on GBX filter pot | 2020-10-05 14:07 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2020-12-14 11:52
2 | WTG-0045-NDGP-0000 | 2293014 | GEARBOX OIL, Replace oil cooler | 2020-10-08 14:01 | Ready to Schedule | GBXOIL | GBXOILCOOL | FORWARD | FORWARD
2 | WTG-0023-0000 | 2292957 | Replace oil Hose | 2020-10-08 08:01 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | BDIAZ |  | 2023-07-13 09:48
5 | WTG-0073-0000 | 2302392 | CAM0073TADS GEN BRGS | 2020-10-22 18:26 | Closed | CMS | CMSGENB | CAMP SPRINGS I | ZKIMPEL |  | 2023-04-10 08:59
1 | WTG-0007-0000 | 2312189 | GEARBOX, Replace bypass hose (leaking) | 2020-11-13 08:35 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | GRAND RIDGE |  | 2021-01-19 14:42
4.2 | WTG-0076-NDGP-0000 | 2317074 | GEARBOX OIL, Replace oil cooler | 2020-11-23 09:04 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2020-11-25 07:32
4.2 | WTG-0066-NDGP-0000 | 2317073 | GEARBOX OIL, Replace oil cooler | 2020-11-23 09:03 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2020-11-24 06:41
1 | WTG-0034-0000 | 2322876 | GEARBOX OIL, Fix oil leak | 2020-12-04 16:42 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | STAYLOR |  | 2023-07-28 14:02
4 | WTG-0029A-0000 | 2323523 | GEARBOX OIL, Add/Top-Off about 5 Gallons | 2020-12-07 15:53 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-05-25 09:44
2 | GBX-000059 | 2324110 | Gearbox oil overtemp | 2020-12-10 07:18 | Closed | GBXOIL | EM77 | ORANGEVILLE | BMEST |  | 2020-12-11 13:38
1 | GBX-000021 | 2324111 | Gearbox oil overtemp | 2020-12-10 14:27 | Closed | GBXOIL | EM77 | ORANGEVILLE | BMEST |  | 2020-12-11 13:36
4 | WTG-0039-0000 | 2327920 | GEARBOX OIL, Add 5 gallons | 2020-12-17 17:25 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-06-02 10:58
1 | WTG-0016-NDG0-0000 | 2343242 | GEARBOX OIL, Fix oil leak | 2021-01-27 14:55 | Closed | GBXOIL | GBXOILLEAK | MCADOO | MCADOO |  | 2021-01-27 15:12
4 | WTG-0025-0000 | 2372054 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
2 | WTG-0220-0000 | 2285972 | GEARBOX OIL, Fix oil leak - Hoses | 2020-09-22 14:07 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | RKUDERA |  | 2021-01-05 13:27
4 | WTG-0074A-NDGP-0000 | 2302434 | GEARBOX OIL, Catch tray needed | 2020-10-23 07:15 | Closed | GBXOIL | GBXFILTELEM | FORWARD | GOTKIN |  | 2021-07-02 07:03
1 | WTG-0068-0000 | 2336938 | PALL Filter Housing Leak | 2021-01-08 15:15 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2021-02-05 14:14
4 | WTG-0071A-0000 | 2348426 | Check oil catch bucket | 2021-02-01 13:58 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2023-01-30 10:54
4 | WTG-0018-0000 | 2372047 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0019-0000 | 2372048 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0020-0000 | 2372049 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0021-0000 | 2372050 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0022-0000 | 2372051 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0023-0000 | 2372052 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0024-0000 | 2372053 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0026-0000 | 2372055 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0027-0000 | 2372056 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0031-0000 | 2372060 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0028-0000 | 2372057 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0029-0000 | 2372058 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0030-0000 | 2372059 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0032-0000 | 2372061 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0033-0000 | 2372062 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0034-0000 | 2372063 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0035-0000 | 2372064 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0036-0000 | 2372065 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0037-0000 | 2372066 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0041-0000 | 2372070 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0038-0000 | 2372067 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0039-0000 | 2372068 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0040-0000 | 2372069 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0042-0000 | 2372071 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0043-0000 | 2372072 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0044-0000 | 2372073 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0045-0000 | 2372074 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0046-0000 | 2372075 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0047-0000 | 2372076 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0098-0000 | 2372127 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0048-0000 | 2372077 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0049-0000 | 2372078 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0050-0000 | 2372079 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0099-0000 | 2372128 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0100-0000 | 2372129 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0101-0000 | 2372130 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0102-0000 | 2372131 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0103-0000 | 2372132 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0107-0000 | 2372136 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0104-0000 | 2372133 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0105-0000 | 2372134 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0106-0000 | 2372135 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0108-0000 | 2372137 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0109-0000 | 2372138 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0110-0000 | 2372139 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0111-0000 | 2372140 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0112-0000 | 2372141 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0113-0000 | 2372142 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0114-0000 | 2372143 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0118-0000 | 2372147 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0115-0000 | 2372144 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0116-0000 | 2372145 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0117-0000 | 2372146 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0119-0000 | 2372148 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0120-0000 | 2372149 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0004-0000 | 2372033 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0001-0000 | 2372030 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0002-0000 | 2372031 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0003-0000 | 2372032 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0005-0000 | 2372034 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0006-0000 | 2372035 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0007-0000 | 2372036 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0062-0000 | 2372091 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0008-0000 | 2372037 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0009-0000 | 2372038 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0010-0000 | 2372039 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0063-0000 | 2372092 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0064-0000 | 2372093 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0065-0000 | 2372094 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0069-0000 | 2372098 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0066-0000 | 2372095 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0067-0000 | 2372096 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0068-0000 | 2372097 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0070-0000 | 2372099 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0071-0000 | 2372100 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0072-0000 | 2372101 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0073-0000 | 2372102 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0074-0000 | 2372103 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0075-0000 | 2372104 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0079-0000 | 2372108 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0076-0000 | 2372105 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0077-0000 | 2372106 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0078-0000 | 2372107 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0080-0000 | 2372109 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0081-0000 | 2372110 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0082-0000 | 2372111 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0083-0000 | 2372112 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0084-0000 | 2372113 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0085-0000 | 2372114 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
1 | WTG-0090-0000 | 2374238 | GEARBOX OIL, Add/Top-Off | 2021-02-17 09:41 | Closed | GBXOIL | GBXOILADD | WAKE 1 | CMORALES |  | 2021-03-19 10:50
4 | WTG-0086-0000 | 2372115 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0087-0000 | 2372116 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0088-0000 | 2372117 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
1 | WTG-0003-0000 | 2374234 | GEARBOX OIL, Add/Top-Off | 2021-02-17 09:35 | Closed | GBXOIL | GBXOILADD | WAKE 1 | CMORALES |  | 2021-02-17 10:29
1 | WTG-0038-0000 | 2374236 | GEARBOX OIL, Add/Top-Off | 2021-02-17 09:40 | Closed | GBXOIL | GBXOILADD | WAKE 1 | CMORALES |  | 2021-02-25 07:52
1 | WTG-0026-0000 | 2374235 | GEARBOX OIL, Add/Top-Off | 2021-02-17 09:39 | Closed | GBXOIL | GBXOILADD | WAKE 1 | CMORALES |  | 2021-02-17 10:27
1 | WTG-0101-0000 | 2376353 | GEARBOX OIL, Fix oil leak | 2021-02-25 09:25 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2021-07-16 09:27
1 | WTG-0306-0000 | 2381949 | Oil hose | 2021-03-08 16:11 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | CWERNER |  | 2021-05-13 15:30
4 | WTG-0082-0000 | 2381926 | 7 gallons oil needed | 2021-03-08 15:13 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2021-07-20 06:37
1 | WTG-0202-0000 | 2382748 | GEARBOX OIL, Fix oil leak | 2021-03-11 18:19 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | AHOFFMANN |  | 2021-08-30 14:17
2 | WTG-0042-NDG0-0000 | 2383361 | Add Amsoil | 2021-03-15 13:55 | Closed | GBXOIL | GBXOILADD | VANTAGE | VANTAGE |  | 2021-03-15 16:11
4 | WTG-0036-0000 | 2384154 | Winergy Yellow Oil Hose Replacement Needed | 2021-03-19 07:57 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2021-06-02 11:00
5 | WTG-0054-NDGP-0000 | 2392528 | GEARBOX OIL, Replace oil pump | 2021-03-26 09:35 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | PMASAKI |  | 2023-07-17 13:33
5 | WTG-0062-NDGP-0000 | 2395550 | Gearbox, replace gear oil pumps spider gear | 2021-04-01 07:26 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2021-06-18 07:52
1 | WTG-0039-0000 | 2400127 | GEARBOX OIL, Fix oil leak | 2021-04-09 08:26 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | PMAGER |  | 2022-09-19 13:31
1 | WTG-0003-0000 | 2400128 | GEARBOX OIL, Fix oil leak | 2021-04-09 08:31 | Cancelled | GBXOIL | GBXOILLEAK | GORDON BUTTE | PMAGER |  | 2022-08-19 07:47
1 | WTG-0042-0000 | 2400936 | GEARBOX OIL, Fix oil leak | 2021-04-14 08:23 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | PMAGER |  | 2023-09-28 09:04
9 | WTG-0008-NDG0-0000 | 2402252 | GEARBOX, Oil Change | 2021-04-21 10:22 | Closed | GBXOIL | GBXOILCHG | BLOOMING GROVE | DGEORGE |  | 2021-04-28 10:38
1 | WTG-0305-0000 | 2402076 | GEARBOX OIL, Fix oil leak | 2021-04-20 08:46 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | JSTAHLECKER |  | 2021-08-30 14:14
4 | WTG-0082-NDGP-0000 | 2467359 | Secondary filter plastic insert replacement | 2021-07-16 10:11 | Closed | GBXOIL | GBXFILTELEM | FORWARD | JJENSEMA |  | 2022-07-05 08:22
4 | WTG-0082-0000 | 2467360 | Purple hose replacement | 2021-07-16 10:30 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2022-07-05 08:23
1 | WTG-0328-NDG0-0000 | 2467700 | GEARBOX OIL, Particle counter installation - WTG 328 - Install | 2021-07-19 22:20 | Closed | GBXOIL | GBXPARTINS | BISHOP HILL III | MCOURTNEY |  | 2021-09-07 15:11
1 | WTG-0021-NDG0-0000 | 2417903 | GEARBOX OIL, Fix oil leak | 2021-05-11 15:41 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | CWRIGHT |  | 2021-07-15 14:38
2 | WTG-0097-0000 | 2421888 | GEARBOX OIL, Fix oil leak | 2021-05-19 15:25 | Closed | GBXOIL | GBXOILLEAK | BETHEL | EAVILA |  | 2022-05-16 14:36
5 | WTG-0036-NDG0-0000 | 2424621 | GEARBOX OIL, Add/Top-Off 5gals | 2021-05-26 14:11 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2022-04-08 09:20
1 | WTG-0030-0000 | 2467770 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2021-07-20 09:25 | Closed | GBXOIL | GBXOILCOOL | ORANGEVILLE | ECOPELAND |  | 2021-10-18 11:53
1 | WTG-0022-0000 | 2440794 | Gearbox Oil Pressure | 2021-06-22 14:42 | Closed | GBXOIL | GBXOILCOOL | GREXP | FANAYA |  | 2021-07-13 15:53
5 | WTG-0075B-NDG0-0000 | 2442763 | About 7 gallons oil needed | 2021-06-28 15:07 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2021-07-20 06:44
4 | WTG-0071A-0000 | 2464166 | GEARBOX OIL, Add about 5 gallons | 2021-07-08 13:20 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-12-20 09:24
2 | WTG-0024-0000 | 2476112 | GEARBOX, Gearbox borescope Inspection | 2021-08-09 14:18 | Closed | CMS | GBXBORE | SANTA RITA EAST | CBILLIG |  | 2021-08-17 15:26
1 | WTG-0033-0000 | 2571244 | GEARBOX OIL, Fix oil leak | 2021-08-31 15:44 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2023-03-07 16:19
4 | WTG-0053-0000 | 2573683 | Replace gearbox oil pump seals and coupling | 2021-09-02 15:05 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2021-09-13 12:05
4 | WTG-0028-NDG0-0000 | 2577840 | GEARBOX OIL, Add 3-5 gallons | 2021-09-13 14:27 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-03-18 06:54
2 | WTG-0084-0000 | 2614364 | Administration | 2021-10-06 16:18 | Cancelled | GBXOIL | GBXFILTELEM | DEUEL HARVEST | CKRAUS |  | 2022-09-27 10:20
2 | WTG-0038-0000 | 2614348 | Gearbox Borescope Inspection & Report | 2021-10-06 15:36 | Closed | CMS | CMSGBXBORE | SUNDANCE | CBILLIG |  | 2022-02-16 13:32
4 | WTG-0013-0000 | 2616426 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2021-10-13 16:14 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-04-26 09:00
1 | WTG-0023-0000 | 2616330 | GEARBOX OIL, Oil Sample | 2021-10-13 10:29 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | DKEETON |  | 2021-10-13 16:46
1 | WTG-0026-0000 | 2616331 | GEARBOX OIL, Oil Sample | 2021-10-13 10:32 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | DKEETON |  | 2021-10-13 16:45
5 | WTG-0011-NDG0-0000 | 2617662 | GEARBOX OIL, Add 5 gals of gear oil | 2021-10-19 07:00 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2021-10-26 06:46
2 | WTG-0075-NDGP-0000 | 2624048 | Gearbox Oil Work/Issue | 2021-10-26 15:57 | Cancelled | GBXOIL | OILCOOLERFILTER | DEUEL HARVEST | DROGGENBUCK |  | 2023-02-21 10:42
5 | BRG-000090 | 2631348 | CMS Main Bearing Check | 2021-11-02 11:49 | Closed | CMS | CMSMB | SANTA RITA EAST | CBILLIG |  | 2022-02-08 08:49
5 | WTG-0034-0000 | 2632794 | GEARBOX OIL, Secondary filter leak | 2021-11-04 15:59 | Closed | GBXOIL | GBXFILTINS | FORWARD | DMONROE |  | 2022-02-01 14:06
2 | WTG-0027-NDG0-0000 | 2645360 | CMS Gearbox Borescope | 2021-11-15 15:12 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | MWILSON |  | 2021-11-17 13:14
2 | WTG-0D10-0000 | 2651731 | CMS HSS Check | 2021-11-30 10:35 | Closed | CMS | CMSHSS | COYOTE RIDGE | CBILLIG |  | 2022-01-03 08:45
1 | WTG-0092-0000 | 2653909 | GEARBOX OIL Cooler, Fix oil leak | 2021-12-01 12:26 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MLEGLEITER |  | 2022-12-19 08:51
5 | WTG-2011-0000 | 2930145 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-05-11 11:27 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-01-20 07:41
1 | WTG-0037-0000 | 2668149 | Gearbox hose replacement | 2021-12-13 12:01 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2021-12-30 07:46
4 | WTG-0058-0000 | 2668934 | GEARBOX OIL, Add/Top-Off about 3 gallons | 2021-12-14 14:46 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-06-24 07:09
1 | WTG-0093-0000 | 2374239 | GEARBOX OIL, Add/Top-Off | 2021-02-17 09:41 | Closed | GBXOIL | GBXOILADD | WAKE 1 | CMORALES |  | 2021-03-19 10:11
1 | WTG-0102-0000 | 2374241 | GEARBOX OIL, Add/Top-Off | 2021-02-17 09:42 | Closed | GBXOIL | GBXOILADD | WAKE 1 | CMORALES |  | 2021-02-25 07:53
2 | WTG-0017-NDG0-0000 | 2376710 | Add Amsoil | 2021-02-26 09:47 | Closed | GBXOIL | GBXOILADD | VANTAGE | VANTAGE |  | 2021-04-02 10:29
1 | GBX-000063 | 2381921 | EM: Gearbox oil pessure too low | 2021-03-08 15:09 | Closed | GBXOIL | BLANK | GOLDTHWAITE | OLAM |  | 2021-03-23 14:43
2 | GBX-000006 | 2381952 | gear box oil level low | 2021-03-08 16:40 | Closed | GBXOIL | GBXOILADD | GUNSIGHT | JWAELLIS |  | 2021-03-08 18:53
1 | WTG-0017-0000 | 2384632 | Gearbox Leak and clean up | 2021-03-23 11:52 | Closed | GBXOIL | GBXOILLEAK | GUNSIGHT | DKEETON |  | 2021-05-23 18:02
2 | WTG-0215-0000 | 2384831 | GEARBOX OIL, Add/Top-Off | 2021-03-24 08:34 | Closed | GBXOIL | GBXOILADD | PRAIRIE BREEZE2 | RKUDERA |  | 2021-08-30 14:17
1 | WTG-0004-NDGP-0000 | 2385222 | GEARBOX OIL, Particle counter installation | 2021-03-24 15:57 | Closed | GBXOIL | GBXPARTINS | STANTON | RPPATEL |  | 2021-04-16 07:27
1 | WTG-0022-NDGP-0000 | 2385223 | GEARBOX OIL, Particle counter installation | 2021-03-24 15:59 | Closed | GBXOIL | GBXPARTINS | STANTON | RPPATEL |  | 2021-05-03 16:18
1 | WTG-0005-0000 | 2400631 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2021-04-12 15:31 | Closed | GBXOIL | GBXOILCOOL | SANTA RITA EAST | ABARRON |  | 2021-04-13 08:20
1 | WTG-0308-0000 | 2402077 | GEARBOX OIL, Fix oil leak | 2021-04-20 08:50 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | JSTAHLECKER |  | 2021-08-30 14:14
9 | WTG-0033-NDG0-0000 | 2402297 | GEARBOX, Oil Change | 2021-04-21 13:33 | Closed | GBXOIL | GBXOILCHG | BLOOMING GROVE | DGEORGE |  | 2021-04-30 10:23
9 | WTG-0036-NDG0-0000 | 2402298 | GEARBOX, Oil Change | 2021-04-21 13:35 | Closed | GBXOIL | GBXOILCHG | BLOOMING GROVE | DGEORGE |  | 2021-04-30 10:22
9 | WTG-0007-NDG0-0000 | 2402299 | GEARBOX, Oil Change | 2021-04-21 13:40 | Closed | GBXOIL | GBXOILCHG | BLOOMING GROVE | DGEORGE |  | 2021-04-28 10:34
4 | WTG-0007-0000 | 2468264 | Secondary Oil Filtration Leak | 2021-07-22 13:08 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JJENSEMA |  | 2022-06-10 08:48
1 | WTG-0078-NDGP-0000 | 2437371 | Gearbox oil pressure too low | 2021-06-12 14:18 | Closed | GBXOIL | GBXOILCOOL | GREXP | GBLATNIK |  | 2021-06-27 09:08
5 | WTG-0010-0000 | 2439108 | GEARBOX OIL, Fix oil leak | 2021-06-18 15:51 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2021-06-22 07:04
1 | WTG-0036-NDGP-0000 | 2439052 | Replace Oil Filter Breather Hose | 2021-06-18 14:02 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | GBUNCH |  | 2022-08-05 14:50
1 | SITE-DEUEL | 2441329 | Site gearbox oil samples | 2021-06-24 09:42 | Closed | GBXOIL | GBXOILSAMP | DEUEL HARVEST | CNIEMANN |  | 2021-10-15 12:57
1 | WTG-0101-0000 | 2442020 | Fix oil leak | 2021-06-26 05:39 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SBAY |  | 2021-07-29 12:01
1 | WTG-039E-NDG0-0000 | 2470628 | GEARBOX OIL, Adjustment and oil level check | 2021-07-29 15:14 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | JROULIER |  | 2021-08-26 08:33
5 | WTG-0096-0000 | 2470830 | GEARBOX OIL, Fix oil leak | 2021-07-30 08:34 | Closed | GBXOIL | GBXOILLEAK | BETHEL | EAVILA |  | 2021-09-29 08:43
1 | WTG-0101-0000 | 2471503 | GEARBOX OIL, Secondary filter system installation | 2021-07-30 16:37 | Closed | GBXOIL | GBXFILTINS | CAMP SPRINGS II | JSULLIVAN |  | 2023-11-28 09:56
2 | WTG-0094-0000 | 2476111 | GEARBOX, Gearbox borescope Inspection | 2021-08-09 14:04 | Closed | CMS | GBXBORE | SANTA RITA EAST | CBILLIG |  | 2021-08-17 15:22
1 | WTG-0063A-NDG0-0000 | 2570703 | GEARBOX OIL, Fix oil leak from planetary oil supply | 2021-08-30 14:45 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2021-09-03 10:30
4 | WTG-0046-0000 | 2537511 | GEARBOX OIL, Add/Top-Off | 2021-08-25 09:56 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2021-09-03 10:16
4 | WTG-0046-0000 | 2537512 | GEARBOX OIL, Secondary filter system seal repair | 2021-08-25 10:05 | Closed | GBXOIL | GBXFILTELEM | FORWARD | KLEFFELMAN |  | 2021-09-03 10:16
4.2 | WTG-0095-NDG0-0000 | 2573681 | GEARBOX OIL, Oil Sample | 2021-09-02 15:10 | Closed | GBXOIL | GBXOILSAMP | FORWARD | ACASPER |  | 2021-09-03 10:21
5 | WTG-0213-0000 | 2576286 | GEARBOX OIL, Particle counter troubleshooting | 2021-09-07 16:26 | Cancelled | GBXOIL | GBXPARTTS | FORWARD | CBILLIG |  | 2021-09-08 13:09
1 | WTG-0028-0000 | 2576750 | GEARBOX OIL, Fix oil leak | 2021-09-09 09:51 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | FRAMIREZ |  | 2021-09-13 16:33
5 | WTG-0048-0000 | 2579309 | Replace Jensen Pump Seal | 2021-09-20 11:43 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JJENSEMA |  | 2022-04-08 09:23
1 | AWPL | 2611656 | 51 Alliant Oil Changes Fall of 2021 | 2021-10-04 20:52 | Closed | GBXOIL | BLANK | FSO | NZIRBEL |  | 2022-06-09 08:28
1 | WTG-0079-0000 | 2622060 | GEARBOX OIL, Fix oil leak | 2021-10-21 16:59 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | PMAGER |  | 2022-03-16 08:05
2 | BRG-000117 | 2631342 | CMS Main Bearing Borescope | 2021-11-02 11:07 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | CBILLIG |  | 2021-11-18 10:37
4 | WTG-0010-NDG0-0000 | 2632873 | GEARBOX Oil Leak, Secondary Filter Seal | 2021-11-05 07:04 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2021-11-24 07:13
5 | WTG-0220-0000 | 2644166 | GEARBOX OIL, clean belly/ gbx metal flakes | 2021-11-09 14:34 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | AHOFFMANN |  | 2022-06-28 12:24
5 | WTG-0210-0000 | 2649031 | GEARBOX OIL, Fix oil leak | 2021-11-22 14:45 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | RKUDERA |  | 2022-06-28 12:23
4 | WTG-0096-NDGP-0000 | 2650113 | Secondary filter switch not staying on | 2021-11-23 11:53 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2022-01-24 09:09
5 | WTG-0207-0000 | 2660586 | GEARBOX OIL, Fix oil leak | 2021-12-08 15:37 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | RKUDERA |  | 2022-10-28 16:22
4 | WTG-0057-0000 | 2669233 | GEARBOX OIL, Add/Top-Off about 3 gallons | 2021-12-15 14:23 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-12-27 10:56
2 | WTG-0217-NDB0-0000 | 2679474 | CMS Main Bearing Borescope | 2021-12-17 09:07 | Closed | CMS | CMSMBBORE | PRAIRIE BREEZE2 | CWERNER |  | 2022-01-10 20:24
1 | WTG-0041-NDGP-0000 | 2691198 | Secondary oil leak | 2022-01-03 16:36 | Closed | GBXOIL | BLANK | JUDITH GAP | JSTAGNER |  | 2022-08-10 08:15
5 | WTG-00B3-0000 | 2725805 | MAIN BEARING, Grease Purge | 2022-01-17 16:05 | Cancelled | CMS | MBPURGE | COYOTE RIDGE | CBILLIG |  | 2022-03-22 12:26
4 | WTG-0213-0000 | 2727688 | GEARBOX OIL, Add/Top-Off 5 gallons | 2022-01-19 16:15 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-01-24 09:43
4 | WTG-0058-0000 | 2741097 | GEARBOX secondary pump seal leaking | 2022-02-01 09:56 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2022-06-24 07:10
1 | WTG-0065-0000 | 2794513 | Replace main suction hose to pump (Moventas) | 2022-02-04 13:59 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU
1 | WTG-0307-0000 | 2794566 | Oil leak | 2022-02-04 16:37 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | DPRAUNER |  | 2023-01-06 10:44
2 | WTG-0028-0000 | 2795998 | CMS Main Bearing Borescope | 2022-02-07 15:06 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | CBILLIG |  | 2022-02-23 14:01
2 | WTG-00B3-NDB0-0000 | 2796300 | Main Bearing Inspection | 2022-02-07 16:50 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | JPETERSON |  | 2022-07-01 10:31
2 | WTG-0312-NDB0-0000 | 2809142 | CMS Main Bearing Borescope | 2022-02-28 14:36 | Cancelled | CMS | CMSMBBORE | BISHOP HILL III | CBILLIG |  | 2022-08-15 13:14
2 | WTG-0312-NDB0-0000 | 2809143 | MAIN BEARING, Grease Purge | 2022-02-28 14:40 | Cancelled | CMS | MBPURGE | BISHOP HILL III | CBILLIG |  | 2022-08-15 13:16
2 | WTG-0055A-0000 | 2813493 | GEARBOX OIL, Replace oil pump motor | 2022-03-08 07:40 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2022-03-18 07:07
1 | WTG-0019-0000 | 2815361 | GEARBOX OIL, Fix oil leak | 2022-03-14 16:17 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | PMAGER |  | 2022-08-17 14:54
2 | WTG-0344-0000 | 2874607 | CMS Gearbox Borescope | 2022-03-21 13:05 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | CBILLIG |  | 2022-05-05 15:06
2 | WTG-0024-0000 | 2882840 | GEARBOX OIL, Secondary filter system element change | 2022-03-21 16:27 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | PMAGER |  | 2022-08-31 08:11
4 | WTG-0049-0000 | 2889695 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2022-03-22 13:08 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-04-10 17:44
5 | WTG-2028-NDG0-0000 | 2904261 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-03-29 12:14 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-13 12:13
2 | GBX-00028 | 2907975 | CMS Gearbox Borescope - Gearbox EOW | 2022-04-04 16:10 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | CBILLIG |  | 2022-05-18 13:23
1 | WTG-0035-0000 | 2909445 | GEARBOX OIL, Fix oil leak | 2022-04-06 17:10 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | PMAGER |  | 2023-04-10 11:04
1 | WTG-2061-0000 | 2909451 | GEARBOX OIL, Fix oil leak | 2022-04-06 18:06 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | KDYER |  | 2022-07-11 11:52
4.2 | WTG-0082-0000 | 2909510 | GEARBOX OIL, Replace oil cooler | 2022-04-07 07:00 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCRESSWELL |  | 2022-07-20 06:46
5 | WTG-0029A-0000 | 2920435 | GEARBOX OIL, Replace primary GBX oil filter | 2022-04-14 12:28 | Closed | GBXOIL | GBXFILTINS | FORWARD | JLAWRENCE |  | 2022-06-24 07:16
1 | WTG-0082-0000 | 2920356 | GEARBOX OIL, Fix oil leak | 2022-04-14 11:55 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH |  | 2022-04-20 16:26
2 | WTG-0059A-NDGP-0000 | 2921579 | Replace oil cooler fan motor | 2022-04-20 10:56 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2022-12-09 09:41
2 | WTG-0003-NDGP-0000 | 2922310 | GEARBOX OIL, Add/Top-Off | 2022-04-22 12:46 | Closed | GBXOIL | GBXOILADD | MCADOO | ZHURT |  | 2022-04-25 09:49
5 | WTG-0017-0000 | 2923156 | Secondary filter leaking | 2022-04-25 13:03 | Closed | GBXOIL | GBXFILTELEM | FORWARD | DMONROE |  | 2022-10-07 15:00
1 | WTG-0015-NDG0-0000 | 2923528 | GEARBOX OIL, Fix oil leak | 2022-04-25 06:00 | Closed | GBXOIL | GBXOILLEAK | BLOOMING GROVE | DGEORGE |  | 2022-04-28 12:24
5 | WTG-0041A-0000 | 2927894 | Replace primary GBX Filter | 2022-05-04 13:37 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-07-05 08:44
2 | WTG-0037-NDG0-0000 | 2929420 | Add Amsoil, 10 gallons | 2022-05-09 16:40 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2022-06-30 14:24
5 | WTG-0003-0000 | 2931881 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-05-17 12:40 | Cancelled | CMS | CMSTRBLSHOOT | GORDON BUTTE | CBILLIG |  | 2022-06-08 14:58
1 | WTG-0086-0000 | 2931882 | CMS Generator Bearing Check | 2022-05-17 12:48 | Closed | CMS | CMSGENB | MAVERICK | CBILLIG |  | 2022-07-01 07:37
1 | WTG-0A07-0000 | 3220479 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2023-11-07 08:28 | Closed | GBXOIL | GBXOILCOOL | JAYHAWK | DRWEBB |  | 2024-02-13 11:41
4 | WTG-0002C-0000 | 2935912 | GEARBOX OIL, Fix oil leak at secondary filter | 2022-05-19 13:37 | Closed | GBXOIL | GBXOILLEAK | FORWARD | DMONROE |  | 2022-12-19 08:15
4.2 | WTG-0095-NDGP-0000 | 2935803 | GEARBOX OIL, Fix oil leak | 2022-05-19 08:17 | Closed | GBXOIL | GBXOILLEAK | GRATIOT | GBOTT |  | 2022-05-19 08:24
2 | GBX-00009 | 2935684 | CMS Gearbox Borescope | 2022-05-18 15:32 | Closed | CMS | CMSGBXBORE | UPSTREAM | DGORDON |  | 2022-06-28 12:13
5 | WTG-0070-0000 | 2937442 | GEARBOX OIL, Add 5 Gallons | 2022-05-23 15:37 | Closed | GBXOIL | GBXOILADD | FORWARD | TBUYESKE |  | 2022-06-10 09:24
1 | WTG-0040-0000 | 2938314 | Oil Pump Motor Inversion | 2022-05-25 17:08 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MCONDON |  | 2025-04-29 10:06
1 | WTG-0089-0000 | 2940906 | Oil clean up | 2022-05-31 07:33 | Closed | GBXOIL | GBXOILLEAK | DEUEL HARVEST | LCRUZ |  | 2022-07-27 11:58
5 | WTG-0010-0000 | 2941642 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-03 15:07 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2022-09-01 12:00
5 | GBX-00097 | 2941634 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-03 15:00 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-09-07 13:06
5 | WTG-0001-0000 | 2941638 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-03 15:02 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2022-09-01 12:00
5 | WTG-0096-0000 | 2941639 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-03 15:04 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 11:00
1 | WTG-0032-0000 | 2941779 | Replace oil pump coupling | 2022-06-04 06:40 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | MCARBAJAL |  | 2022-06-22 16:18
1 | WTG-0023-0000 | 2943685 | GEARBOX OIL, Fix oil leak | 2022-06-09 15:52 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | APEREZ |  | 2022-06-16 09:01
1 | WTG-1085-0000 | 2943656 | Missing spider line | 2022-06-09 10:51 | Closed | GBXOIL | GBXOILSAMP | TRAVERSE | ATHOMPSON |  | 2022-10-24 14:22
5 | WTG-0055-0000 | 2950291 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Completed Awaiting Review | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG
5 | WTG-0238-0000 | 2684360 | GEARBOX OIL, Fix oil leak | 2021-12-22 11:05 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | RKUDERA |  | 2022-10-28 16:22
5 | WTG-0116-NDB0-0000 | 2684964 | CMS Main Bearing Check | 2021-12-27 14:25 | Closed | CMS | CMSMB | CAMP SPRINGS II | JSULLIVAN |  | 2021-12-28 07:56
2 | WTG-0008-NDB0-0000 | 2804887 | CMS Main Bearing Borescope | 2022-02-23 10:05 | Cancelled | CMS | CMSMBBORE | DEUEL HARVEST | CBILLIG |  | 2022-08-10 11:08
5 | WTG-00B8-0000 | 2725808 | MAIN BEARING, Grease Purge | 2022-01-17 16:09 | Cancelled | CMS | MBPURGE | COYOTE RIDGE | CBILLIG |  | 2022-08-15 15:38
4 | WTG-0203B-0000 | 2736721 | Replace gear oil pump red spider insert | 2022-01-24 16:11 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-01-25 16:51
4 | WTG-0204A-0000 | 2738815 | GEARBOX OIL, Replace Spider Gear | 2022-01-27 15:42 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2022-02-01 13:33
5 | WTG-0018-0000 | 2800007 | Generator Bearing Inspection | 2022-02-08 14:54 | Closed | CMS | CMSGENB | SUNDANCE | TKORNELE |  | 2022-03-08 10:15
9 | SITE-WHISP | 2807735 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
9 | WTG-0425-0000 | 2807737 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
9 | WTG-0426-0000 | 2807738 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
9 | WTG-0427-0000 | 2807739 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
9 | WTG-0440-0000 | 2807740 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
9 | WTG-0470-0000 | 2807741 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
9 | WTG-0481-0000 | 2807742 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
9 | WTG-0456-0000 | 2807743 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
9 | WTG-0449-0000 | 2807744 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
9 | WTG-0431-0000 | 2807745 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
9 | WTG-0446-0000 | 2807747 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
9 | WTG-0421-0000 | 2807748 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
1 | WTG-0078-0000 | 2812308 | GEARBOX OIL, Oil Sample | 2022-03-04 12:19 | Cancelled | GBXOIL | GBXOILSAMP | MAVERICK | JROULIER |  | 2022-07-11 15:38
9 | WTG-0409-0000 | 2812896 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
9 | WTG-0415-0000 | 2812897 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:10 | Closed | GBXOIL |  | WHISPERING WILL | KBJORKLUND |  | 2024-06-14 09:51
2 | WTG-0050-0000 | 2814475 | CMS Gearbox Borescope | 2022-03-10 07:00 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | CGREIS |  | 2022-03-10 14:16
1 | WTG-0034-NTV0-0000 | 2814588 | EM: Vibrations detector defect | 2022-03-10 16:37 | Closed | CMS | EM41 | SUNDANCE | TKORNELE |  | 2022-04-21 09:55
2 | WTG-0053-NDG0-0000 | 2814352 | Add Amsoil | 2022-03-10 09:56 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2022-03-28 10:28
1 | WTG-0033-0000 | 2908154 | GEARBOX OIL, Fix oil leak | 2022-04-05 08:56 | Cancelled | GBXOIL | GBXOILLEAK | JUDITH GAP | PMAGER |  | 2023-04-06 16:31
1 | WTG-0F10-ND00-0000 | 2908740 | GEARBOX OIL, Particle counter installation | 2022-04-05 15:34 | Closed | GBXOIL | GBXPARTINS | JAYHAWK | CBILLIG |  | 2022-04-18 08:06
1 | BRG-000085 | 2910100 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-04-07 11:30 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | CBILLIG |  | 2022-04-20 13:33
4 | WTG-0025-0000 | 2910531 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2022-04-07 11:41 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-10-10 15:24
4 | WTG-0025-0000 | 2910532 | GEARBOX OIL, Replace Orange Hose | 2022-04-07 11:42 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2023-03-27 10:23
2 | WTG-0217-0000 | 2911345 | GEARBOX OIL, Add/Top-Off | 2022-04-08 14:18 | Closed | GBXOIL | GBXOILADD | BEECH RIDGE II | KHASS |  | 2022-07-18 10:25
2 | WTG-0086-0000 | 2920340 | GEARBOX OIL, Add/Top-Off | 2022-04-14 15:30 | Closed | GBXOIL | GBXOILADD | BUCKEYE | MLEGLEITER |  | 2022-07-20 15:18
5 | WTG-0022-0000 | 2921113 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-04-18 15:44 | Cancelled | CMS | CMSTRBLSHOOT | MAVERICK | CBILLIG |  | 2022-08-23 10:21
5 | WTG-0206-0000 | 2936159 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-05-20 10:02 | Closed | CMS | CMSTRBLSHOOT | BEECH RIDGE II | CBILLIG |  | 2022-07-05 12:42
1 | WTG-0066-NDGP-0000 | 2938342 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2022-05-25 17:42 | Closed | GBXOIL | GBXOILCOOL | SUNDANCE | TKORNELE |  | 2022-06-01 16:08
1 | WTG-2049-0000 | 2940207 | GEARBOX OIL, Fix oil leak | 2022-06-01 09:01 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | LWRIGHT |  | 2022-10-24 14:12
2 | GBX-00045 | 2945173 | GEARBOX OIL, Particle counter installation | 2022-06-14 10:56 | Closed | GBXOIL | GBXPARTINS | SANTA RITA EAST | CBILLIG |  | 2022-07-07 08:59
2 | GBX-00118 | 2945175 | GEARBOX OIL, Particle counter installation | 2022-06-14 10:58 | Closed | GBXOIL | GBXPARTINS | SANTA RITA EAST | CBILLIG |  | 2022-06-24 08:32
5 | WTG-0049-0000 | 2947234 | GEARBOX OIL, Fix oil leak | 2022-06-17 09:57 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2023-11-10 14:18
1 | GEN-000074 | 2948135 | GEARBOX OIL, Fix oil leak | 2022-06-21 14:50 | Cancelled | GBXOIL | GBXOILLEAK | GRAND RIDGE | JCARRETTO |  | 2023-06-29 13:27
5 | WTG-0043-0000 | 2950280 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-09-06 11:49
5 | WTG-0044-0000 | 2950281 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-12-07 10:20
5 | WTG-0045-0000 | 2950282 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-09-06 11:49
5 | WTG-0048-0000 | 2950283 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-08-28 14:43
5 | WTG-0049-0000 | 2950284 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-25 10:42
5 | WTG-0005-0000 | 2950285 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-12-07 10:19
5 | WTG-0050-0000 | 2950286 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-01-12 10:04
5 | WTG-0051-0000 | 2950287 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-08-15 06:46
5 | WTG-0052-0000 | 2950288 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Cancelled | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-09-19 10:24
5 | WTG-0053-0000 | 2950289 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-04-07 09:25
5 | WTG-0054-0000 | 2950290 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-08-15 11:46
5 | WTG-0057-0000 | 2950292 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-04 15:36
5 | WTG-0006-0000 | 2950293 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-07 09:28
5 | WTG-0060-0000 | 2950294 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-04-07 09:24
5 | WTG-0061-0000 | 2950295 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG
5 | WTG-0062-0000 | 2950296 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG
5 | WTG-0068-0000 | 2950300 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Cancelled | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-07 09:14
5 | WTG-0063-0000 | 2950297 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-04-07 09:24
5 | WTG-0066-0000 | 2950298 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-27 13:43
5 | WTG-0067-0000 | 2950299 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-11-16 08:05
5 | WTG-0069-0000 | 2950301 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-22 14:22
5 | WTG-0007-0000 | 2950302 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-07 14:16
5 | WTG-0070-0000 | 2950303 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Cancelled | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-11-29 09:15
5 | WTG-0071-0000 | 2950304 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2024-07-26 09:46
5 | WTG-0073-0000 | 2950305 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-25 10:42
5 | WTG-0074-0000 | 2950306 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-08-22 12:10
5 | WTG-0075-0000 | 2950307 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-25 10:42
5 | WTG-0080-0000 | 2950311 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-08-15 06:44
5 | WTG-0078-0000 | 2950308 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2024-01-11 10:55
5 | WTG-0079-0000 | 2950309 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-25 10:42
5 | WTG-0008-0000 | 2950310 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-18 09:28
5 | WTG-0081-0000 | 2950312 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2024-01-30 11:39
5 | WTG-0083-0000 | 2950313 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-09-06 11:48
5 | WTG-0084-0000 | 2950314 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-08-15 06:37
5 | WTG-0085-0000 | 2950315 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-07-12 10:47
5 | WTG-0086-0000 | 2950316 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-08-24 14:28
5 | WTG-0087-0000 | 2950317 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | In Progress | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG
5 | WTG-0088-0000 | 2950318 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2024-07-16 12:26
5 | WTG-0096-0000 | 2950322 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-04-07 09:24
5 | WTG-0009-0000 | 2950319 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-18 09:27
5 | WTG-0090-0000 | 2950320 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-25 10:42
5 | WTG-0095-0000 | 2950321 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG
5 | GBX-00024 | 2951065 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-29 12:27 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | CBILLIG |  | 2022-08-26 10:50
4 | WTG-0082-0000 | 2951077 | GEARBOX OIL, Add/Top-Off 3-5 gallons | 2022-06-29 11:31 | Closed | GBXOIL | GBXOILADD | FORWARD | DMONROE |  | 2023-01-30 11:31
4 | WTG-0025-NDGP-0000 | 2951130 | Secondary Oil Pump Washer and Cone Replacement | 2022-06-29 15:59 | Cancelled | GBXOIL | GBXFILTINS | WOLVERINE CREEK | DLOWREY |  | 2023-09-25 14:40
2 | WTG-1005-NDB0-0000 | 2954530 | CMS Main Bearing Borescope | 2022-07-05 10:18 | Closed | CMS | CMSMBBORE | TRAVERSE | CBILLIG |  | 2022-10-24 14:42
5 | WTG-0350-NDG0-0000 | 2954599 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-07-05 14:51 | Closed | CMS | CMSTRBLSHOOT | BISHOP HILL III | CBILLIG |  | 2023-04-24 11:30
5 | WTG-0043-0000 | 2962404 | GEARBOX OIL, Fix oil leak at CCJen | 2022-07-20 12:22 | Closed | GBXOIL | GBXOILLEAK | FORWARD | DMONROE |  | 2022-10-31 15:16
1 | WTG-0003-0000 | 2968354 | Clean up oil spill | 2022-07-28 10:20 | Closed | GBXOIL | GBXOILLEAK | MAVERICK | MWEBER |  | 2022-12-15 11:17
4 | WTG-0034-0000 | 2973025 | GEARBOX OIL, Add/Top-Off | 2022-08-05 09:38 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-10-31 14:51
5 | WTG-1139-0000 | 2987692 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-01-20 13:02
2 | WTG-1038-0000 | 2987693 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-04-13 15:38
5 | WTG-1068-0000 | 2987694 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-04-14 16:05
5 | WTG-1019-0000 | 2987695 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-04-13 15:04
3 | WTG-1043-0000 | 2987696 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-04-13 15:48
5 | WTG-1048-0000 | 2987697 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-01-20 13:00
5 | WTG-1052-0000 | 2987698 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-01-20 13:00
5 | WTG-2033-NDG0-0000 | 2998455 | CMS HSS Check | 2022-08-24 12:45 | Closed | CMS | CMSHSS | TRAVERSE | CBILLIG |  | 2023-01-20 07:39
5 | WTG-0015-NDB0-0000 | 3011542 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-09-02 11:11 | Cancelled | CMS | CMSTRBLSHOOT | DEUEL HARVEST | CBILLIG |  | 2022-09-21 11:15
5 | WTG-0057-0000 | 3011632 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-07-12 10:09
5 | WTG-0054-0000 | 3011633 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | In Progress | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG
5 | WTG-0045-0000 | 3011634 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2024-04-25 11:57
5 | WTG-0037-0000 | 3011635 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2025-03-24 09:22
5 | WTG-0003-0000 | 3011642 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-25 10:37
1 | WTG-0015-0000 | 2951105 | Oil Pump Replacement & Motor Inversion | 2022-06-29 15:11 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MCONDON |  | 2022-06-29 16:24
5 | WTG-0027-NDD0-0000 | 2971011 | CMS Generator Bearing Check | 2022-08-02 10:36 | Closed | CMS | CMSGENB | SUNDANCE | CBILLIG |  | 2022-08-26 08:45
5 | GBX-00027 | 2984185 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:00 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-08-23 09:38
5 | WTG-1053-0000 | 2987699 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-01-20 13:01
5 | WTG-1065-0000 | 2987700 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-10 10:01
5 | WTG-1067-0000 | 2987701 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-01-20 13:01
5 | WTG-1133-0000 | 2987702 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG
5 | WTG-1134-0000 | 2987703 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-01-20 13:02
5 | WTG-1104-0000 | 2987691 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-08 15:44 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-01-20 13:02
1 | WTG-0015-0000 | 2988513 | GEARBOX OIL, Fix oil leak | 2022-08-11 07:34 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | NSPINK |  | 2022-08-11 11:33
2 | GBX-00009 | 3010437 | CMS Gearbox Borescope | 2022-08-31 16:47 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2022-10-11 14:07
5 | WTG-0033-0000 | 3011636 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-09-05 16:02
5 | WTG-0027-0000 | 3011637 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG
5 | WTG-0030-0000 | 3011638 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2024-04-18 13:54
5 | WTG-0025-0000 | 3011639 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Cancelled | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-07-11 10:07
5 | WTG-0001-0000 | 3011640 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-25 10:37
5 | WTG-0068-0000 | 3011641 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-25 10:37
5 | WTG-0014-0000 | 3011643 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-25 10:37
5 | WTG-0015-0000 | 3011644 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Cancelled | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-05-25 12:50
5 | WTG-0016-0000 | 3011645 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-25 10:37
5 | WTG-0026-0000 | 3011646 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG
5 | WTG-0052-0000 | 3011647 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-25 10:36
5 | WTG-0084-0000 | 3011648 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | In Progress | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG
4 | WTG-0041A-0000 | 3012464 | GEARBOX OIL, Add/Top-Off about 8-10 gallons | 2022-09-06 14:10 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-12-09 10:36
2 | 1GT2-BRG-202 | 3012399 | GT2 bearing vibration BB5 has been reading erratic. | 2022-09-06 12:20 | Closed | CMS |  | GRAYS HARBOR | PHUGHES |  | 2022-12-01 14:39
5 | WTG-0A08-0000 | 3016141 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-09-09 16:21 | Cancelled | CMS | CMSTRBLSHOOT | JAYHAWK | CBILLIG |  | 2023-01-17 15:51
4 | WTG-0001-0000 | 3122537 | Replace Orange GBX Hose | 2023-05-04 12:58 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2024-05-08 14:39
1 | WTG-0095-0000 | 3027737 | Secondary oil pump, Fix oil leak | 2022-09-29 15:55 | Cancelled | GBXOIL | GBXOILLEAK | JUDITH GAP | TWIEDEMEIER |  | 2023-01-03 15:31
1 | WTG-0100-0000 | 3029913 | GEARBOX OIL, Fix oil leak | 2022-10-04 12:00 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | SMILLER |  | 2022-10-07 15:07
2 | WTG-0015-NDB0-0000 | 3032633 | CMS Main Bearing Check | 2022-10-11 09:51 | Cancelled | CMS | CMSMB | MAVERICK | CBILLIG |  | 2023-02-21 15:35
1 | WTG-0043-0000 | 3033413 | GEARBOX OIL, Fix oil leak | 2022-10-12 10:09 | Closed | GBXOIL | GBXOILLEAK | STANTON | MROMAN |  | 2022-10-13 08:23
2 | WTG-0012-NDG0-0000 | 3033417 | GEARBOX OIL, Particle counter troubleshooting | 2022-10-12 10:23 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-07-18 14:33
2 | WTG-0045-NDG0-0000 | 3033424 | GEARBOX OIL, Particle counter troubleshooting | 2022-10-12 10:27 | Cancelled | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-01-27 14:00
2 | WTG-0011-0000 | 3037172 | GEARBOX OIL, Secondary filter system element change | 2022-10-21 12:32 | Closed | GBXOIL | GBXFILTELEM | BUCKEYE | BROHR |  | 2023-02-13 14:24
2 | WTG-0037-NDG0-0000 | 3037805 | GEARBOX OIL, Add/Top-Off | 2022-10-24 16:32 | Closed | GBXOIL | GBXOILADD | VANTAGE | CCUSACK |  | 2023-05-22 12:04
5 | WTG-2003-0000 | 3038404 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-10-26 12:26 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-13 12:25
9 | WTG-0027-0000 | 3038725 | GEARBOX, Oil Change | 2022-10-27 10:00 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | JGARLAND |  | 2022-11-21 13:04
5 | WTG-00B5-NDG0-0000 | 3014579 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-09-09 10:54 | Closed | CMS | CMSTRBLSHOOT | COYOTE RIDGE | CBILLIG |  | 2022-10-13 14:14
1 | WTG-0006-0000 | 3020623 | Gearbox Oil Work/Issue | 2022-09-19 15:19 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | JCORDELL |  | 2023-02-06 15:20
5 | GBX-00084 | 3024174 | CMS HSS Check | 2022-09-20 12:10 | Closed | CMS | CMSHSS | SANTA RITA EAST | CBILLIG |  | 2022-12-12 07:54
2 | 011D194 | 3026216 | Replace Pump Bearings | 2022-09-25 20:32 | Rejected | CMS |  | NELSON | LZIMMERMAN |  | 2024-05-22 13:47
5 | WTG-3018-0000 | 3027196 | CMS HSS Check | 2022-09-28 13:41 | Closed | CMS | CMSHSS | TRAVERSE | HBELTRAN |  | 2022-10-25 09:30
9 | WTG-0020-0000 | 3038721 | GEARBOX, Oil Change | 2022-10-27 09:58 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | JGARLAND |  | 2022-11-21 13:07
9 | WTG-0023-0000 | 3038722 | GEARBOX, Oil Change | 2022-10-27 09:58 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | JGARLAND |  | 2023-02-24 15:35
9 | WTG-0024-0000 | 3038723 | GEARBOX, Oil Change | 2022-10-27 09:59 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | JGARLAND |  | 2023-02-28 16:22
9 | WTG-0016-0000 | 3038717 | GEARBOX, Oil Change | 2022-10-27 09:46 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | RTROWBRIDGE |  | 2022-11-29 12:21
9 | WTG-0026-0000 | 3038724 | GEARBOX, Oil Change | 2022-10-27 09:59 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | JGARLAND |  | 2022-11-21 13:05
9 | WTG-0022-0000 | 3038726 | GEARBOX, Oil Change | 2022-10-27 10:00 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | JGARLAND |  | 2022-11-21 13:09
2 | WTG-0093-0000 | 3039940 | CMS Gearbox Borescope per GE CMS - Potential Planet Bearing Issue | 2022-10-31 14:20 | Closed | CMS | CMSINSP | MIAMI 1 | CMORRISON |  | 2023-06-13 09:27
2 | WTG-3053-NDG0-0000 | 3041390 | Main Bearing Inspection | 2022-11-03 07:26 | Cancelled | CMS | CMSMBBORE | TRAVERSE | JTBROWN |  | 2023-02-02 09:35
9 | WTG-0028-0000 | 3041963 | GEARBOX, Oil Change | 2022-11-04 10:59 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2022-11-22 10:35
2 | WTG-2007-NDB0-0000 | 3045565 | CMS Main Bearing Check | 2022-11-14 14:37 | Closed | CMS | CMSMB | TRAVERSE | WDEAS |  | 2023-01-30 14:44
5 | WTG-0069-NDG0-0000 | 3045554 | CMS HSS Check | 2022-11-14 14:29 | Closed | CMS | CMSHSS | SUNDANCE | CBILLIG |  | 2023-03-30 15:43
1 | SITE-VWEC | 3049121 | Oil Sample Bottle Misc, Consumption | 2022-11-22 10:13 | Closed | GBXOIL | GBXOILSAMP | VANTAGE | JVERA |  | 2022-12-08 09:42
9 | WTG-0063-0000 | 3049146 | GEARBOX, Oil Change | 2022-11-22 11:46 | Closed | GBXOIL | GBXOILCHG | BETHEL | AALEMAN |  | 2023-03-06 16:23
9 | WTG-0112-0000 | 3050486 | GEARBOX, Oil Change | 2022-11-28 09:10 | Closed | GBXOIL | GBXOILCHG | BETHEL | JGARLAND |  | 2023-06-05 16:40
5 | WTG-0009-0000 | 3050637 | Secondary Filter Oil Leak | 2022-11-28 13:12 | Closed | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE |  | 2023-02-10 13:23
9 | WTG-0108-0000 | 3050484 | GEARBOX, Oil Change | 2022-11-28 09:08 | Closed | GBXOIL | GBXOILCHG | BETHEL | TMILLER2 |  | 2023-01-27 12:59
2 | WTG-0003-NDG0-0000 | 3051120 | CMS Gearbox Borescope | 2022-11-29 12:23 | Closed | CMS | CMSGBXBORE | GORDON BUTTE | WDEAS |  | 2023-02-03 16:29
2 | WTG-0007-0000 | 3051165 | GEARBOX OIL, Oil Sample from secondary | 2022-11-29 14:38 | Cancelled | GBXOIL | GBXOILSAMP | FORWARD | TBUYESKE |  | 2022-12-19 09:45
9 | WTG-0117-0000 | 3051931 | GEARBOX, Oil Change | 2022-11-30 13:27 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-06-09 12:29
9 | WTG-0100-0000 | 3054080 | GEARBOX, Oil Change | 2022-12-06 12:02 | Closed | GBXOIL | GBXOILCHG | BETHEL | MHERRERA |  | 2023-05-25 15:53
9 | WTG-0074-0000 | 3054079 | GEARBOX, Oil Change | 2022-12-06 11:59 | Closed | GBXOIL | GBXOILCHG | BETHEL | AALEMAN |  | 2023-02-28 14:31
2 | WTG-0037-0000 | 3054799 | CMS Gearbox Borescope | 2022-12-08 07:56 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | ECOPELAND |  | 2022-12-08 13:21
9 | WTG-0106-0000 | 3054975 | GEARBOX, Oil Change | 2022-12-08 12:21 | Closed | GBXOIL | GBXOILCHG | BETHEL | MRAHMAN |  | 2023-05-31 15:26
5 | WTG-2117-0000 | 3054899 | CMS HSS Check | 2022-12-08 11:50 | Closed | CMS | CMSHSS | TRAVERSE | WDEAS |  | 2023-02-23 11:23
9 | WTG-0102-0000 | 3054977 | GEARBOX, Oil Change | 2022-12-08 12:54 | Closed | GBXOIL | GBXOILCHG | BETHEL | MHERRERA |  | 2022-12-16 07:38
9 | WTG-0101-0000 | 3054978 | GEARBOX, Oil Change | 2022-12-08 12:56 | Closed | GBXOIL | GBXOILCHG | BETHEL | MHERRERA |  | 2022-12-13 14:27
2 | GBX-00008 | 3056303 | GEARBOX OIL, Particle counter troubleshooting | 2022-12-13 09:48 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | CBILLIG |  | 2022-12-28 08:05
2 | GBX-00028 | 3056403 | GEARBOX OIL, Particle counter troubleshooting | 2022-12-13 14:04 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | CBILLIG |  | 2022-12-19 09:08
2 | GBX-00016 | 3056328 | GEARBOX OIL, Particle counter troubleshooting | 2022-12-13 10:56 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | CBILLIG |  | 2022-12-19 09:08
5 | WTG-0010-HPA2-T000 | 3057916 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-12-16 17:00 | Cancelled | CMS | CMSTRBLSHOOT | GUNSIGHT | JGRIFFIN |  | 2022-12-16 17:06
2 | WTG-0010-NDB0-0000 | 3059337 | CMS Main Bearing Borescope | 2022-12-21 14:09 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | FALCARAZ |  | 2023-01-16 13:22
9 | WTG-0037-0000 | 3060874 | GEARBOX, Oil Change | 2022-12-28 09:18 | Cancelled | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-01-10 11:51
9 | WTG-0046-0000 | 3060875 | GEARBOX, Oil Change | 2022-12-28 09:18 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-04-03 15:27
9 | WTG-0051-0000 | 3060877 | GEARBOX, Oil Change | 2022-12-28 09:19 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-04-08 08:16
9 | WTG-0037-0000 | 3065990 | GEARBOX, Oil Change | 2023-01-09 08:37 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-01-23 15:46
9 | WTG-0076-0000 | 3065991 | GEARBOX, Oil Change | 2023-01-09 08:38 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-05-03 16:02
9 | WTG-0078-0000 | 3065992 | GEARBOX, Oil Change | 2023-01-09 08:38 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-05-03 15:48
1 | WTG-0312-0000 | 3066282 | GEARBOX OIL, Fix oil leak/sweating hoses | 2023-01-09 17:50 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | AHOFFMANN |  | 2023-10-23 22:54
4 | WTG-0059A-0000 | 3066233 | Secondary Oil Leak | 2023-01-09 15:25 | Closed | GBXOIL | GBXFILTELEM | FORWARD | DMONROE |  | 2023-05-17 13:00
2 | WTG-0095-0000 | 3067976 | MB Inspection | 2023-01-12 14:24 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-01-20 08:57
5 | WTG-0108-NTV0-0000 | 3069383 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-18 11:58 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-01-20 08:55
1 | WTG-0002-0000 | 3070702 | GEARBOX OIL, Particle counter installation | 2023-01-20 15:19 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | GBUTTRY |  | 2023-02-09 14:45
1 | WTG-0024-0000 | 3070711 | GEARBOX OIL, Particle counter installation | 2023-01-20 15:19 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | BVANVALKENBURG |  | 2023-02-09 14:45
1 | GBX-00032 | 3070740 | CMS Gearbox Borescope MB/GBX | 2023-01-20 15:53 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2023-04-04 13:25
5 | WTG-0026-NTV0-0000 | 3071343 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-24 12:52 | Cancelled | CMS | CMSTRBLSHOOT | DEUEL HARVEST | ABARNDT |  | 2023-01-24 12:57
2 | WTG-0099-NDD0-0000 | 3072204 | CMS Generator Bearing Check | 2023-01-25 16:31 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-09-18 15:23
1 | WTG-0100-NDD0-0000 | 3072205 | CMS Generator Bearing Check | 2023-01-25 16:36 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-03-20 12:38
4 | WTG-0204A-0000 | 3072172 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2023-01-25 14:16 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-06-13 11:35
5 | WTG-0032-NTV0-0000 | 3072215 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-25 16:57 | Closed | CMS | CMSTRBLSHOOT | BETHEL | ABARNDT |  | 2023-02-03 09:01
2 | WTG-0116-NDD0-0000 | 3072207 | CMS Generator Bearing Check | 2023-01-25 16:42 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-04-12 17:07
1 | WTG-0039-NDG0-0000 | 3072189 | High Speed Stage Bearing Issue | 2023-01-25 15:54 | Closed | CMS | CMSGBXBORE | BETHEL | ABARNDT |  | 2023-03-21 15:37
1 | WTG-0054-NDD0-0000 | 3072192 | CMS Generator Bearing Check | 2023-01-25 16:07 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-01-27 12:56
5 | WTG-0009-NTV0-0000 | 3072180 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-25 15:32 | Closed | CMS | CMSTRBLSHOOT | BETHEL | ABARNDT |  | 2023-06-21 16:11
2 | WTG-0016-NDD0-0000 | 3072183 | CMS Generator Bearing Check | 2023-01-25 15:39 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-07-03 11:17
1 | WTG-0048-NDD0-0000 | 3072190 | CMS Generator Bearing Check | 2023-01-25 15:57 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-01-27 12:57
2 | WTG-0046-NTV0-0000 | 3072191 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-25 15:59 | Closed | CMS | CMSTRBLSHOOT | BETHEL | ABARNDT |  | 2023-12-14 07:53
5 | WTG-0048-NTV0-0000 | 3073702 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-30 09:24 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-02-15 12:52
1 | WTG-0012-0000 | 3039345 | Low Oil Level | 2022-10-29 06:03 | Closed | GBXOIL |  | BUFFALO MOUNT | TLONG |  | 2022-12-30 14:39
1 | WTG-2131-0000 | 3039933 | CMS Gearbox Borescope | 2022-10-31 14:02 | Closed | CMS | CMSGBXBORE | TRAVERSE | HBELTRAN |  | 2023-02-21 16:13
2 | WTG-0064-NDGP-0000 | 3042068 | GEARBOX OIL, Particle counter troubleshooting | 2022-11-04 14:42 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | CBILLIG |  | 2022-11-11 09:00
9 | WTG-0043-0000 | 3041958 | GEARBOX, Oil Change | 2022-11-04 10:56 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2022-11-29 12:17
9 | WTG-0042-0000 | 3041960 | GEARBOX, Oil Change | 2022-11-04 10:58 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2023-03-23 09:26
9 | WTG-0048-0000 | 3041961 | GEARBOX, Oil Change | 2022-11-04 10:58 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2023-04-08 08:17
9 | WTG-0012-0000 | 3041962 | GEARBOX, Oil Change | 2022-11-04 10:58 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2022-11-30 16:28
2 | GBX-00003 | 3044252 | CMS Gearbox Borescope/needs new CMS monitor | 2022-11-10 10:22 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2023-02-27 22:25
9 | WTG-0107-0000 | 3045508 | GEARBOX, Oil Change | 2022-11-14 11:59 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-03-20 12:27
9 | WTG-0055-0000 | 3045509 | GEARBOX, Oil Change | 2022-11-14 11:59 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2022-11-29 12:22
9 | WTG-0114-0000 | 3045510 | GEARBOX, Oil Change | 2022-11-14 12:01 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-01-13 07:51
9 | WTG-0091-0000 | 3045520 | GEARBOX, Oil Change | 2022-11-14 12:11 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2022-11-30 14:23
1 | WTG-2030-0000 | 3045666 | Gearbox Oil Work/Issue | 2022-11-14 20:16 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | TPARKER |  | 2023-02-23 14:10
1 | WTG-3063-0000 | 3046205 | GEARBOX OIL, Replace IMS seal | 2022-11-16 16:20 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | EMACHALICEK |  | 2023-02-21 11:10
9 | WTG-0034-0000 | 3046210 | GEARBOX, Oil Change | 2022-11-16 16:53 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2022-12-21 13:53
9 | WTG-0032-0000 | 3046211 | GEARBOX, Oil Change | 2022-11-16 16:54 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2022-12-05 22:15
2 | WTG-0014-0000 | 3046459 | CMS Gearbox Borescope | 2022-11-17 08:50 | Closed | CMS | CMSGBXBORE | BETHEL | ACHAVIRA |  | 2022-11-18 14:16
9 | WTG-0066-0000 | 3048881 | GEARBOX, Oil Change | 2022-11-21 11:38 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-01-06 09:44
9 | WTG-0058-0000 | 3049096 | GEARBOX, Oil Change | 2022-11-22 08:26 | Closed | GBXOIL | GBXOILCHG | BETHEL | JGARLAND |  | 2022-12-05 22:10
9 | WTG-0059-0000 | 3049097 | GEARBOX, Oil Change | 2022-11-22 08:26 | Closed | GBXOIL | GBXOILCHG | BETHEL | JGARLAND |  | 2022-12-05 22:11
9 | WTG-0060-0000 | 3049098 | GEARBOX, Oil Change | 2022-11-22 08:27 | Closed | GBXOIL | GBXOILCHG | BETHEL | JGARLAND |  | 2022-12-22 13:10
9 | WTG-0113-0000 | 3050485 | GEARBOX, Oil Change | 2022-11-28 09:09 | Closed | GBXOIL | GBXOILCHG | BETHEL | JGARLAND |  | 2023-05-25 12:46
9 | WTG-0109-0000 | 3050483 | GEARBOX, Oil Change | 2022-11-28 09:06 | Closed | GBXOIL | GBXOILCHG | BETHEL | TMILLER2 |  | 2023-01-31 15:08
2 | GBX-00054 | 3051181 | CMS Gearbox Borescope | 2022-11-29 15:54 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2023-02-03 15:53
1 | WTG-0315-0000 | 3054122 | GEARBOX OIL, Fix oil leak | 2022-12-06 15:06 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | THOLZ |  | 2023-02-10 09:12
9 | WTG-0105-0000 | 3054898 | GEARBOX, Oil Change | 2022-12-08 11:34 | Closed | GBXOIL | GBXOILCHG | BETHEL | MRAHMAN |  | 2023-02-20 15:23
1 | WTG-0037-0000 | 3055602 | GEARBOX OIL, Fix oil leak | 2022-12-12 12:01 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | BPOPE |  | 2024-08-22 08:15
9 | WTG-0111-0000 | 3056322 | GEARBOX, Oil Change | 2022-12-13 10:38 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-03-20 12:32
5 | WTG-0002C-0000 | 3057103 | Oil pump leaking / Top off about 5 gallons | 2022-12-14 14:48 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2023-03-27 10:27
1 | WTG-0208-0000 | 3057998 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2022-12-17 11:56 | Closed | GBXOIL | GBXOILCOOL | PRAIRIE BREEZE2 | THOLZ |  | 2025-03-25 15:53
9 | WTG-0047-0000 | 3060876 | GEARBOX, Oil Change | 2022-12-28 09:19 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-01-26 09:09
1 | WTG-0071-0000 | 3060773 | GEARBOX OIL, Fix oil leak | 2022-12-27 17:54 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | KMERRITT |  | 2023-02-21 15:59
9 | WTG-0079-0000 | 3060905 | GEARBOX, Oil Change | 2022-12-28 10:46 | Closed | GBXOIL | GBXOILCHG | BETHEL | TMILLER2 |  | 2023-02-27 14:01
9 | WTG-0092-0000 | 3063785 | GEARBOX, Oil Change | 2023-01-04 10:18 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-04-12 11:17
9 | WTG-0093-0000 | 3063786 | GEARBOX, Oil Change | 2023-01-04 10:18 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-02-03 12:59
9 | WTG-0067-0000 | 3064753 | GEARBOX, Oil Change | 2023-01-05 13:42 | Closed | GBXOIL | GBXOILCHG | BETHEL | RGRADO |  | 2023-05-02 09:33
2 | WTG-0079-0000 | 3068590 | MB INSPECTION | 2023-01-15 16:09 | Cancelled | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-04-26 07:44
2 | WTG-0096-0000 | 3068592 | MB INSPECTION | 2023-01-15 16:10 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-03-27 12:15
2 | WTG-0109-0000 | 3068593 | MB INSPECTION | 2023-01-15 16:11 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-03-27 12:18
2 | WTG-0117-0000 | 3068594 | MB INSPECTION | 2023-01-15 16:13 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-02-16 09:12
2 | WTG-0118-0000 | 3068595 | MB INSPECTION | 2023-01-15 16:14 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-02-16 09:12
2 | WTG-0149-NDG0-0000 | 3068696 | Nanjing HSS Oil Leak Inspection | 2023-01-16 09:50 | Closed | GBXOIL | GBXOILADD | WAKE 1 | JCULLITY |  | 2023-01-20 11:10
2 | WTG-0032-NDG0-0000 | 3068697 | Nanjing HSS Oil Leak Inspection | 2023-01-16 09:52 | Closed | GBXOIL | GBXOILADD | WAKE 1 | JCULLITY |  | 2023-01-20 11:10
2 | WTG-0073-NDG0-0000 | 3068698 | Nanjing HSS Oil Leak Inspection | 2023-01-16 09:52 | Closed | GBXOIL | GBXOILADD | WAKE 1 | JCULLITY |  | 2023-01-20 11:10
1 | BMEC-DT-001 | 3069336 | WTG001 low oil pressure | 2023-01-18 11:02 | Closed | GBXOIL |  | BUFFALO MOUNT | VFRENCH |  | 2023-05-04 10:34
5 | WTG-0029-NTV0-0000 | 3069367 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-18 11:40 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-01-20 08:55
1 | GBX-00003 | 3070759 | GEARBOX OIL, Particle counter installation | 2023-01-20 16:49 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | GSUGGETT |  | 2023-01-20 17:32
2 | WTG-0027-NDD0-0000 | 3072186 | CMS Generator Bearing Check | 2023-01-25 15:44 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-07-17 11:06
2 | WTG-0038-NDD0-0000 | 3072187 | CMS Generator Bearing Check | 2023-01-25 15:48 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-07-17 09:07
5 | WTG-3061-0000 | 3073895 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-30 12:55 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-02-23 10:15
1 | WTG-00A1-NDGP-0000 | 3078892 | GEARBOX OIL, Particle counter installation | 2023-02-07 10:04 | Cancelled | GBXOIL | GBXPARTINS | COYOTE RIDGE | KHELMS |  | 2023-03-15 13:58
1 | WTG-00C7-NDGP-0000 | 3078893 | GEARBOX OIL, Particle counter installation | 2023-02-07 10:07 | Closed | GBXOIL | GBXPARTINS | COYOTE RIDGE | KHELMS |  | 2023-03-08 11:46
4 | WTG-0084-0000 | 3078978 | Replace two GBX hoses, see comments | 2023-02-07 15:16 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2024-07-19 14:59
2 | WTG-0024-0000 | 3080383 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-11-22 09:44
5 | WTG-0082-NDB0-0000 | 3074286 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-31 15:11 | Closed | CMS | CMSTRBLSHOOT | BETHEL | CBILLIG |  | 2023-05-08 16:24
5 | WTG-0003A-NDGP-0000 | 3078373 | Replace red spider gear | 2023-02-05 13:46 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-02-07 12:09
5 | WTG-0105-0000 | 3080378 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-09-21 14:59
5 | WTG-0116-0000 | 3080379 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-12-07 16:06
5 | WTG-0011-0000 | 3080380 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-10-23 15:34
5 | WTG-0013-0000 | 3080381 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-10-25 09:22
5 | WTG-0002-0000 | 3080382 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-06-19 10:16
5 | WTG-0034-0000 | 3080384 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-11-22 09:46
5 | WTG-0044-0000 | 3080386 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-07-19 16:01
5 | WTG-0005-0000 | 3080387 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-10-26 10:02
5 | WTG-1064-NTV0-0000 | 3080286 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-02-10 10:03 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-02-10 10:05
5 | WTG-0058-0000 | 3080388 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-08-28 15:19
5 | WTG-0067-0000 | 3080389 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-05-02 14:14
5 | WTG-0074-0000 | 3080390 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-08-29 14:55
1 | WTG-0119-0000 | 3080394 | CMS MB Check | 2023-02-10 12:10 | Cancelled | CMS | CMSMB | BETHEL | CBILLIG |  | 2023-03-10 11:25
5 | WTG-0083-0000 | 3080391 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-05-02 09:35
5 | WTG-0084-0000 | 3080392 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-09-07 13:25
5 | WTG-0088-0000 | 3080393 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-09-07 13:26
1 | WTG-0015-0000 | 3080395 | CMS MB Check | 2023-02-10 12:10 | Cancelled | CMS | CMSMB | BETHEL | CBILLIG |  | 2023-03-10 11:26
1 | WTG-0003-0000 | 3080396 | CMS MB Check | 2023-02-10 12:10 | Cancelled | CMS | CMSMB | BETHEL | CBILLIG |  | 2023-03-10 11:26
1 | WTG-0036-0000 | 3080397 | CMS MB Check | 2023-02-10 12:10 | Cancelled | CMS | CMSMB | BETHEL | CBILLIG |  | 2023-03-10 11:26
2 | WTG-0046-NDB0-0000 | 3083846 | CMS Main Bearing Borescope | 2023-02-14 13:49 | Closed | CMS | CMSMBBORE | MAVERICK | JEROMAN |  | 2023-03-27 11:56
4.1 | WTG-0061-0000 | 3083941 | GEARBOX OIL, Fix oil leak | 2023-02-14 14:23 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | THOLZ |  | 2023-10-23 22:54
2 | WTG-0002-NDB0-0000 | 3084027 | CMS Main Bearing Borescope | 2023-02-15 07:55 | Closed | CMS | CMSMBBORE | MAVERICK | JEROMAN |  | 2023-04-07 10:20
1 | WTG-0074-NDB0-0000 | 3084051 | CMS Main Bearing Borescope | 2023-02-15 09:48 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2023-02-22 09:54
2 | WTG-00D9-NDB0-0000 | 3084636 | CMS Main Bearing Borescope | 2023-02-16 14:28 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | CBILLIG |  | 2023-03-22 10:48
1 | WTG-0008-NDGP-0000 | 3086691 | Gearbox Oil overtemp faults | 2023-02-23 12:15 | Closed | GBXOIL | BLANK | MARSH HILL | RTRITES |  | 2023-02-27 08:55
2 | WTG-0075-NDD0-0000 | 3086589 | CMS Generator Bearing Check | 2023-02-23 09:31 | Closed | CMS | CMSGENB | DEUEL HARVEST | ABARNDT |  | 2023-08-11 09:32
1 | WTG-0040-NDD0-0000 | 3086600 | CMS Generator Bearing Check | 2023-02-23 10:23 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-03-31 13:59
3 | WTG-0053-NDD0-0000 | 3086601 | CMS Generator Bearing Check | 2023-02-23 10:27 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-08-31 11:16
3 | WTG-0092-NDD0-0000 | 3086603 | CMS Generator Bearing Check | 2023-02-23 10:29 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-05-15 15:38
2 | WTG-0042-NDG0-0000 | 3088966 | CMS Gearbox Borescope | 2023-03-01 12:44 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | MWILSON |  | 2023-03-28 13:29
5 | WTG-00E3-NDD0-0000 | 3092938 | CMS Generator Bearing Check | 2023-03-03 11:53 | Closed | CMS | CMSGENB | TATANKA RIDGE | CBILLIG |  | 2023-06-06 16:20
5 | WTG-0027-0000 | 3092948 | GEARBOX OIL, Cooler hose leak | 2023-03-03 12:02 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | THOLZ |  | 2023-11-29 21:22
2 | WTG-0015-0000 | 3092929 | CMS Gearbox Borescope | 2023-03-03 11:28 | Closed | CMS | CMSGBXBORE | BETHEL | ACHAVIRA |  | 2023-03-07 09:00
9 | GBX-00081 | 3095126 | T81 GBX Oil Change | 2023-03-09 11:15 | Closed | GBXOIL | GBXOILCHG | PLYMOUTH | TWESTERDAHL |  | 2023-06-30 12:40
9 | GBX-00093 | 3095127 | T93 GBX Oil Change | 2023-03-09 11:18 | Closed | GBXOIL | GBXOILCHG | PLYMOUTH | TWESTERDAHL |  | 2023-09-12 15:11
9 | GBX-00097 | 3095128 | T97 GBX Oil Change | 2023-03-09 11:19 | Closed | GBXOIL | GBXOILCHG | PLYMOUTH | TWESTERDAHL |  | 2023-06-30 12:40
9 | GBX-00100 | 3095130 | T100 GBX Oil Change | 2023-03-09 11:21 | Closed | GBXOIL | GBXOILCHG | PLYMOUTH | TWESTERDAHL |  | 2023-06-30 12:41
2 | GEN-00031 | 3095072 | CMS Generator Bearing Check | 2023-03-09 09:31 | Closed | CMS | CMSGENB | UPSTREAM | CBILLIG |  | 2023-06-23 10:08
1 | WTG-0D11-NDB0-0000 | 3095090 | CMS Main Bearing Borescope | 2023-03-09 10:35 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | CBILLIG |  | 2023-03-23 17:54
1 | WTG-00D3-NDB0-0000 | 3095084 | CMS Main Bearing Borescope | 2023-03-09 10:06 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | CBILLIG |  | 2023-03-22 13:14
2 | GBX-00037 | 3095171 | CMS Gearbox Borescope | 2023-03-09 12:06 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | FALCARAZ |  | 2023-03-28 11:20
9 | GBX-00024 | 3095121 | T24 GBX Oil Change | 2023-03-09 11:10 | Closed | GBXOIL | GBXOILCHG | PLYMOUTH | TWESTERDAHL |  | 2023-06-30 12:41
9 | GBX-00026 | 3095123 | T26 GBX Oil Change | 2023-03-09 11:13 | Closed | GBXOIL | GBXOILCHG | PLYMOUTH | TWESTERDAHL |  | 2023-06-30 12:41
2 | WTG-3021-NDD0-0000 | 3095074 | CMS Generator Bearing Check | 2023-03-09 09:40 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2023-06-27 11:55
5 | WTG-0064-0000 | 3097339 | GEARBOX OIL, Fix oil leak | 2023-03-13 13:59 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | THOLZ |  | 2024-11-08 15:06
5 | WTG-0028-0000 | 3099322 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-15 13:41 | Closed | CMS | CMSTRBLSHOOT | DEUEL HARVEST | ABARNDT |  | 2023-12-11 14:36
3 | WTG-2079-0000 | 3099336 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-15 14:09 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-06-14 12:52
4 | WTG-0048-0000 | 3099337 | Replace Purple GBX Oil Hose | 2023-03-15 14:04 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2023-06-13 11:36
4 | WTG-0023A-0000 | 3099338 | Replace Oil Breather Hose on Primary Filter | 2023-03-15 14:08 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2023-06-09 12:42
5 | WTG-0018-NDGP-0000 | 3101286 | Replace gear oil pump red spider | 2023-03-21 07:03 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-07-20 12:06
1 | WTG-1132-0000 | 3101620 | GEARBOX OIL, Fix oil leak | 2023-03-21 16:40 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | QCROUSE |  | 2023-06-05 12:05
1 | WTG-1105-0000 | 3101622 | GEARBOX OIL, Fix oil leak | 2023-03-21 16:44 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | QCROUSE |  | 2023-06-05 11:14
4 | WTG-0017-0000 | 3101548 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-03-21 14:10 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-09-21 13:05
4 | WTG-0011-NDGP-0000 | 3104935 | Replace red spider insert | 2023-03-29 14:53 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2024-05-08 14:35
4 | WTG-0029A-0000 | 3107939 | GEARBOX OIL, Add 5 Gallons | 2023-04-03 15:16 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-07-17 14:21
5 | WTG-0209-0000 | 3107974 | GEARBOX OIL, Fix oil leakreplace hose. | 2023-04-03 15:08 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | JSTAHLECKER |  | 2024-11-26 13:11
5 | WTG-0209-0000 | 3107975 | GEARBOX OIL, Fix oil leak shrink disk main bearing seal | 2023-04-03 16:32 | Ready to Schedule | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | THOLZ
2 | WTG-0046-NDD0-0000 | 3110038 | CMS Generator Bearing Check | 2023-04-07 13:43 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-10-23 10:57
5 | WTG-0052-NDD0-0000 | 3110040 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-07 13:57 | Closed | CMS | CMSTRBLSHOOT | BETHEL | CBILLIG |  | 2023-08-28 15:20
2 | WTG-0344-NDB0-0000 | 3113027 | CMS Main Bearing Borescope | 2023-04-14 12:37 | Closed | CMS | CMSMBBORE | BISHOP HILL III | CBILLIG |  | 2023-06-02 14:07
1 | WTG-00I5-0000 | 3113853 | Poseidon DM4500 Installation on WEC ZF Gearboxes | 2023-04-17 15:39 | Closed | GBXOIL | GBXPARTINS | TATANKA RIDGE | CBILLIG |  | 2023-07-06 10:18
1 | WTG-0063-0000 | 3113886 | GEARBOX OIL, Fix radiator leak and leaking hose elbow | 2023-04-17 17:03 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2024-10-08 15:06
1 | WTG-1038-0000 | 3113834 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-17 15:06 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2023-05-01 11:13
5 | WTG-0301-0000 | 3114614 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-19 10:22 | Closed | CMS | CMSTRBLSHOOT | BISHOP HILL III | CBILLIG |  | 2023-05-10 15:58
3 | WTG-0053-0000 | 3115482 | CMS Gearbox Borescope | 2023-04-21 10:21 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | ABARNDT |  | 2023-07-18 15:29
4.2 | WTG-0089-0000 | 3116221 | GEARBOX OIL, Replace oil cooler | 2023-04-25 07:45 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCRESSWELL |  | 2023-10-24 06:56
5 | GEN-00044 | 3116094 | CMS Generator Bearing Check | 2023-04-24 13:02 | Cancelled | CMS | CMSGENB | UPSTREAM | CBILLIG |  | 2023-09-14 12:53
5 | WTG-0007-NDGP-0000 | 3116102 | Replace gear oil pump red spider insert | 2023-04-24 13:52 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2025-05-28 14:37
5 | WTG-0011-0000 | 3116880 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-26 13:02 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-04-27 09:52
5 | WTG-0012-0000 | 3116882 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-26 13:05 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-04-27 09:53
5 | WTG-0013-0000 | 3116884 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-26 13:07 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-04-27 09:53
5 | WTG-0015-0000 | 3116887 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-26 13:08 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-04-27 09:54
3 | WTG-2116-0000 | 3116872 | CMS Generator Bearing Check | 2023-04-26 11:39 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2023-05-05 16:41
2 | WTG-00K4-NDG0-0000 | 3116859 | CMS Gearbox Borescope | 2023-04-26 11:01 | Closed | CMS | CMSGBXBORE | TATANKA RIDGE | CBILLIG |  | 2023-06-26 09:37
3 | WTG-0007-0000 | 3116889 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-26 13:17 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-05-12 08:23
5 | WTG-0022-0000 | 3123710 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-08 10:09 | Closed | CMS | CMSTRBLSHOOT | DEUEL HARVEST | ABARNDT |  | 2024-07-25 13:53
3 | WTG-0068-0000 | 3125135 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-10 16:00 | Closed | CMS | CMSTRBLSHOOT | BETHEL | CBILLIG |  | 2025-06-04 09:13
5 | WTG-0026-NDB0-0000 | 3083963 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-02-14 16:04 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | CBILLIG |  | 2024-03-08 15:53
5 | WTG-0057-NDG0-0000 | 3084526 | CMS HSS Check | 2023-02-16 13:17 | Closed | CMS | CMSHSS | THUNDERHEAD | CBILLIG |  | 2023-08-11 14:48
5 | WTG-0110-0000 | 3085515 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-02-20 11:27 | Closed | CMS | CMSTRBLSHOOT | BETHEL | CBILLIG |  | 2025-04-29 14:13
1 | WTG-0018-NDB0-0000 | 3085522 | CMS Main Bearing Check | 2023-02-20 11:42 | Closed | CMS | CMSMB | BETHEL | CBILLIG |  | 2023-03-07 08:53
2 | WTG-0003-NDG0-0000 | 3088006 | CMS HSS Check and Borescope | 2023-02-28 12:12 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-04-21 16:11
1 | WTG-0021-NDGP-0000 | 3096608 | gearbox cooler to pump hose replacement | 2023-03-09 17:21 | Cancelled | GBXOIL | BLANK | JUDITH GAP | LBUELKE |  | 2023-03-20 12:52
2 | WTG-1087-0000 | 3099959 | CMS HSS Check | 2023-03-16 15:51 | Closed | CMS | CMSHSS | TRAVERSE | ABARNDT |  | 2023-04-04 09:31
1 | WTG-1085-NDG0-0000 | 3102896 | Major Gearbox Repair | 2023-03-25 19:43 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | JMCCOY |  | 2023-06-05 10:34
2 | WTG-3030-0000 | 3103797 | CMS Install on WTG | 2023-03-28 12:34 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-06-27 11:56
5 | WTG-0036-0000 | 3113023 | CMS HSS Check | 2023-04-14 12:00 | Closed | CMS | CMSHSS | BLOOMING GROVE | ABARNDT |  | 2023-04-14 16:44
1 | WTG-0067-0000 | 3113032 | GEARBOX OIL, Fix oil leak | 2023-04-14 11:48 | Ready to Schedule | GBXOIL | GBXOILLEAK | BUCKEYE | MLEGLEITER
2 | WTG-0318-0000 | 3114007 | CMS Gearbox Borescope | 2023-04-18 08:28 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | JPOWELL |  | 2023-04-18 14:30
1 | WTG-0071-0000 | 3116148 | GEARBOX OIL, Fix radiator leak and leaking hose elbow | 2023-04-24 16:43 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | ZNASH |  | 2023-11-27 08:58
5 | WTG-0045-0000 | 3116888 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-26 13:08 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-04-27 09:54
3 | WTG-0102-0000 | 3116891 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-26 13:24 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-06-05 14:10
5 | WTG-0026-NT00-0000 | 3125156 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-10 16:48 | Closed | CMS | CMSTRBLSHOOT | BETHEL | CBILLIG |  | 2023-06-27 16:27
1 | WTG-0030-0000 | 3134653 | GEARBOX OIL, Fix radiator leak and leaking hose elbow | 2023-05-31 16:08 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CPOLIFKA |  | 2024-03-14 07:47
3.1 | WTG-00J1-NDG0-0000 | 3132544 | GEARBOX OIL, Particle counter installation | 2023-05-25 10:48 | Closed | GBXOIL | GBXPARTINS | TATANKA RIDGE | CBILLIG |  | 2023-09-29 04:49
3.1 | WTG-00P6-NDG0-0000 | 3132546 | GEARBOX OIL, Particle counter installation | 2023-05-25 10:49 | Closed | GBXOIL | GBXPARTINS | TATANKA RIDGE | CBILLIG |  | 2024-02-13 11:32
1 | WTG-0016-0000 | 3132768 | Poseidon inspection | 2023-05-25 12:59 | Closed | GBXOIL | GBXPARTTS | MAVERICK | MWEBER |  | 2023-07-08 11:26
2 | GBX-00088 | 3134109 | CMS Gearbox Borescope | 2023-05-30 14:33 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | MWILSON |  | 2023-05-31 09:06
4 | WTG-0097-0000 | 3137805 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2023-06-05 13:23 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-07-20 11:38
3 | WTG-1056-0000 | 3142446 | CMS Generator Bearing Check | 2023-06-13 11:04 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2024-02-19 14:04
1 | WTG-0019-NDGP-0000 | 3142463 | GEARBOX OIL, Replace Oil Cooler | 2023-06-13 11:52 | Cancelled | GBXOIL | GBXOILCOOL | WILLOW CREEK | MMCCABE |  | 2023-09-13 11:10
2 | WTG-0030-NDGP-0000 | 3143733 | GEARBOX OIL, Fix oil leak | 2023-06-16 17:43 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | CADAMS |  | 2023-08-31 11:41
3 | WTG-1115-0000 | 3145077 | CMS Generator Bearing Check | 2023-06-21 11:32 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2024-01-02 09:15
2 | WTG-2028-0000 | 3146247 | CMS Generator Bearing Check | 2023-06-23 09:19 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2023-08-21 12:41
2 | WTG-0050-NDG0-0000 | 3146337 | GEARBOX OIL, Add/Top-Off | 2023-06-23 10:48 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2023-11-16 09:46
1 | WTG-0049-0000 | 3153366 | GEARBOX OIL, Fix oil leak | 2023-07-06 09:26 | Closed | GBXOIL | GBXOILLEAK | BETHEL | EAVILA |  | 2023-08-02 17:13
4 | WTG-0049-0000 | 3155269 | CMS HSS Check | 2023-07-11 14:06 | Closed | CMS | CMSHSS | UPSTREAM | ABARNDT |  | 2024-10-08 15:18
5 | WTG-0084-0000 | 3156114 | GEARBOX OIL SECONDARY, Fix oil leak | 2023-07-13 11:34 | Closed | GBXOIL | GBXOILLEAK | FORWARD | DMONROE |  | 2023-10-02 11:59
1 | WTG-0112-0000 | 3156146 | GEARBOX OIL, Fix radiator leak | 2023-07-13 13:42 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CPOLIFKA |  | 2023-07-19 16:03
1 | WTG-0044-0000 | 3156144 | Replace gearbox cooler plenum | 2023-07-13 13:32 | Cancelled | GBXOIL | GBXOILCOOL | SUNDANCE | SDUNAVANT |  | 2023-07-14 17:40
2 | GBX-00110 | 3157669 | GEARBOX OIL, Particle counter troubleshooting | 2023-07-18 08:23 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JWWILSON |  | 2023-07-18 13:42
2 | GBX-00003 | 3157716 | GEARBOX OIL, Particle counter troubleshooting | 2023-07-18 08:50 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JWWILSON |  | 2023-07-18 13:42
5 | WTG-0002-0000 | 3161674 | CMS Install on WTG | 2023-07-25 13:06 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | ABARNDT |  | 2023-09-06 11:53
4 | WTG-0083-NDG0-0000 | 3168850 | GEARBOX OIL, add 5 gals | 2023-08-03 07:07 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2023-09-15 14:57
3 | WTG-2003-0000 | 3168955 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-08-03 10:16 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-08-22 12:11
2 | WTG-0084-NDGP-0000 | 3169799 | Replace oil cooler | 2023-08-04 14:25 | Ready to Schedule | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN
5 | WTG-0063A-0000 | 3170745 | Replace Secondary Pump Shaft Seal | 2023-08-08 07:14 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2023-10-13 14:40
1 | WTG-0024-0000 | 3172623 | GEARBOX OIL, Particle counter removal | 2023-08-11 09:41 | Closed | GBXOIL | GBXPARTREM | BLOOMING GROVE | BVANVALKENBURG |  | 2024-03-21 11:19
1 | WTG-0042-0000 | 3172640 | GEARBOX OIL, Particle counter removal | 2023-08-11 09:47 | Closed | GBXOIL | GBXPARTREM | BLOOMING GROVE | BVANVALKENBURG |  | 2024-01-29 14:55
5 | WTG-0059-0000 | 3174102 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-08-15 08:51 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | ABARNDT |  | 2024-09-12 11:27
2 | WTG-0025-0000 | 3174534 | GEARBOX OIL, Secondary oil pump | 2023-08-15 15:44 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | WBLYTHE |  | 2024-01-08 14:02
4 | WTG-0210A-0000 | 3176246 | Secondary Oil leak | 2023-08-18 09:59 | Cancelled | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE |  | 2023-09-08 10:09
1 | WTG-3025-0000 | 3176213 | GEARBOX OIL, Particle counter troubleshooting | 2023-08-18 12:06 | Closed | GBXOIL | GBXPARTTS | TRAVERSE | LWRIGHT |  | 2023-08-27 14:43
1 | WTG-0031-0000 | 3177168 | CMS Gearbox Borescope | 2023-08-22 09:52 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2023-08-28 09:55
1 | WTG-0009-0000 | 3178088 | GEARBOX OIL, Fix oil leak | 2023-08-24 14:09 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | AUMSCHEID |  | 2023-09-05 11:07
2 | WTG-00G3-0000 | 3181298 | CMS Main Bearing Borescope | 2023-08-30 12:36 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | ABARNDT |  | 2023-09-21 10:01
4 | WTG-0045-NDGP-0000 | 3182753 | Replace Secondary pump seal | 2023-08-31 14:42 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2023-12-15 10:52
1 | WTG-0073-0000 | 3188081 | CMS Main Bearing Check | 2023-09-08 16:20 | Closed | CMS | CMSMB | MAVERICK | AALATORRE |  | 2023-11-13 15:30
4 | WTG-0028-0000 | 3187981 | Oil Cooler Shroud Replacement _Blue Vent tube | 2023-09-08 13:44 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2024-09-23 12:14
4 | WTG-0204A-0000 | 3191499 | Secondary Oil Leak | 2023-09-14 13:19 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2024-06-10 09:46
4 | WTG-0066-0000 | 3191498 | Secondary Oil Leak | 2023-09-14 13:15 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2024-08-26 08:42
1 | GBX-000010 | 3192939 | EM: Gearbox oil overtemperature | 2023-09-18 14:24 | Closed | GBXOIL | EM77 | SPRING CANYON | CMUSTAIN |  | 2023-10-19 10:48
1 | GBX-000001 | 3192937 | EM: Gearbox oil overtemperature | 2023-09-18 14:22 | Cancelled | GBXOIL | EM77 | SPRING CANYON | CMUSTAIN |  | 2023-09-19 16:12
1 | WTG-0010-0000 | 3200293 | EM: Gearbox cooling fan | 2023-10-02 20:42 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | MMILLER |  | 2023-10-05 09:43
3 | WTG-0026-0000 | 3200492 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-03 09:49 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | ABARNDT |  | 2023-10-27 12:28
3 | WTG-0025-0000 | 3201739 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 11:51 | Ready to Schedule | GBXOIL | GBXPARTTS | SUNDANCE | ABARNDT
3 | WTG-0035-0000 | 3201743 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 11:54 | Ready to Schedule | GBXOIL | GBXPARTTS | SUNDANCE | ABARNDT
3 | WTG-0045-0000 | 3201756 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 12:13 | Ready to Schedule | GBXOIL | GBXPARTTS | SUNDANCE | ABARNDT
3 | WTG-0012-0000 | 3201745 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 11:56 | In Progress | GBXOIL | GBXPARTTS | SUNDANCE | ABARNDT
3 | WTG-1035-0000 | 3201853 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 16:31 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
3 | WTG-1050-0000 | 3201851 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 16:08 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
3 | WTG-1111-0000 | 3201852 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 16:22 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
3 | WTG-2080-0000 | 3202568 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-05 14:54 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
3 | WTG-2056-0000 | 3202558 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-05 14:49 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT |  | 2024-01-17 12:23
4 | WTG-0038-0000 | 3206873 | GEARBOX OIL, Add/Top-Off | 2023-10-13 07:53 | Closed | GBXOIL | GBXOILADD | FORWARD | TBUYESKE |  | 2024-05-08 14:45
2 | WTG-0032-NDGP-0000 | 3208541 | GEARBOX OIL LEAK, Front Seal | 2023-10-18 10:52 | Ready to Schedule | GBXOIL | GBXOILLEAK | WILLOW CREEK | CADAMS
4 | WTG-0041A-0000 | 3210057 | GEARBOX OIL, Install O'Hain Oil Bucket LLC | 2023-10-23 14:12 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2024-05-08 14:49
4 | WTG-0041A-0000 | 3210056 | GEARBOX OIL, Add 3 Gallons | 2023-10-23 14:11 | Closed | GBXOIL | GBXOILADD | FORWARD | TBUYESKE |  | 2024-05-08 14:48
1 | WTG-0038-0000 | 3223931 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2023-11-10 10:04 | Closed | GBXOIL | GBXOILCOOL | ORANGEVILLE | CSTRZELEC |  | 2023-11-17 12:17
2 | WTG-0032-0000 | 3224601 | CMS Generator Bearing Check | 2023-11-10 14:21 | Closed | CMS | CMSGENB | PLYMOUTH | ABARNDT |  | 2023-12-08 13:42
1 | WTG-0E12-0000 | 3225880 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:36 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2024-01-30 11:57
4.2 | WTG-0033-0000 | 1401366 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:30 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-27 18:57
1 | WTG-0034-0000 | 3125079 | GEARBOX OIL, Secondary filter system installation | 2023-05-10 14:48 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | MSCHMITT |  | 2023-06-26 14:56
2 | WTG-00I5-NDG0-0000 | 3132523 | GEARBOX OIL, Particle counter removal | 2023-05-25 10:41 | Closed | GBXOIL | GBXPARTREM | TATANKA RIDGE | CBILLIG |  | 2023-07-24 09:32
5 | WTG-0050-0000 | 3134035 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-30 13:14 | Cancelled | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-05-30 13:16
1 | WTG-0020-0000 | 3134245 | GEARBOX OIL, Particle counter troubleshooting | 2023-05-30 17:32 | Closed | GBXOIL | GBXPARTTS | MAVERICK | JMILES |  | 2023-07-08 11:34
1 | WTG-0060-0000 | 3135078 | GEARBOX OIL, Particle counter troubleshooting | 2023-06-01 10:40 | Closed | GBXOIL | GBXPARTTS | MAVERICK | JMILES |  | 2023-10-31 14:59
5 | GEN-00042 | 3135098 | CMS Generator Bearing Check | 2023-06-01 10:48 | Cancelled | CMS | CMSGENB | UPSTREAM | CBILLIG |  | 2023-09-14 12:52
3 | WTG-0085-0000 | 3144096 | CMS Generator Bearing Check | 2023-06-19 09:59 | Closed | CMS | CMSGENB | MAVERICK | ABARNDT |  | 2023-10-30 13:12
3 | WTG-0115-0000 | 3144097 | CMS Generator Bearing Check | 2023-06-19 10:05 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-09-25 13:16
1 | WTG-2033-NDG0-0000 | 3145080 | GEARBOX OIL, Fix oil leak | 2023-06-21 11:42 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | WDEAS |  | 2023-08-01 15:28
1 | GBX-000087 | 3145177 | EM: Gearbox oil overtemperature | 2023-06-21 13:47 | Closed | GBXOIL | EM77 | CAMP SPRINGS I | CMORRIS |  | 2023-07-21 07:31
5 | WTG-0004-NDGP-0000 | 3157653 | GEARBOX OIL, Add/Top-Off 5 gals oil oil | 2023-07-18 07:06 | Cancelled | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2023-10-27 12:41
5 | WTG-0004-NDGP-0000 | 3157651 | Replace red spider on gear oil pump | 2023-07-18 07:04 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-11-14 12:17
1 | WTG-0104-0000 | 3160046 | GEARBOX OIL, Fix radiator leak | 2023-07-21 16:35 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | LDURLER |  | 2025-02-17 15:11
2 | WTG-0028-ND00-0000 | 3166548 | Gearbox Borescope | 2023-08-01 14:54 | Closed | CMS | CMSGBXBORE | CAMP SPRINGS I | JSULLIVAN |  | 2023-08-01 14:58
4 | WTG-0072A-0000 | 3166543 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-08-01 12:05 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-12-15 10:47
3 | WTG-3016-0000 | 3174955 | CMS Main Bearing Check | 2023-08-16 13:18 | Closed | CMS | CMSMB | TRAVERSE | ABARNDT |  | 2023-10-16 16:04
1 | WTG-0312-0000 | 3176118 | CMS Gearbox Borescope | 2023-08-18 10:31 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | ABARNDT |  | 2023-08-19 13:54
4.2 | WTG-0024-0000 | 3188669 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2023-09-11 15:19 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-03-19 15:34
1 | GBX-HAN-EH804A-004/LM040 8 | 3195997 | WTG-004 LOW OIL PRESSURE | 2023-09-25 09:09 | Closed | GBXOIL |  | BUFFALO MOUNT | VFRENCH |  | 2023-12-16 13:48
4 | WTG-0034-0000 | 3198187 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-09-28 15:25 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-07-31 12:11
1 | WTG-0094-0000 | 3201828 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 15:47 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT
1 | WTG-0011-0000 | 3203367 | EM: Gearbox oil level too low alarm | 2023-10-08 06:00 | Closed | GBXOIL | EM425 | BUFFALO MOUNT | CWOOLLEY |  | 2023-12-29 18:34
1 | WTG-0003-0000 | 3203369 | EM: Torque deviation non GE - "LOW WORKING PRESSURE EM163" not deviation related | 2023-10-08 06:01 | Closed | GBXOIL | EM163 | BUFFALO MOUNT | CWOOLLEY |  | 2023-12-29 18:33
3 | WTG-0013-NDG0-0000 | 3212063 | CMS Generator Bearing Check | 2023-10-25 11:47 | Closed | CMS | CMSGENB | UPSTREAM | LXPEREZ |  | 2024-01-23 16:14
4 | WTG-0009-0000 | 3212089 | Jensen pump leaking at the pump shaft seal | 2023-10-25 13:22 | Closed | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE |  | 2024-03-19 15:34
4 | WTG-0002C-0000 | 3218974 | GEARBOX OIL, Add/Top-Off 3-5 gallons | 2023-11-03 07:15 | Cancelled | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-11-17 15:51
1 | WTG-0077-0000 | 3219880 | GEARBOX OIL, Fix oil leak | 2023-11-06 09:42 | Closed | GBXOIL | GBXOILLEAK | BETHEL | MTERRONES |  | 2023-11-07 09:31
1 | WTG-0012-0000 | 3481593 | GEARBOX OIL, Fix oil leak | 2024-12-20 07:35 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | CGREIS |  | 2024-12-23 12:21
1 | WTG-0035-0000 | 3481602 | GEARBOX OIL, Fix oil leak | 2024-12-20 08:29 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | BMEST |  | 2024-12-23 12:21
2 | WTG-0089-NDGP-0000 | 2188005 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2020-02-14 15:29 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2020-02-19 10:17
4 | WTG-0037-TDTA-0000 | 1602060 | Gearbox needs 5Gal. of oil | 2016-11-14 11:58 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2016-11-15 08:57
2 | WTG-0042-NDG0-0000 | 1668731 | GEARBOX OIL, Add/Top-Off | 2017-02-02 14:47 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-02-03 13:14
4.2 | WTG-0041-NDG0-0000 | 1668733 | GEARBOX OIL, Add/Top-Off | 2017-02-02 14:58 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-05-12 10:12
4.2 | WTG-0036-NDG0-0000 | 1668734 | GEARBOX OIL, Add/Top-Off | 2017-02-02 14:59 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-05-04 10:58
4.2 | WTG-0039-NDG0-0000 | 1668738 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:16 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-05-09 17:46
4.2 | WTG-0038-NDG0-0000 | 1668739 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:16 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-05-05 15:08
2 | WTG-0009-NDG0-0000 | 1276562 | GEARBOX OIL, Add/Top-Off | 2016-05-31 10:41 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | RCARSON |  | 2016-05-31 11:16
4 | WTG-0212-NDG0-0000 | 1268917 | GEARBOX OIL, Add/Top-Off | 2016-05-03 13:25 | Closed | GBXOIL | GBXOILADD | FORWARD | JJENSEMA |  | 2016-05-05 09:34
1 | WTG-0022-N000-0000 | 1401543 | Cleaned Oil Spill | 2016-08-12 15:50 | Closed | GBXOIL | GBXOILLEAK | GUNSIGHT | CHUBBARD |  | 2016-08-12 17:58
4.2 | WTG-0032-0000 | 1401365 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:30 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-15 13:10
4.2 | WTG-0039-0000 | 1401378 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:32 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:48
4.2 | WTG-0027-0000 | 1401358 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:29 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-27 18:59
4.2 | WTG-0021-0000 | 1401352 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:28 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-30 16:59
4.2 | WTG-0025-0000 | 1401356 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:29 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:52
4.2 | WTG-0026-0000 | 1401357 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:29 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-27 19:00
4.2 | WTG-0035-0000 | 1401370 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:31 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:49
4.2 | WTG-0036-0000 | 1401375 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:32 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-15 13:07
4.2 | WTG-0037-0000 | 1401376 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:32 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:49
4.2 | WTG-0038-0000 | 1401377 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:32 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-12 12:46
4.2 | WTG-0042-0000 | 1401381 | gearbox oil sample and Post oil change Oil sample | 2016-08-12 14:33 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:35
4.2 | WTG-0019-0000 | 1401350 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:28 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:54
4.2 | WTG-0020-0000 | 1401351 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:28 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:54
4.2 | WTG-0030-0000 | 1401361 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:30 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:50
4.2 | WTG-0008-0000 | 1401328 | gearbox oil sample and Post oil change Oil sample | 2016-08-12 14:24 | Cancelled | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-17 16:24
4.2 | WTG-0011-0000 | 1401334 | gearbox oil sample and Post oil change Oil sample | 2016-08-12 14:24 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-30 17:03
4.2 | WTG-0014-0000 | 1401343 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:26 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-30 17:00
4.2 | WTG-0034-0000 | 1401367 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:31 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:50
4.2 | WTG-0040-0000 | 1401379 | gearbox oi change and Post oil change Oil sample | 2016-08-12 14:33 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-27 18:57
4.2 | WTG-0041-0000 | 1401380 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:33 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:35
4.2 | WTG-0043-0000 | 1401384 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:33 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:34
1 | WTG-0164-NDGP-0000 | 1655567 | GEARBOX OIL, Oil Sample | 2017-01-05 13:13 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS II | MSNOW |  | 2017-09-01 15:13
1 | WTG-0174-NDGP-0000 | 1655568 | GEARBOX OIL, Oil Sample | 2017-01-05 13:15 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS II | MSNOW |  | 2017-02-10 09:26
1 | WTG-0059-NDGP-0000 | 1267381 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:34 | Closed | GBXOIL | GBXFILTELEM | GRAND RIDGE | MSNOW |  | 2016-12-06 09:10
9 | WTG-0012-NDG0-0000 | 1281550 | Tower Clean Up Needed due to oi leak - Gearbox Hose | 2016-06-10 15:39 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2017-09-14 16:39
2 | WTG-0082-NDG0-0000 | 1260348 | GEARBOX OIL, Oil Sample | 2016-04-07 14:28 | Closed | GBXOIL | GBXOILSAMP | JUDITH GAP | JJUTILA |  | 2016-04-08 09:48
1 | WTG-0034-NDGP-0000 | 1272489 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 13:51 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | RJOHNSON |  | 2016-10-28 06:11
1 | WTG-0027-NDGP-0000 | 1272490 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 13:51 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | RJOHNSON |  | 2017-01-10 07:32
1 | WTG-0091-NDGP-0000 | 1272491 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 13:51 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | RJOHNSON |  | 2017-01-10 07:32
1 | WTG-0051-NDGP-0000 | 1272492 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | MCADOO | RJOHNSON |  | 2016-07-22 12:55
1 | WTG-0018-NDGP-0000 | 1272493 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | MCADOO | RJOHNSON |  | 2016-08-04 08:32
1 | WTG-0049-NDGP-0000 | 1272494 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | MCADOO | RJOHNSON |  | 2016-07-22 12:55
1 | WTG-0054-NDGP-0000 | 1272495 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | MCADOO | RJOHNSON |  | 2016-07-22 12:55
1 | WTG-0015-NDGP-0000 | 1272496 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | MCADOO | RJOHNSON |  | 2016-06-24 09:09
1 | WTG-0009-NDGP-0000 | 1272497 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | MCADOO | RJOHNSON |  | 2016-06-15 08:12
1 | WTG-0003-NDGP-0000 | 1272498 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | MCADOO | RJOHNSON |  | 2016-06-10 10:44
1 | WTG-0012-NDG0-0000 | 1404860 | GEARBOX OIL, Fix oil leak | 2016-08-24 06:13 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | ZMUELLER |  | 2016-08-29 14:56
9 | WTG-0019-0000 | 1655430 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2017-01-05 08:34 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | KIRBY | 30 | 2017-01-26 15:20
1 | WTG-0036-0000 | 1096760 | GEARBOX OIL, Oil Sample | 2015-02-24 12:17 | Closed | GBXOIL | GBXOILSAMP | CAL RIDGE | JCHEUVRONT |  | 2015-03-06 15:44
1 | WTG-0098-0000 | 1096761 | GEARBOX OIL, Oil Sample | 2015-02-24 12:19 | Closed | GBXOIL | GBXOILSAMP | CAL RIDGE | JCHEUVRONT |  | 2015-03-06 15:45
1 | WTG-0110-0000 | 1096586 | GEARBOX OIL, Oil Sample | 2015-02-24 09:22 | Closed | GBXOIL | GBXOILSAMP | CAL RIDGE | BCAPPELLO |  | 2015-03-06 15:45
1 | WTG-0122-0000 | 1096587 | GEARBOX OIL, Oil Sample | 2015-02-24 09:23 | Closed | GBXOIL | GBXOILSAMP | CAL RIDGE | BCAPPELLO |  | 2015-03-06 15:45
5 | WTG-0041A-NDGP-0000 | 1100005 | GBXOILLEAK - Oil Cooler Leak | 2015-02-27 14:58 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ACARR |  | 2015-03-02 10:50
2 | WTG-0002C-NDGP-0000 | 1111007 | WTG #2_Gearbox Oil Cooler is leaking and needs to be replaced | 2015-03-23 08:02 | Closed | GBXOIL | GBXOILCOOL | FORWARD | RSOBER |  | 2015-07-27 09:11
1 | WTG-0201-0000 | 1222220 | HSS oil leak 201 | 2015-12-18 16:45 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | CHADDIX |  | 2016-09-20 16:17
1 | WTG-0205-NDG0-0000 | 1555479 | GEARBOX OIL, Fix oil leak | 2016-09-22 15:50 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE |  | 2017-03-03 16:47
1 | WTG-0E05-NDG0-0000 | 1230007 | Leaking oil cooler pump. | 2016-01-08 14:06 | Closed | GBXOIL | GBXOILCOOL | HIGH SHELDON | BHUNTER |  | 2016-01-11 10:00
1 | GBX-000022 | 1281941 | GEARBOX OIL, Fix oil leak | 2016-06-13 07:26 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | DWEINGARDT |  | 2016-06-15 21:47
1 | WTG-0060-NDG0-0000 | 1574941 | GEARBOX OIL, Fix oil leak | 2016-10-01 10:25 | Closed | GBXOIL | GBXOILLEAK | MCADOO | DHALE |  | 2016-10-03 09:09
1 | WTG-0039-NDGP-0000 | 1606499 | GEARBOX OIL, Replace oil cooler hose | 2016-11-18 17:29 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | JFREEMAN |  | 2016-12-30 07:30
1 | WTG-0035-NDGP-0000 | 1642639 | GEARBOX OIL, Replace oil cooler fan motor | 2016-12-15 07:39 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-08-14 12:07
1 | WTG-0I09-NDGP-0000 | 1642657 | GEARBOX OIL, Oil Sample | 2016-12-15 09:51 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | MSNOW |  | 2017-01-03 08:31
1 | WTG-0114-0000 | 1667302 | GEARBOX OIL, Replace oil cooler hose | 2017-02-01 15:22 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-02-06 16:14
5 | WTG-0012-NDGP-0000 | 1602322 | GEARBOX OIL, Secondary filter system element change | 2016-11-15 12:39 | Closed | GBXOIL | GBXFILTELEM | WOLVERINE CREEK | DSTEO |  | 2016-11-18 08:35
1 | WTG-0055-NDGP-0000 | 1602414 | GEARBOX OIL, Replace oil cooler hose | 2016-11-16 09:00 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | JFREEMAN |  | 2017-04-13 07:22
4.2 | WTG-0011-NDG0-0000 | 1668759 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:21 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-20 06:50
4.2 | WTG-0012-NDG0-0000 | 1668761 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:21 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-22 09:42
4.2 | WTG-0013-NDG0-0000 | 1668763 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:22 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-22 09:41
4.2 | WTG-0014-NDG0-0000 | 1668764 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:23 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-23 14:40
4.2 | WTG-0015-NDG0-0000 | 1668765 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:24 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-14 10:09
4.2 | WTG-0016-NDG0-0000 | 1668766 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:24 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-28 10:08
4.2 | WTG-0019-NDG0-0000 | 1668769 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:25 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-30 15:20
4.2 | WTG-0001-NDG0-0000 | 1668742 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:17 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-02-16 08:39
4.2 | WTG-0002-NDG0-0000 | 1668744 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:18 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-02-17 11:38
4.2 | WTG-0004-NDG0-0000 | 1668746 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:18 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-06-29 10:59
4.2 | WTG-0005-NDG0-0000 | 1668749 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:18 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-02-27 07:55
4.2 | WTG-0027-NDG0-0000 | 1668750 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:19 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-04-14 08:15
4 | WTG-0056A-NDG0-0000 | 1644657 | Replace Gearbox Hose | 2016-12-20 08:46 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2017-01-04 12:14
4.2 | WTG-0040-NDG0-0000 | 1668737 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:15 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-05-09 17:46
1 | WTG-0017-N000-0000 | 1252900 | GEARBOX OIL, Suck out bottom of nacelle | 2016-03-16 15:11 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | JCUMMINGS |  | 2016-03-17 15:03
9 | WTG-0080-0000 | 1602034 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-11-14 08:50 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS | 30 | 2016-12-29 14:44
9 | WTG-0036-0000 | 1602035 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-11-14 08:51 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS | 30 | 2017-02-06 13:01
9 | WTG-0070-NDG0-0000 | 1281555 | Tower Clean Up Needed due to oi leak - Oil Cooler | 2016-06-10 15:45 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2016-07-15 09:51
1 | WTG-0079-0000 | 1281561 | GEARBOX OIL, Fix oil leak | 2016-06-10 16:02 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MIAMI |  | 2016-06-30 07:51
9 | WTG-0044-NDG0-0000 | 1281564 | Tower Clean Up Needed due to oi leak - Gearbox | 2016-06-10 15:46 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2016-08-18 09:24
3 | WTG-0025-NDGP-0000 | 1281516 | Install Winergy oil pump inversion kit | 2016-06-10 12:14 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2016-09-30 14:10
9 | WTG-0025-NDG0-0000 | 1281552 | Tower Clean Up Needed due to oi leak - Gearbox Botton Bolt Nanjing issue | 2016-06-10 15:42 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2016-12-19 09:43
9 | WTG-0052-NDG0-0000 | 1281553 | Tower Clean Up Needed due to oi leak - Gearbox Front Seal - AA Wind Pro | 2016-06-10 15:43 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2017-02-16 15:13
9 | WTG-0009-NDG0-0000 | 1281554 | Tower Clean Up Needed due to oi leak - Oil Cooler | 2016-06-10 15:44 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2016-07-19 13:05
9 | WTG-0014-NDG0-0000 | 1281551 | Tower Clean Up Needed due to oi leak - Filter Housing | 2016-06-10 15:41 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2017-01-09 08:45
1 | WTG-0026-0000 | 1231660 | GEARBOX OIL, Oil Sample | 2016-01-19 08:17 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | KCOOPER |  | 2016-01-22 10:37
1 | WTG-0022-0000 | 1231667 | GEARBOX OIL, Oil Sample | 2016-01-19 08:36 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | MBELCHER |  | 2016-01-22 10:37
1 | WTG-0031-NDGP-0000 | 1237044 | EM: Gearbox oilpressure mechanical pump not OK | 2016-02-01 15:01 | Closed | GBXOIL | EM256 | MCADOO | BJAMESON |  | 2016-02-02 08:22
5 | WTG-0007-NDGP-0000 | 1612353 | GEARBOX OIL,( Replace gear oil pump motor) | 2016-11-28 16:18 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-12-02 14:23
1 | WTG-0003-NDGP-0000 | 1851052 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2018-03-09 08:04 | Closed | GBXOIL | GBXOILCOOL | GRAND RIDGE | SSMITH |  | 2018-10-11 15:58
2 | WTG-0009-0000 | 1822609 | Add Oil to Gearbox | 2017-12-06 16:15 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 16:32
2 | WTG-0021-0000 | 1822611 | Add Oil to Gearbox | 2017-12-06 16:19 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 16:31
1 | GBX-000095 | 1660664 | Gearbox noise | 2017-01-19 17:46 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | JSTAHLECKER |  | 2017-01-26 12:21
1 | WTG-0019-NDG0-0000 | 1646117 | GEARBOX OIL, Fix oil leak | 2016-12-22 08:34 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | JBRILEY |  | 2016-12-22 10:44
1 | WTG-0001-0000 | 1251255 | Gearbox Oil Work/Issue | 2016-03-07 17:50 | Closed | GBXOIL | GBXOILLEAK | STANTON | DAVANT |  | 2016-03-28 06:57
2 | GBX-000011 | 1260330 | Radiator Oil Cooler Leak - Cap leak | 2016-04-07 12:15 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2016-05-20 15:29
2 | WTG-0022-NDG0-0000 | 1261504 | Oil hose leaking from crimp | 2016-04-14 13:17 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | STAYLOR |  | 2017-04-30 19:46
1 | WTG-0075-0000 | 1235297 | GEARBOX OIL, Fix oil leak | 2016-01-31 18:34 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | JLAPPIN |  | 2016-02-24 09:31
2 | WTG-0013-NDG0-0000 | 1402242 | GEARBOX OIL, Fix oil leak on filter pot | 2016-08-16 14:40 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2016-08-18 14:26
4.2 | WTG-0136-NDG0-0000 | 1001603 | Post-Gearbox Oil Change Oil Sample | 2014-05-08 15:52 | Closed | GBXOIL |  | GRAND RIDGE IV | R5 |  | 2015-04-29 14:57
1 | WTG-0025-NDGP-0000 | 1271760 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-05-14 12:57 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | ZMUELLER |  | 2016-06-13 10:53
1 | WTG-0078-NDG0-0000 | 1241661 | GEARBOX OIL, Fix oil leak | 2016-02-10 10:49 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | JBRILEY |  | 2016-02-10 15:09
1 | WTG-0037-NDGP-0000 | 1272513 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 12:51 | Closed | GBXOIL | GBXFILTELEM | VANTAGE | RJOHNSON |  | 2018-06-01 09:24
2 | WTG-0013-NDGP-0000 | 1272484 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Closed | GBXOIL | GBXFILTELEM | GOLDTHWAITE | RJOHNSON |  | 2017-05-16 09:46
2 | WTG-0015-NDGP-0000 | 1272485 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Closed | GBXOIL | GBXFILTELEM | GOLDTHWAITE | RJOHNSON |  | 2017-09-26 09:23
1 | WTG-0076-NDGP-0000 | 1272469 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS I | RJOHNSON |  | 2017-08-03 15:26
1 | WTG-0063-NDGP-0000 | 1272470 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS I | RJOHNSON |  | 2017-08-03 15:26
3 | WTG-0132-NDGP-0000 | 1272471 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS II | RJOHNSON |  | 2017-08-03 15:24
1 | WTG-0121-NDGP-0000 | 1272472 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS II | RJOHNSON |  | 2017-08-03 15:20
1 | WTG-0108-NDGP-0000 | 1272473 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | CAMP SPRINGS II | RJOHNSON |  | 2017-08-03 15:19
1 | WTG-0096-NDGP-0000 | 1272486 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | GREXP | RJOHNSON |  | 2017-01-17 12:43
1 | WTG-0116-NDGP-0000 | 1272487 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | GREXP | RJOHNSON |  | 2017-06-22 07:51
1 | WTG-0008-NDGP-0000 | 1272488 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 13:51 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | RJOHNSON |  | 2016-09-28 08:52
1 | WTG-0026-NDGP-0000 | 1272499 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | MCADOO | RJOHNSON |  | 2016-06-29 11:46
1 | WTG-0057-NDGP-0000 | 1272500 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | MCADOO | RJOHNSON |  | 2016-06-10 10:45
1 | WTG-0026-NDGP-0000 | 1272501 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | STANTON | RJOHNSON |  | 2016-10-24 13:14
1 | WTG-0042-NDG0-0000 | 1353502 | Gearbox has crack in the bottom of the housing | 2016-07-27 13:37 | Closed | GBXOIL | GBXOILLEAK | STANTON | JMORRIS |  | 2016-11-30 12:31
1 | WTG-0025-0000 | 1642696 | Leaking Filter Housing | 2016-12-13 13:59 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CSEIDER |  | 2016-12-19 09:42
1 | WTG-0115-NDG0-0000 | 1656827 | GEARBOX OIL, Fix oil leak | 2017-01-09 11:15 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | CAL RIDGE |  | 2018-02-19 11:31
9 | WTG-0091-0000 | 1188554 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 08:54 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
9 | WTG-0063-0000 | 1188557 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:00 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:46
9 | WTG-0081-0000 | 1188559 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:04 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
1 | GBX-000107 | 1112800 | Pall Filter Housing Leak | 2015-03-26 19:33 | Closed | GBXOIL | EM89 | PRAIRIE BREEZE | DHOLTER |  | 2015-04-02 11:20
4 | WTG-0055A-NDGP-0000 | 1275105 | GEARBOX OIL, Replace oil pump | 2016-05-26 11:34 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-06-01 12:31
4 | WTG-0040A-NDGP-0000 | 1275198 | GEARBOX OIL, Replace oil cooler fan/motor/pump(pump leaking) | 2016-05-26 13:55 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2016-07-13 09:19
1 | WTG-0079-0000 | 1279447 | GEARBOX OIL, Fix oil leak | 2016-06-02 11:08 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2016-08-19 09:20
1 | WTG-0109-NDG0-0000 | 1600860 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:57 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 07:48
9 | WTG-0044-NDG0-0000 | 1600809 | Tower Clean Up Needed - Inspect | 2016-11-07 12:27 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2017-04-11 10:08
3 | WTG-0004-NDGP-0000 | 1337733 | GEARBOX OIL, Fix oil leak | 2016-06-29 12:51 | Cancelled | GBXOIL | GBXOILLEAK | JUDITH GAP | RCARSON |  | 2017-08-17 18:17
9 | WTG-0031-0000 | 1343128 | Gearbox replaced Oil Converted to Amsoil | 2016-07-08 10:35 | Closed | GBXOIL | GBXOILCHG | GOLDTHWAITE | DDIAZ |  | 2016-07-08 10:45
9 | WTG-0086-0000 | 1343129 | Gearbox replaced Oil Converted to Amsoil | 2016-07-08 10:37 | Closed | GBXOIL | GBXOILCHG | GOLDTHWAITE | DDIAZ |  | 2016-07-08 10:45
9 | WTG-0079-0000 | 1343130 | Gearbox Replaced Oil converted to Amsoil | 2016-07-08 10:39 | Closed | GBXOIL | GBXOILCHG | GOLDTHWAITE | DDIAZ |  | 2016-07-08 10:45
9 | WTG-0008-0000 | 1343131 | Gearbox Replaced Oil converted to Amsoil | 2016-07-08 10:41 | Closed | GBXOIL | GBXOILCHG | GOLDTHWAITE | DDIAZ |  | 2016-07-08 10:45
1 | WTG-0009-0000 | 1346953 | Oil sample | 2016-07-21 15:09 | Closed | GBXOIL | GBXOILSAMP | PRAIRIE BREEZE | NSCHINDLER |  | 2016-07-26 17:33
1 | WTG-0034-NDGP-0000 | 1655202 | GEARBOX OIL, Secondary filter system element change | 2017-01-04 10:55 | Closed | GBXOIL | GBXFILTELEM | WOLVERINE CREEK | DSTEO |  | 2017-01-04 14:09
4 | WTG-0059A-NDGP-0000 | 1645981 | EM: Gear oil temperature switching contact ( oil cooler fan not going High) | 2016-12-21 14:29 | Closed | GBXOIL | EM72 | FORWARD | FORWARD |  | 2017-01-04 13:58
2 | WTG-0090-NDGP-0000 | 1581170 | GEARBOX OIL, Fix oil leak(flange between filter housing and pump) | 2016-10-05 15:07 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2018-01-18 14:03
1 | WTG-0012-NDGP-0000 | 1581427 | Radiator Replacement | 2016-10-06 07:48 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | AMARTORANA |  | 2016-10-10 09:07
2 | WTG-0065-NDGP-0000 | 1581025 | GEARBOX OIL, Particle counter troubleshooting | 2016-10-05 11:55 | Closed | GBXOIL | GBXPARTINS | MCADOO | MSNOW |  | 2016-10-07 14:59
4 | WTG-0204A-NDGP-0000 | 1516189 | GEARBOX OIL, Replace oil pump | 2016-09-16 15:02 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-01-16 15:48
3 | WTG-0035-NDGP-0000 | 1595780 | Install Winergy oil pump inversion kit | 2016-10-31 10:05 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2016-11-14 08:07
3 | WTG-0005-NDGP-0000 | 1595781 | Install Winergy oil pump inversion kit | 2016-10-31 10:05 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2016-11-17 13:57
2 | WTG-0005-0000 | 1595787 | GEARBOX OIL, Add/Top-Off | 2016-10-31 10:06 | Closed | GBXOIL | GBXOILADD | WILLOW CREEK | MSTONER |  | 2016-11-17 13:57
9 | WTG-0083-0000 | 1647349 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-12-27 12:19 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH | 30 | 2017-01-03 13:29
4 | WTG-0090-NDG0-0000 | 1659575 | EM: Gearbox oil level too low | 2017-01-15 18:45 | Closed | GBXOIL | EM51 | RONCEVAUX | CRO EAST |  | 2017-01-17 08:42
1 | WTG-0015-0000 | 1668001 | Gearbox leaking | 2017-02-02 08:00 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | RWALL |  | 2018-04-02 15:05
2 | WTG-0020-NDGP-0000 | 1600110 | GEARBOX OIL, Particle counter removal | 2016-11-04 11:58 | Closed | GBXOIL | GBXPARTREM | TURKEY TRACK | MSNOW |  | 2016-11-08 07:42
1 | WTG-0142-NDG0-0000 | 1649621 | Fix leaks on Nanjing gearboxes | 2016-12-28 14:31 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 07:47
1 | WTG-0152-0000 | 1649623 | GEARBOX OIL, Replace oil cooler hose | 2016-12-28 14:36 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-04 11:14
1 | WTG-0102-NDGP-0000 | 1649636 | GEARBOX OIL, Fix oil leak | 2016-12-27 14:44 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2017-01-19 14:43
1 | WTG-0150-0000 | 1649622 | GEARBOX OIL, Replace oil cooler hose | 2016-12-28 14:35 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-04 11:14
1 | WTG-0122-0000 | 1151534 | GEARBOX OIL, Fix oil leak | 2015-06-18 07:10 | Closed | GBXOIL | GBXOILLEAK | GREXP | CCOTTINGHAM |  | 2017-12-19 16:00
1 | WTG-0024-0000 | 1209703 | Clean up oil in belly | 2015-11-24 08:25 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2018-02-03 16:40
2 | WTG-0058-0000 | 1218049 | Pre-Gearbox Oil Change Detergent Add | 2015-12-04 16:44 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NKLEIBER | 1 | 2015-12-08 10:04
2 | WTG-0061-0000 | 1218050 | Pre-Gearbox Oil Change Detergent Add | 2015-12-04 16:47 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NKLEIBER | 1 | 2015-12-08 10:05
5 | WTG-0014-0000 | 1221751 | GEARBOX OIL, Fix oil leak | 2015-12-16 16:25 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2016-04-06 16:13
1 | WTG-0203B-NDG0-0000 | 1227730 | GEARBOX OIL, Fix oil leak | 2016-01-04 11:01 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2016-01-21 10:22
1 | WTG-0031-NDG0-0000 | 1038355 | Gearbox Oil Sample (Special) | 2014-09-02 14:20 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | MCONWELL |  | 2015-03-16 12:34
1 | WTG-0010-NDG0-0000 | 1038410 | Gearbox Oil Sample (Special) | 2014-09-02 14:20 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | MCONWELL |  | 2015-03-03 09:07
9 | WTG-0002-0000 | 1246931 | GEARBOX, Oil Change | 2016-02-29 15:08 | Closed | GBXOIL | GBXOILCHG | RATTLESNAKE 1 | JGASTON |  | 2016-03-25 09:54
9 | WTG-0006-0000 | 1246943 | GEARBOX, Oil Change | 2016-02-29 15:22 | Closed | GBXOIL | GBXOILCHG | RATTLESNAKE 1 | JGASTON |  | 2016-03-25 09:54
1 | WTG-0079-0000 | 1248710 | Filter housing replacement | 2016-03-01 09:06 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | LPORTER |  | 2016-03-31 07:21
1 | WTG-0032-0000 | 1253274 | Install secondary filtration system on gearbox oil | 2016-03-18 14:34 | Closed | GBXOIL | GBXFILTINS | GRAND RIDGE | GRAND RIDGE | 1 | 2016-03-18 14:42
1 | WTG-0045-NDGP-0000 | 1254394 | Replace oil pump | 2016-03-25 13:56 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2016-03-28 09:57
1 | WTG-0G04-0000 | 1640659 | Post Gear Box Oil Sample CT 320 | 2016-12-12 07:09 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2016-12-12 07:49
1 | WTG-0G05-0000 | 1640660 | Post Gear Box Oil Sample CT 320 | 2016-12-12 07:30 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2016-12-12 07:45
1 | WTG-0K01-0000 | 1640661 | Post Gear Box Oil Sample CT 320 | 2016-12-12 07:30 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2016-12-12 07:57
1 | WTG-0K04-0000 | 1640662 | Post Gear Box Oil Sample CT 320 | 2016-12-12 07:31 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2016-12-12 07:33
2 | WTG-0151-NDG0-0000 | 1102337 | GEARBOX OIL, Oil Sample | 2015-03-03 11:31 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS II | MSNOW |  | 2015-03-06 15:07
1 | WTG-0144-0000 | 1103881 | GEARBOX OIL, Fix oil leak | 2015-03-09 08:45 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KYARNOLD |  | 2015-06-19 07:36
4 | WTG-0020-NDGP-0000 | 1243551 | Lube Pump Leaking - Replace Lube Pump | 2016-02-17 09:50 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2016-02-22 14:56
1 | WTG-0079-0000 | 1279536 | GEARBOX OIL, Oil Sample | 2016-06-02 15:45 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | JGASTON |  | 2016-06-03 15:08
1 | WTG-0082-0000 | 1279537 | GEARBOX OIL, Oil Sample | 2016-06-02 15:46 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | JGASTON |  | 2016-06-03 15:09
1 | WTG-0007-NDGP-0000 | 1152727 | GEARBOX OIL, Replace oil pump motor | 2015-06-24 13:15 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TALVARADO |  | 2015-06-26 07:55
1 | WTG-0077-0000 | 1154299 | GEARBOX OIL, Oil Sample | 2015-06-29 13:09 | Closed | GBXOIL | GBXOILSAMP | GRATIOT | NMARTYN |  | 2015-06-29 14:13
4.2 | WTG-0073-NDG0-0000 | 1001366 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GREXP | R5 |  | 2015-03-04 14:19
4.2 | WTG-0097-NDG0-0000 | 1001380 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GREXP | R5 |  | 2015-03-26 14:56
4.2 | WTG-0099-NDG0-0000 | 1001381 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GREXP | R5 |  | 2015-03-30 14:54
2 | WTG-0072-0000 | 1191648 | GEARBOX OIL, Fix oil leak | 2015-10-16 07:51 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CWADE |  | 2016-03-08 11:50
1 | WTG-0232-NDG0-0000 | 1594937 | GEARBOX OIL, Fix oil leak | 2016-10-28 08:34 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE |  | 2017-12-05 15:59
4 | WTG-0002-0000 | 1401061 | Post oil change Oil sample | 2016-08-11 16:48 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CHUBBARD |  | 2016-08-12 18:03
4 | WTG-0001-0000 | 1401062 | Gearbox Oil change Post oil change Oil sample | 2016-08-11 16:50 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CHUBBARD |  | 2016-08-12 18:02
1 | WTG-0081-0000 | 1430641 | replace inlet hose | 2016-09-09 13:51 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | CAL RIDGE |  | 2016-09-14 13:35
1 | WTG-0042-0000 | 1239936 | GEARBOX OIL, Fix oil leak | 2016-02-07 14:44 | Closed | GBXOIL | GBXOILLEAK | STANTON | CINGRAM |  | 2016-04-22 11:58
1 | WTG-0072-NDG0-0000 | 1243852 | GEARBOX OIL, Oil Sample | 2016-02-17 15:45 | Closed | GBXOIL | GBXOILSAMP | PRAIRIE BREEZE | CBUHRMAN |  | 2016-02-24 17:52
4 | WTG-0023A-NDGP-0000 | 1280651 | Gearbox Oil Pump Leaking - Needs Replaced | 2016-06-07 06:55 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-10-21 10:21
5 | WTG-0001-ND00-0000 | 1410661 | GEARBOX OIL, Particle counter removal | 2016-08-26 17:56 | Closed | GBXOIL | GBXPARTREM | ORANGEVILLE | MSNOW |  | 2016-09-14 10:57
5 | WTG-0055-ND00-0000 | 1410662 | GEARBOX OIL, Particle counter removal | 2016-08-26 17:57 | Closed | GBXOIL | GBXPARTREM | ORANGEVILLE | MSNOW |  | 2016-09-14 10:57
2 | WTG-0013-NDGP-0000 | 1443174 | GBX Oil Leak | 2016-09-12 07:52 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2016-09-27 15:55
1 | WTG-0043-0000 | 1649593 | GEARBOX OIL, Replace oil cooler hose | 2016-12-28 13:22 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-08-08 08:51
1 | WTG-0004-0000 | 1649598 | GEARBOX OIL, Replace oil cooler hose | 2016-12-28 13:30 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-04-24 07:37
1 | WTG-0041-0000 | 1649599 | GEARBOX OIL, Replace oil cooler hose | 2016-12-28 13:41 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-03-30 07:17
1 | WTG-0052-0000 | 1649602 | GEARBOX OIL, Replace oil cooler hose | 2016-12-28 13:46 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-04-07 07:39
4 | WTG-0098-NDG0-0000 | 1578290 | GEARBOX OIL, Replace oil pump | 2016-10-04 09:17 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-10-05 14:42
5 | WTG-0004-NDG0-0000 | 1656825 | GEARBOX OIL, Fix oil leak - inlet hose | 2017-01-09 11:04 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | CAL RIDGE |  | 2017-04-03 13:59
1 | WTG-0061-NDGP-0000 | 1643224 | GEARBOX OIL, Fix oil leak | 2016-12-15 16:58 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | SMILLER |  | 2016-12-19 07:23
1 | WTG-0097-NDG0-0000 | 1001476 | Pre-Gearbox Oil Change Detergent Add | 2014-05-08 15:51 | Closed | GBXOIL | GBXOILSAMP | GREXP | R5 |  | 2015-03-24 06:49
9 | WTG-0054-0000 | 1610740 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-11-28 11:26 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ | 30 | 2016-12-29 14:44
1 | WTG-0028-0000 | 1643183 | GEARBOX OIL, Fix oil leak | 2016-12-15 10:34 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH |  | 2017-02-07 14:33
1 | WTG-0020-0000 | 1234033 | Oil Filter Seal Replacement | 2016-01-28 07:32 | Closed | GBXOIL | GBXOILCOOL | CAL RIDGE | BDAILY |  | 2016-01-29 09:01
2 | WTG-0092-NDGP-0000 | 1107221 | Change Jensen System Filter | 2015-03-11 14:28 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE | CBORER |  | 2015-07-15 17:28
2 | WTG-0013-NDGP-0000 | 1107219 | Change Jensen System Filter | 2015-03-11 14:28 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE | CBORER |  | 2015-04-02 11:07
2 | WTG-0089-NDGP-0000 | 1107220 | Change Jensen System Filter | 2015-03-11 14:28 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE | CBORER |  | 2015-07-15 17:28
1 | GBX-000022 | 1108913 | Gearbox Oil Work/Issue (K 11 contacor slow side cooling needs replaced) | 2015-03-18 12:48 | Closed | GBXOIL | GBXOILCOOL | CAL RIDGE | MPUCKETT |  | 2015-05-04 08:12
5 | WTG-0089-NDGP-0000 | 1091351 | GEARBOX OIL, Fix oil leak | 2015-02-04 09:01 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ACARR |  | 2015-05-21 12:09
1 | WTG-0213-NDG0-0000 | 1130636 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2015-04-28 15:56 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2015-05-04 11:16
1 | WTG-0050-NDG0-0000 | 1683465 | Gearbox Oil Work/Issue | 2017-03-10 15:03 | Closed | GBXOIL | GBXOILLEAK | CAMP SPRINGS I | JSULLIVAN |  | 2017-03-10 15:07
1 | WTG-0086-NDG0-0000 | 1686346 | GEARBOX OIL, Fix oil leak | 2017-03-24 13:16 | Closed | GBXOIL | GBXOILLEAK | CAMP SPRINGS I | AHILL |  | 2017-03-31 07:57
2 | WTG-0086-NDGP-0000 | 1696870 | GEARBOX OIL, Replace oil cooler fan/motor/pump-Bearings starting to fail | 2017-04-20 13:27 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-06-08 13:49
1 | WTG-0141-NDGP-0000 | 1705595 | GEARBOX OIL, Fix oil leak | 2017-05-04 12:37 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | BWHEELER |  | 2017-05-22 11:09
1 | WTG-0141-NDGP-0000 | 1705596 | GEARBOX OIL, Fix oil leak | 2017-05-04 12:37 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | BWHEELER |  | 2017-05-22 11:09
1 | WTG-0142-NDG0-0000 | 1705597 | GEARBOX OIL, Fix oil leak | 2017-05-04 12:42 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | BWHEELER |  | 2017-05-22 11:09
2 | CSI-WTG-077 | 1708891 | EM: Gearbox oil overtemperature | 2017-05-18 12:11 | Closed | GBXOIL | EM77 | CAMP SPRINGS I | JCRAWFORD |  | 2017-05-19 10:11
1 | WTG-0031-NDGP-0000 | 1734405 | GEARBOX OIL, Particle counter removal | 2017-06-08 10:51 | Closed | GBXOIL | GBXPARTREM | STANTON | MSNOW |  | 2017-07-24 09:06
9 | WTG-0029-0000 | 1136567 | Oil Cooler Hose Leak | 2015-05-05 18:59 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2016-04-11 14:09
1 | WTG-0071-ND00-0000 | 1117705 | GEARBOX OIL, Fix oil leak | 2015-04-02 19:54 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | AMITCHELL |  | 2015-04-29 17:21
1 | WTG-0027-NDGP-0000 | 1139623 | Oil pump replacement, leaking | 2015-05-15 13:20 | Closed | GBXOIL | GBXOILLEAK | VANTAGE | PMASAKI |  | 2015-05-15 14:06
3 | WTG-0002-NDGP-0000 | 1160084 | GEARBOX OIL, Gearbox oil pump needs inversion (slight leak) | 2015-07-08 11:15 | Closed | GBXOIL | GBXOILCOOL | GRAND RIDGE | SSMITH |  | 2016-02-05 14:37
5 | WTG-0047-0000 | 1161776 | replace leaking rad | 2015-07-20 10:22 | Cancelled | GBXOIL | GBXOILCOOL | RALEIGH | KNOLAN |  | 2020-01-28 18:42
5 | WTG-0028-0000 | 1161778 | replace leaking rad | 2015-07-20 10:24 | Cancelled | GBXOIL | GBXOILCOOL | RALEIGH | KNOLAN |  | 2020-01-28 18:42
5 | WTG-0018-0000 | 1161806 | Replace Leaking Rad | 2015-07-20 12:07 | Cancelled | GBXOIL | GBXOILCOOL | RALEIGH | ARUDAKAS |  | 2020-01-28 18:42
1 | GBX-000029 | 1096512 | Replace oil pump motor | 2015-02-23 13:15 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JJUTILA |  | 2015-02-27 09:39
1 | WTG-0068-NDG0-0000 | 1191908 | GEARBOX OIL, Oil Sample | 2015-10-19 13:55 | Closed | GBXOIL | GBXOILSAMP | PRAIRIE BREEZE | LHINKLE |  | 2015-10-29 17:23
1 | WTG-0097-NDG0-0000 | 1191909 | GEARBOX OIL, Oil Sample | 2015-10-19 13:57 | Closed | GBXOIL | GBXOILSAMP | PRAIRIE BREEZE | LHINKLE |  | 2015-12-15 16:18
1 | WTG-0109-0000 | 1191985 | Pall filter housing leak | 2015-10-20 09:08 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2015-11-06 07:16
5 | GBX-000023 | 1177669 | Need to replace oil filter housing - Leaking down inside tower | 2015-09-01 12:56 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2016-05-11 15:41
1 | WTG-0037-NDG0-0000 | 1180805 | GEARBOX OIL, Oil Sample | 2015-09-11 08:14 | Closed | GBXOIL | GBXOILSAMP | FORWARD | ACARR |  | 2015-09-14 13:52
2 | WTG-0082-0000 | 1182198 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2015-09-23 06:58 | Closed | GBXOIL | GBXOILCOOL | BISHOP HILL | JBELLAVANCE |  | 2016-02-18 12:43
1 | WTG-0067-0000 | 1112792 | GEARBOX OIL, Fix oil leak | 2015-03-26 18:10 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2015-11-11 07:10
3 | WTG-0002-NDGP-0000 | 1640212 | GEARBOX OIL, Replace oil pump | 2016-12-08 19:12 | Cancelled | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2018-01-31 18:38
3 | WTG-0002-NDG0-0000 | 1640213 | GEARBOX OIL, Add/Top-Off | 2016-12-08 19:13 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2017-01-31 13:46
2 | WTG-0039-NDGP-0000 | 1640302 | Gearbox Oil Secondary Filter System Element Change | 2016-12-09 11:39 | Closed | GBXOIL | GBXFILTELEM | WOLVERINE CREEK | AMARTORANA | 1 | 2016-12-09 13:11
1 | WTG-0026-NDGP-0000 | 1135106 | GEARBOX OIL, Oil Sample | 2015-05-01 15:09 | Closed | GBXOIL | GBXOILSAMP | FORWARD | ACASPER |  | 2015-05-04 11:39
4 | WTG-0048-NDGP-0000 | 1230236 | GEARBOX OIL, Replace oil pump motor | 2016-01-10 16:21 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2016-02-17 10:33
1 | WTG-0022-0000 | 1161909 | GEARBOX OIL, Oil Sample - oil sample from yaw service | 2015-07-20 13:47 | Closed | GBXOIL | GBXOILSAMP | FORWARD | TALVARADO |  | 2015-07-23 10:05
9 | WTG-0058-NDB0-0000 | 1190459 | Tower Clean Up Needed - Nanjing Gearbox Oil leak from bottom bolt | 2015-10-12 08:59 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS |  | 2017-02-16 15:13
1 | WTG-0085-NDG0-0000 | 1200104 | Oil filter housing leak. | 2015-11-09 14:02 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CRWADE |  | 2016-02-25 09:58
2 | WTG-0008-NDGP-0000 | 964937 | WTG #8_Replace gearbox oil cooler | 2014-03-11 07:50 | Closed | GBXOIL |  | FORWARD | TALVARADO |  | 2015-11-17 12:16
1 | WTG-0079-0000 | 1262262 | GEARBOX OIL, Fix oil leak | 2016-04-20 15:12 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JJUTILA |  | 2016-04-21 06:11
1 | WTG-0061-NDGP-0000 | 1271078 | GEARBOX OIL, replace PAL filter housing | 2016-05-11 19:45 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CBUHRMAN |  | 2016-07-19 17:44
1 | BMEC-DT-008 | 1149030 | wtg-008 low oil level | 2015-06-08 16:59 | Closed | GBXOIL |  | BUFFALO MOUNT | CLAWSON |  | 2015-08-05 09:30
1 | WTG-0041-NDG0-0000 | 1152285 | In-House GearBox Oil Change Out | 2015-06-22 12:26 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | RIRVING |  | 2015-07-01 13:29
1 | WTG-0080-0000 | 1161123 | Pall filter housing leak | 2015-07-14 12:27 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2015-11-01 10:52
1 | WTG-0135-NDGP-0000 | 1182698 | Needs pump inversion | 2015-09-24 15:51 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE IV | JDISS |  | 2018-09-27 09:29
1 | WTG-0080-0000 | 1219069 | GEARBOX OIL, Fix oil leak | 2015-12-09 07:30 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | BCRUTCHFIELD |  | 2015-12-11 07:35
1 | WTG-0023-0000 | 1095685 | Pall Housing Change | 2015-02-18 13:30 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2015-02-23 14:23
2 | WTG-0022-NDG0-0000 | 1097360 | GEARBOX OIL, Oil Sample- Gearbox Express | 2015-02-25 10:37 | Closed | GBXOIL | GBXOILSAMP | MCADOO | LCOPELAND |  | 2015-02-25 14:28
1 | WTG-0115-NDG0-0000 | 1230758 | Drain and replace oil due to wrong type being put in | 2016-01-13 09:51 | Closed | GBXOIL | GBXOILCHG | SCEXP | STAYLOR |  | 2016-01-27 12:59
2 | WTG-0138-0000 | 1663196 | Pump inversion needed - not leaking | 2017-01-25 12:17 | Cancelled | GBXOIL | GBXOILCOOL | GRAND RIDGE IV | MFERRARO |  | 2023-06-29 13:12
5 | WTG-0071A-NDGP-0000 | 1108297 | WTG#71_gear oil pump leaking | 2015-03-16 08:07 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2015-03-30 14:03
4 | WTG-0095-NDGP-0000 | 1659815 | GEARBOX OIL, Replace oil cooler fan/motor/pump (do216 21A1 replacement) | 2017-01-16 18:47 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-03-31 13:45
1 | BMEC-DT-010 | 1154332 | WTG010 low oil pressure | 2015-06-29 15:00 | Closed | GBXOIL |  | BUFFALO MOUNT | CLAWSON |  | 2015-07-06 17:45
1 | WTG-0026-0000 | 1182680 | GEARBOX OIL, Oil Sample | 2015-09-24 14:54 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | SEVANS |  | 2015-09-30 14:54
1 | GBX-000034 | 1182718 | GEARBOX OIL, Fix oil leak | 2015-09-24 16:35 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | JCUMMINGS |  | 2016-03-15 13:47
1 | WTG-0034-0000 | 1182676 | GEARBOX OIL, Oil Sample | 2015-09-24 14:44 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | MBELCHER |  | 2015-09-30 14:54
1 | WTG-0022-0000 | 1182678 | GEARBOX OIL, Oil Sample | 2015-09-24 14:47 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | SEVANS |  | 2015-09-30 14:54
2 | WTG-0033-0000 | 1230840 | GEARBOX OIL, Add/Top-Off | 2016-01-13 16:22 | Closed | GBXOIL | GBXOILADD | BUCKEYE | CWADE |  | 2016-03-14 08:09
1 | WTG-0105-0000 | 1244184 | Replace Oil Cooler Inlet Hose | 2016-02-19 11:31 | Closed | GBXOIL | GBXOILCOOL | CAL RIDGE | BDAILY |  | 2016-02-22 07:52
2 | WTG-0039-NDG0-0000 | 1240463 | GEARBOX OIL, Add/Top-Off | 2016-02-08 15:07 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | RCARSON |  | 2016-02-17 12:49
9 | WTG-0071-0000 | 1259740 | Radiator Cooler Oil Leak Found - Nanjing | 2016-04-05 14:06 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ | 30 | 2018-02-07 15:13
1 | WTG-0048-0000 | 1283735 | GEARBOX OIL, Fix oil leak | 2016-06-21 15:26 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2016-06-27 12:42
2 | WTG-0116-NDG0-0000 | 1300507 | GEARBOX OIL, Particle counter installation | 2016-06-27 12:58 | Closed | GBXOIL | GBXPARTINS | GREXP | NFALASZ |  | 2016-10-19 07:11
2 | WTG-0106-NDG0-0000 | 1300508 | GEARBOX OIL, Particle counter installation | 2016-06-27 13:00 | Closed | GBXOIL | GBXPARTINS | GREXP | NFALASZ |  | 2016-11-03 10:15
1 | WTG-0054-0000 | 1588540 | GEARBOX OIL, clean oil out of belly | 2016-10-18 12:40 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | CAL RIDGE |  | 2018-04-02 15:09
1 | WTG-0054-0000 | 1588550 | GEARBOX OIL, gearbox filter housing leaking | 2016-10-18 12:44 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | CAL RIDGE |  | 2017-05-02 14:47
1 | WTG-0083-NDG0-0000 | 1666216 | Gearbox Oil Work/Issue | 2017-01-31 07:11 | Closed | GBXOIL | EM225 | RONCEVAUX | OGALLANT |  | 2017-02-21 17:22
2 | WTG-0028-0000 | 1671263 | Replace oil filter housing and Oil clean up | 2017-02-10 16:43 | Closed | GBXOIL | GBXOILCOOL | RATTLESNAKE 1 | JGASTON |  | 2017-06-29 15:50
1 | WTG-0049-0000 | 1703988 | GEARBOX OIL, Fix oil leak | 2017-05-02 15:50 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JJOHNSON |  | 2017-05-22 11:09
1 | WTG-0067-0000 | 1671916 | Leaking plug on Radiator | 2017-02-14 15:31 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2017-03-17 15:28
3 | WTG-0012-NDGP-0000 | 1671927 | GEARBOX OIL, Replace oil pump & invert | 2017-02-14 13:51 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2017-05-18 16:37
1 | WTG-0036-0000 | 1671958 | GEARBOX OIL, Fix oil leak | 2017-02-14 20:40 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | RATTLESNAKE |  | 2017-02-15 16:35
1 | GBX-000022 | 1672758 | Replace gear box thermal switch | 2017-02-08 12:08 | Closed | GBXOIL | GBXOILCOOL | ORANGEVILLE | ECOPELAND |  | 2017-02-20 09:35
2 | WTG-0024-0000 | 1822613 | Add Oil to Gearbox | 2017-12-07 16:30 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-10 09:49
9 | GBX-000057 | 1676318 | Add pre oil change detergant | 2017-02-25 12:23 | Closed | GBXOIL | GBXOILCHG | HIGH SHELDON | ECOPELAND |  | 2017-02-27 09:50
1 | WTG-0107-0000 | 1676806 | GEARBOX OIL, Fix oil leak | 2017-02-27 08:01 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KYARNOLD |  | 2017-02-28 07:50
1 | WTG-0116-0000 | 1680999 | GEARBOX OIL, Fix oil leak | 2017-03-02 14:01 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | DLANGDON |  | 2017-04-03 14:03
5 | WTG-0032-NDGP-0000 | 1682392 | GEARBOX OIL, (do216 21A1 replacement) | 2017-03-07 09:49 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2018-03-02 16:13
4 | WTG-0058-NDG0-0000 | 1684824 | Replace Band holding blue vent tube | 2017-03-17 15:32 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2017-03-24 12:24
1 | WTG-0053-0000 | 1690870 | GEARBOX OIL, Fix Leaking GBX Hose | 2017-04-04 08:21 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CSEIDER |  | 2017-04-05 12:24
1 | WTG-0011-0000 | 1692890 | Oil cooler leak at plug | 2017-04-05 08:53 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS |  | 2017-05-18 09:46
3 | WTG-0076-NDGP-0000 | 1694272 | GEARBOX OIL, Replace oil pump | 2017-04-10 14:39 | Cancelled | GBXOIL | GBXOILCOOL | JUDITH GAP | LHATVELDT |  | 2017-10-09 15:52
2 | WTG-0109-NDGP-0000 | 1694987 | Take Oil Sample of WTG 109 | 2017-04-12 16:23 | Closed | GBXOIL | GBXOILSAMP | RONCEVAUX | MCOURTNEY |  | 2017-04-18 09:09
1 | GBX-000111 | 1696523 | EM: Gearbox bearing overtemperature | 2017-04-19 11:05 | Closed | GBXOIL | EM98 | TURKEY TRACK | JBRILEY |  | 2017-04-20 09:55
2 | WTG-0021-NDG0-0000 | 1696653 | GEARBOX OIL, Add/Top-Off | 2017-04-19 17:49 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2017-04-26 14:30
2 | WTG-0103-0000 | 1698892 | GEARBOX OIL, Fix oil leak | 2017-04-25 18:12 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2017-06-29 15:54
9 | WTG-0034-0000 | 1699263 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2017-04-27 08:13 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH | 30 | 2017-05-01 10:06
1 | WTG-0029-0000 | 1700305 | GEARBOX OIL, Fix oil leak | 2017-04-28 14:37 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | ALUNA |  | 2017-04-30 13:27
1 | WTG-0054-0000 | 1703994 | GEARBOX OIL, Fix oil leak | 2017-05-02 15:56 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JJOHNSON |  | 2017-05-22 11:09
1 | WTG-0051-0000 | 1703992 | GEARBOX OIL, Fix oil leak | 2017-05-02 15:56 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JJOHNSON |  | 2017-05-22 11:09
1 | WTG-0077-0000 | 1705014 | Gearbox pump coupler needs replaced | 2017-05-03 11:56 | Cancelled | GBXOIL | GBXOILCOOL | CAL RIDGE | MWINGLER
1 | WTG-0077-0000 | 1705015 | GEARBOX OIL, Fix oil leak | 2017-05-03 11:57 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2017-06-14 10:19
1 | WTG-0135-0000 | 1705694 | GEARBOX OIL, Fix oil leak | 2017-05-04 15:42 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDEWEESE |  | 2017-05-22 11:09
2 | WTG-0055-NDGP-0000 | 1705691 | GEARBOX OIL, Fix oil leak | 2017-05-04 15:25 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDKEY |  | 2017-05-22 11:09
1 | WTG-0138-0000 | 1705697 | GEARBOX OIL, Fix oil leak | 2017-05-04 15:59 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDEWEESE |  | 2017-05-22 11:09
1 | WTG-0057-NDG0-0000 | 1707355 | GEARBOX OIL, Fix oil leak | 2017-05-11 13:00 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE2 |  | 2018-10-08 14:56
1 | WTG-0002-0000 | 1706850 | GEARBOX OIL, Fix oil leak | 2017-05-09 13:15 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDEWEESE |  | 2017-05-22 11:08
1 | WTG-0150-NDGP-0000 | 1706828 | GEARBOX OIL, Fix oil leak | 2017-05-09 11:54 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | BWHEELER |  | 2017-05-22 11:08
1 | WTG-0051-0000 | 1708349 | GEARBOX OIL, Fix oil leak | 2017-05-16 14:11 | Closed | GBXOIL | GBXOILLEAK | BISHOP HILL | BISHOP HILL |  | 2017-05-24 09:29
1 | WTG-0218-0000 | 1709198 | GEARBOX OIL, Fix oil leak, radiator hose | 2017-05-20 08:06 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2019-10-22 17:00
1 | WTG-0217-0000 | 1709197 | GEARBOX OIL, Fix oil leak, radiator hose | 2017-05-20 08:02 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2020-07-30 14:40
2 | WTG-0063-0000 | 1712878 | GearBox Oil Sample | 2017-05-31 08:38 | Closed | GBXOIL | GBXOILSAMP | BUCKEYE | TSHARP |  | 2017-06-21 10:27
1 | WTG-0026-NDGP-0000 | 1712880 | GEARBOX OIL, Secondary filter system element change | 2017-05-31 08:46 | Closed | GBXOIL | GBXFILTELEM | TURKEY TRACK | JBRILEY |  | 2017-10-06 10:37
1 | WTG-0080-0000 | 1716147 | GEARBOX OIL, Oil Sample | 2017-06-02 15:40 | Closed | GBXOIL | GBXOILSAMP | BETHEL | JVICTOR |  | 2017-07-19 08:03
2 | WTG-0072-NDGP-0000 | 1734391 | GEARBOX OIL, Particle counter removal | 2017-06-08 10:21 | Closed | GBXOIL | GBXPARTINS | JUDITH GAP | MSNOW |  | 2017-06-19 08:27
2 | WTG-0028-NDGP-0000 | 1734400 | GEARBOX OIL, Particle counter removal | 2017-06-08 10:45 | Closed | GBXOIL | GBXPARTINS | MCADOO | MSNOW |  | 2017-06-21 10:55
5 | WTG-0031-NDGP-0000 | 1734404 | GEARBOX OIL PARTICLE COUNTER Removal | 2017-06-08 10:50 | Closed | GBXOIL | GBXPARTREM | WOLVERINE CREEK | MSNOW |  | 2018-10-05 10:30
4.2 | WTG-0031-NDGP-0000 | 1740405 | Oil Filter Change With Yellow Dish | 2017-06-28 09:59 | Closed | GBXOIL |  | FORWARD | FORWARD |  | 2017-07-20 08:42
1 | WTG-0041-0000 | 1749665 | GEARBOX OIL, Fix oil leak | 2017-07-19 15:57 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DESPINOSA |  | 2017-07-19 21:55
2 | WTG-0073-0000 | 1750260 | GEARBOX OIL, Secondary filter system element change | 2017-07-21 14:17 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-07-24 14:59
2 | WTG-0066-0000 | 1750261 | GEARBOX OIL, Secondary filter system element change | 2017-07-21 14:18 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-07-24 14:59
1 | WTG-0097-0000 | 1752634 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2017-07-26 07:44 | Closed | GBXOIL | GBXOILCOOL | BISHOP HILL | BISHOP HILL |  | 2017-08-02 11:24
4.2 | WTG-0084-NDGP-0000 | 1752635 | Replace Heat Exchanger | 2017-07-26 07:57 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2017-11-16 07:13
1 | WTG-0036-0000 | 1752636 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2017-07-26 08:01 | Closed | GBXOIL | GBXOILCOOL | BISHOP HILL | NLARIMER |  | 2017-08-02 11:24
1 | WTG-0101-NDGP-0000 | 1765056 | GEARBOX OIL, Oil Sample | 2017-08-23 09:10 | Closed | GBXOIL | GBXOILSAMP | BUCKEYE | MSNOW |  | 2017-08-25 10:42
2 | WTG-0059-0000 | 1764957 | GEARBOX OIL, Secondary filter system element change | 2017-08-22 15:23 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-08-23 07:02
1 | WTG-0035-NDGP-0000 | 1765303 | GEARBOX OIL, Oil Sample | 2017-08-23 16:35 | Closed | GBXOIL | GBXOILSAMP | GRAND RIDGE | MSNOW |  | 2018-04-23 08:49
2 | WTG-0025-0000 | 1821856 | Add Oil to Gearbox | 2017-12-12 09:19 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:02
3 | WTG-0047-NDGP-0000 | 1737515 | finish oil pump inversion | 2017-06-20 15:51 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2018-08-07 12:44
1 | WTG-0038-NDG0-0000 | 1738790 | EM: Gear oil temperature switching contact | 2017-06-24 14:18 | Closed | GBXOIL | EM72 | GUNSIGHT | CHUBBARD |  | 2017-06-27 08:20
4 | WTG-0008-NDG0-0000 | 1740041 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:00 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-07-19 17:08
4 | WTG-0013-NDG0-0000 | 1740045 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:01 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-09-11 08:43
4 | WTG-0004-NDG0-0000 | 1740055 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:05 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-08-21 14:30
4 | WTG-0010-NDG0-0000 | 1740042 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:00 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2018-01-02 10:31
4 | WTG-0011-NDG0-0000 | 1740043 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:00 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-09-07 20:26
4 | WTG-0012-NDG0-0000 | 1740044 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:00 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-09-11 08:43
1 | WTG-0074-0000 | 1740266 | Replace Filter Housing | 2017-06-28 07:56 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2017-11-02 11:17
1 | WTG-0059-NDGP-0000 | 1741033 | EM: Gearbox oilpressure mechanical pump not OK | 2017-06-29 16:14 | Closed | GBXOIL | EM256 | BETHEL | CWADE |  | 2017-06-30 07:46
4 | WTG-0009-NDGP-0000 | 1746608 | GEARBOX OIL, Replace oil pump | 2017-07-07 13:33 | Closed | GBXOIL | GBXOILCOOL | FORWARD | CMITCHELL |  | 2017-07-11 11:26
1 | WTG-0111-0000 | 1748015 | GEARBOX OIL, Fix oil leak | 2017-07-13 10:55 | Closed | GBXOIL | GBXOILLEAK | BETHEL | BETHEL |  | 2017-07-19 08:02
1 | WTG-0084-NDGP-0000 | 1749209 | GEARBOX OIL, Replace oil pump | 2017-07-18 15:52 | Cancelled | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2018-11-14 16:50
1 | GBX-000059 | 1749222 | Gearbox hose replacement | 2017-07-18 17:10 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS |  | 2017-07-20 10:51
1 | WTG-0048-0000 | 1751316 | GEARBOX OIL, Fix oil leak | 2017-07-24 15:18 | Closed | GBXOIL | GBXOILLEAK | MCADOO | TRUDE |  | 2017-07-26 10:36
1 | WTG-0114-0000 | 1751325 | GEARBOX OIL, Oil Sample | 2017-07-24 15:59 | Closed | GBXOIL | GBXOILSAMP | SCEXP | SCEXP |  | 2017-09-08 12:20
1 | WTG-0019-NDG0-0000 | 1753484 | EM: Gearbox oil overtemperature | 2017-07-27 08:19 | Closed | GBXOIL | EM77 | WAKE 1 | BWHEELER |  | 2017-07-31 16:13
5 | WTG-0042-0000 | 1760016 | GEARBOX OIL, Check Nanjing replacement hose condition | 2017-08-11 14:03 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | AMAXWELL |  | 2017-12-05 07:20
5 | WTG-0050-0000 | 1760018 | GEARBOX OIL, Check Nanjing replacement hose condition | 2017-08-11 14:07 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | AMAXWELL |  | 2018-04-10 07:32
4.2 | WTG-0122-0000 | 1760067 | GEARBOX, Amsoil Change | 2017-08-11 14:36 | Closed | GBXOIL | GBXOILCHG | CAMP SPRINGS II | AMAXWELL |  | 2018-03-14 19:13
4.2 | WTG-0128-0000 | 1760068 | GEARBOX, Amsoil Change | 2017-08-11 14:37 | Closed | GBXOIL | GBXOILCHG | CAMP SPRINGS II | AMAXWELL |  | 2018-03-06 18:34
5 | WTG-0017-0000 | 1760101 | Oil cooler hose replacement | 2017-08-11 16:32 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH |  | 2017-08-18 11:59
4.2 | WTG-0148-0000 | 1760071 | GEARBOX, Amsoil Change | 2017-08-11 14:38 | Closed | GBXOIL | GBXOILCHG | CAMP SPRINGS II | AMAXWELL |  | 2018-04-10 19:26
4.2 | WTG-0156-0000 | 1760072 | GEARBOX, Amsoil Change | 2017-08-11 14:38 | Closed | GBXOIL | GBXOILCHG | CAMP SPRINGS II | AMAXWELL |  | 2018-04-18 19:14
4.2 | WTG-0163-0000 | 1760073 | GEARBOX, Amsoil Change | 2017-08-11 14:39 | Closed | GBXOIL | GBXOILCHG | CAMP SPRINGS II | AMAXWELL |  | 2018-04-13 08:53
4.2 | WTG-0149-0000 | 1760074 | GEARBOX, Amsoil Change | 2017-08-11 14:39 | Closed | GBXOIL | GBXOILCHG | CAMP SPRINGS II | AMAXWELL |  | 2018-04-12 11:46
4.2 | WTG-0178-0000 | 1760075 | GEARBOX, Amsoil Change | 2017-08-11 14:40 | Closed | GBXOIL | GBXOILCHG | CAMP SPRINGS II | AMAXWELL |  | 2018-04-12 11:45
2 | WTG-0126-0000 | 1760748 | GEARBOX OIL, Secondary filter system element change | 2017-08-15 10:28 | Closed | GBXOIL | GBXFILTELEM | BISHOP HILL | MBELCHER |  | 2017-09-28 09:38
2 | WTG-0124-0000 | 1760750 | GEARBOX OIL, Secondary filter system element change | 2017-08-15 12:23 | Closed | GBXOIL | GBXFILTELEM | BISHOP HILL | ARUSHING |  | 2017-09-28 09:38
2 | WTG-0125-0000 | 1760747 | GEARBOX OIL, Secondary filter system element change | 2017-08-15 09:31 | Closed | GBXOIL | GBXFILTELEM | BISHOP HILL | MBELCHER |  | 2017-09-28 09:38
2 | WTG-0127-0000 | 1760751 | GEARBOX OIL, Secondary filter system element change | 2017-08-15 12:24 | Closed | GBXOIL | GBXFILTELEM | BISHOP HILL | BISHOP HILL |  | 2017-09-28 09:38
2 | WTG-0067-0000 | 1763844 | GEARBOX OIL, Secondary filter system element change | 2017-08-18 11:50 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-08-21 07:17
2 | WTG-0068-0000 | 1763845 | GEARBOX OIL, Secondary filter system element change | 2017-08-18 11:51 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-08-21 07:17
2 | WTG-0069-0000 | 1763846 | GEARBOX OIL, Secondary filter system element change | 2017-08-18 11:52 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-08-21 07:17
2 | WTG-0085-NDGP-0000 | 1767355 | gearbox oil cooler leaking | 2017-08-30 16:20 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2018-11-01 11:42
2 | WTG-0091-NDGP-0000 | 1771079 | Replace secondary filtration system filter on gearbox oil | 2017-09-06 15:20 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GBOTT | 1 | 2017-09-07 06:56
1 | WTG-0073-0000 | 1771866 | GEARBOX OIL, Fix oil leak | 2017-09-07 15:02 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | NHEITHOFF
1 | WTG-0227-0000 | 1774144 | GEARBOX OIL, Fix oil leak | 2017-09-13 17:05 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | CHADDIX |  | 2017-09-18 17:27
2 | WTG-0086-0000 | 1774935 | GEARBOX OIL, Secondary filter system element change | 2017-09-15 14:33 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-09-18 07:41
2 | WTG-0087-0000 | 1774936 | GEARBOX OIL, Secondary filter system element change | 2017-09-15 14:33 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-09-18 07:41
2 | WTG-0088-0000 | 1774943 | GEARBOX OIL, Secondary filter system element change | 2017-09-15 14:43 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-09-18 07:41
1 | WTG-0080-NDG0-0000 | 1774993 | GEARBOX OIL, Fix oil leak | 2017-09-15 15:19 | Closed | GBXOIL | GBXOILLEAK | GREXP | JDISS |  | 2017-09-18 09:53
9 | WTG-0117-0000 | 1775017 | TERP GBX Oil Change | 2017-09-15 15:23 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE | AMELENGU | 1 | 2017-10-31 16:57
2 | WTG-0084-0000 | 1774932 | GEARBOX OIL, Secondary filter system element change | 2017-09-15 14:32 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-09-18 07:41
2 | WTG-0085-0000 | 1774933 | GEARBOX OIL, Secondary filter system element change | 2017-09-15 14:32 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-09-18 07:41
2 | WTG-0106-0000 | 1774934 | GEARBOX OIL, Secondary filter system element change | 2017-09-15 14:32 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-09-18 07:41
9 | WTG-0037-0000 | 1775007 | TERP GBX Oil Change | 2017-09-15 15:22 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE | AMELENGU | 1 | 2017-10-31 16:57
9 | WTG-0105-0000 | 1775015 | TERP GBX Oil Change | 2017-09-15 15:23 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE | AMELENGU | 1 | 2017-10-31 16:57
1 | WTG-0234-0000 | 1775528 | GEARBOX OIL, Fix oil leak | 2017-09-19 09:32 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | CBORER |  | 2017-09-22 16:35
1 | WTG-0108-0000 | 1779560 | GEARBOX OIL, Fix oil leak - bypass cap leaking | 2017-09-28 12:01 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2018-02-28 11:48
2 | WTG-0003-0000 | 1780381 | Inspect on next climb - Gearbox leak - See comments | 2017-09-29 16:00 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | JDWILLIAMS |  | 2019-08-14 16:55
1 | WTG-0H09-NDG0-0000 | 1784175 | GEARBOX OIL, Particle counter installation | 2017-10-05 11:14 | Closed | GBXOIL | GBXPARTINS | BEECH RIDGE | SCLARK |  | 2017-10-25 10:32
5 | WTG-0102-0000 | 1784179 | GEARBOX OIL, Particle counter installation | 2017-10-05 11:22 | Closed | GBXOIL | GBXPARTINS | CAMP SPRINGS II | AMAXWELL |  | 2018-05-11 13:03
5 | WTG-0040-NDGP-0000 | 1784174 | GEARBOX OIL, Particle counter installation | 2017-10-05 11:02 | Closed | GBXOIL | GBXPARTINS | VANTAGE | MSNOW |  | 2017-10-09 09:25
1 | WTG-0J06-NDG0-0000 | 1785623 | GEARBOX OIL, Particle counter installation | 2017-10-10 09:01 | Closed | GBXOIL | GBXPARTINS | HIGH SHELDON | SCLARK |  | 2017-10-12 09:16
2 | WTG-0025-NDGP-0000 | 1788642 | leaking secondary pump | 2017-10-19 15:57 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-10-26 15:35
2 | WTG-0C03-0000 | 1789591 | CT-320 Oil Samples | 2017-10-24 14:27 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2017-10-24 14:37
2 | WTG-0F03-0000 | 1789592 | CT-320 Oil Samples | 2017-10-24 14:27 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2017-10-24 14:52
2 | WTG-0K04-0000 | 1789593 | CT-320 Oil Samples | 2017-10-24 14:28 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2017-10-24 14:51
2 | WTG-0B01-0000 | 1789590 | CT-320 Oil Samples | 2017-10-24 14:26 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2017-10-24 14:35
2 | WTG-0081-NDGP-0000 | 1789975 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2017-10-25 10:08 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-10-26 15:38
4 | WTG-0006-NDG0-0000 | 1798156 | GEARBOX OIL, Add/Top-Off 5 gal | 2017-11-03 12:56 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2017-11-30 14:02
2 | WTG-0062-0000 | 1799453 | GEARBOX OIL, Add/Top-Off | 2017-11-08 16:49 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JFREEMAN |  | 2017-11-09 07:24
2 | WTG-0127-0000 | 1799452 | GEARBOX OIL, Add/Top-Off | 2017-11-08 15:54 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JFREEMAN |  | 2017-11-09 07:25
2 | WTG-0059-NDGP-0000 | 1801458 | Needs washer for secondary filter | 2017-11-16 08:15 | Closed | GBXOIL | GBXFILTELEM | GRAND RIDGE | MFERRARO |  | 2018-05-18 07:55
1 | WTG-0116-0000 | 1801339 | GEARBOX OIL, Fix oil leak | 2017-11-15 14:33 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BDIAZ
4 | WTG-0007-NDG0-0000 | 1802237 | GEARBOX OIL, Add/Top-Off (about 5 gallons) | 2017-11-21 08:30 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2017-11-27 09:36
5 | WTG-0091-NDGP-0000 | 1804364 | Secondary filter cut-out contactor installation | 2017-11-28 17:35 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | JUDITHGAP |  | 2018-04-19 11:10
1 | WTG-0096-NDGP-0000 | 1808980 | GEARBOX OIL, Replace oil cooler radiator | 2017-12-06 16:24 | Closed | GBXOIL | GBXOILCOOL | GREXP | GRAND RIDGE |  | 2018-02-14 10:57
2 | WTG-0011-0000 | 1809646 | Add Oil to Gearbox | 2017-12-09 08:30 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NSCHMEIDLER |  | 2017-12-20 10:33
2 | WTG-0022-0000 | 1809714 | Add Oil to Gearbox | 2017-12-10 07:03 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NSCHMEIDLER |  | 2017-12-20 10:32
2 | WTG-0017-0000 | 1809647 | Add Oil to Gearbox | 2017-12-09 08:30 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NSCHMEIDLER |  | 2017-12-20 10:33
2 | WTG-0036-0000 | 1814046 | Add Oil to Gearbox | 2017-12-19 15:38 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 09:40
2 | WTG-0032-0000 | 1814049 | Add Oil to Gearbox | 2017-12-13 15:42 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 09:39
2 | WTG-0044-0000 | 1814053 | Add Oil to Gearbox | 2017-12-13 15:46 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 09:37
2 | WTG-0037-0000 | 1814043 | Add Oil to Gearbox | 2017-12-19 15:37 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:55
2 | WTG-0026-0000 | 1814045 | Add Oil to Gearbox | 2017-12-19 15:38 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 09:41
2 | WTG-0048-0000 | 1814050 | Add Oil to Gearbox | 2017-12-13 15:42 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 09:39
2 | WTG-0052-0000 | 1814054 | Add Oil to Gearbox | 2017-12-14 15:47 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 09:37
2 | WTG-0054-0000 | 1814055 | Add Oil to Gearbox | 2017-12-14 15:47 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 09:32
2 | WTG-0058-0000 | 1814057 | Add Oil to Gearbox | 2017-12-14 15:48 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 09:20
5 | WTG-0060A-NDGP-0000 | 1814068 | GEARBOX OIL, Add/Top-Off 5gals needed | 2017-12-19 14:40 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2017-12-22 12:27
2 | WTG-0050-0000 | 1814052 | Add Oil to Gearbox | 2017-12-14 15:45 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 09:39
1 | WTG-0023-NDG0-0000 | 1814099 | GEARBOX OIL, Fix oil leak | 2017-12-20 06:50 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | BFETZNER |  | 2017-12-20 07:49
9 | WTG-0032-0000 | 1813789 | Oil change | 2017-12-18 13:55 | Closed | GBXOIL | GBXOILCHG | CAL RIDGE | JDALTON |  | 2017-12-19 11:27
1 | WTG-0205-NDGP-0000 | 1819819 | GEARBOX OIL, Replace motor | 2018-01-03 08:09 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2018-01-08 09:55
2 | WTG-0061-0000 | 1821621 | Add Oil to Gearbox | 2018-01-06 08:02 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-08 10:58
2 | WTG-0063-0000 | 1821623 | Add Oil to Gearbox | 2018-01-06 08:04 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-08 10:57
2 | WTG-0051-0000 | 1821851 | Add Oil to Gearbox | 2017-12-12 09:07 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:04
1 | WTG-0036-0000 | 1827680 | PALL Filter Housing Replacement | 2018-01-23 11:22 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2018-04-24 23:52
2 | WTG-0017-NDD0-0000 | 1840984 | Generator fan motor gen side replacement | 2018-02-19 14:50 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2018-04-13 14:09
4 | WTG-0039-NDG0-0000 | 1846920 | GEARBOX OIL, Add/Top-Off 5 gals | 2018-03-01 13:13 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2018-07-17 16:42
4 | WTG-0036-NDGP-0000 | 1851552 | Jensen Pump Leaking at the Pump | 2018-03-13 07:06 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2019-06-20 15:41
4 | WTG-0010-NDG0-0000 | 1852476 | GEARBOX OIL, Add/Top-Off | 2018-03-15 12:24 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2018-03-16 16:28
2 | WTG-0030-NDG0-0000 | 1856825 | GEARBOX OIL, Sample | 2018-03-29 10:00 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | MSNOW |  | 2018-09-10 17:54
1 | WTG-0037-ND00-0000 | 1862381 | Gearbox Oil Work/Issue | 2018-04-09 17:07 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 11:57
1 | WTG-0039-ND00-0000 | 1862382 | Gearbox Oil Work/Issue | 2018-04-09 17:07 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 11:57
1 | WTG-0057-ND00-0000 | 1862383 | Gearbox Oil Work/Issue | 2018-04-09 17:08 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 12:02
1 | WTG-0059-ND00-0000 | 1862384 | Gearbox Oil Work/Issue | 2018-04-09 17:09 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 12:02
1 | WTG-0060-ND00-0000 | 1862385 | Gearbox Oil Work/Issue | 2018-04-09 17:09 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 12:04
1 | WTG-0006-ND00-0000 | 1863005 | Gearbox Oil Work/Issue | 2018-04-12 16:20 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TMORRIS |  | 2018-07-20 11:48
1 | WTG-0106-ND00-0000 | 1862833 | Gearbox Oil Work/ Issue | 2018-04-11 15:30 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | AVILLARREAL |  | 2018-07-25 10:16
1 | WTG-0101-ND00-0000 | 1863080 | Gearbox Oil Work/ Issue | 2018-04-13 08:47 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BSHOOK
4.2 | WTG-0093-NDGP-0000 | 1862700 | Replace oil cooler duct | 2018-04-11 07:52 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCAPEN |  | 2018-04-23 06:53
1 | WTG-0060-NDGP-0000 | 1863844 | Oil Pump Replacement | 2018-04-16 15:56 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2018-04-16 16:23
1 | WTG-0024-0000 | 1863846 | GEARBOX OIL, Fix oil leak | 2018-04-16 14:41 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BDIAZ |  | 2018-04-23 09:07
4 | WTG-0062-NDG0-0000 | 1872807 | GEARBOX OIL, Secondary filter system installation | 2018-05-07 17:50 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | DKEETON |  | 2018-05-31 15:04
1 | WTG-0047-NDG0-0000 | 1875073 | GEARBOX OIL, Oil Sample | 2018-05-16 16:32 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | SCLARK |  | 2018-05-25 09:57
2 | WTG-0056-0000 | 1878792 | GEARBOX OIL, Fix oil leak-Replace Filter Housing | 2018-05-30 17:05 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE3 |  | 2018-06-01 09:59
1 | WTG-0003-0000 | 1892747 | GEARBOX OIL, Fix oil leak | 2018-06-12 15:45 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CHADDIX |  | 2018-07-24 16:53
1 | WTG-0154-NDGP-0000 | 1892827 | GEARBOX OIL, Particle counter troubleshooting | 2018-06-13 09:59 | Closed | GBXOIL | GBXPARTINS | CAMP SPRINGS II | MSNOW |  | 2018-12-17 16:37
5 | WTG-0043-NDG0-0000 | 1893580 | GEARBOX OIL, Add/Top-Off Needs 2 to 3 Gals. | 2018-06-15 10:59 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2018-06-22 13:25
1 | WTG-0152-NDGP-0000 | 1895185 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2018-06-22 11:11 | Closed | GBXOIL | GBXOILCOOL | CAMP SPRINGS II | JCRAWFORD |  | 2018-06-26 08:56
1 | WTG-0059-0000 | 1895261 | GEARBOX OIL, Fix oil leak | 2018-06-22 14:15 | Closed | GBXOIL | GBXOILLEAK | BETHEL | AGALARZA |  | 2018-06-25 09:27
1 | WTG-0052-0000 | 1916202 | rFSA claim for Gearbox front seal | 2018-01-25 16:53 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | RBABIK |  | 2018-07-30 14:35
1 | WTG-0213-NDGP-0000 | 1916957 | GEARBOX OIL, Fix oil leak | 2018-06-28 09:22 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SCEXP |  | 2019-04-18 17:31
5 | WTG-0033-0000 | 1922037 | GEARBOX OIL, Add 5 Gal | 2018-07-06 13:45 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2019-01-07 11:44
5 | WTG-0059-NDGP-0000 | 1922059 | Oil Pump Replacement | 2018-07-06 14:03 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2018-11-16 16:22
4 | WTG-0056A-0000 | 1925881 | Gearbox needs new desiccant | 2018-07-18 13:49 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2018-08-15 16:54
9 | WTG-0024-0000 | 1925753 | GEARBOX, Oil Change | 2018-07-18 10:19 | Closed | GBXOIL | GBXOILCHG | GOLDTHWAITE | GOLDTHWAITE |  | 2018-07-18 10:22
5 | WTG-0032-NDG0-0000 | 1925723 | Replace cooler hoses | 2018-07-18 07:36 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2021-03-25 07:00
4 | GBX-737000003999 | 1926775 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
2 | WTG-0026-0000 | 1821859 | Add Oil to Gearbox | 2017-12-12 09:22 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:01
4 | WTG-0087-NDG0-0000 | 1826757 | GEARBOX OIL, Add/Top-Off 5 gallons | 2018-01-19 15:28 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2018-05-30 09:30
1 | WTG-0034-0000 | 1827498 | Leak from Thermal Bypass Cap | 2018-01-22 12:33 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2018-03-14 08:49
5 | WTG-0019-N000-0000 | 1831338 | Secondary filter cut-out contactor installation | 2018-01-25 17:16 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | JUDITHGAP |  | 2018-03-16 14:46
1 | WTG-0008-TDTA-0000 | 1831332 | Leaking Oil Pump | 2018-01-25 16:38 | Closed | GBXOIL | GBXOILLEAK | VANTAGE | VANTAGE |  | 2018-01-26 10:37
1 | WTG-0076-NDGP-0000 | 1834228 | Secodary oil filter leaking | 2018-01-31 12:21 | Closed | GBXOIL | GBXFILTINS | GREXP | MFERRARO |  | 2018-06-07 10:29
1 | WTG-0096-0000 | 1838623 | GEARBOX OIL, Fix oil leak | 2018-02-07 14:20 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | BDAILY |  | 2018-02-12 21:03
4 | WTG-0024-NDG0-0000 | 1839154 | GEARBOX OIL, Add/ 5 gals. | 2018-02-09 19:26 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2018-06-18 12:56
2 | WTG-0046-NDG0-0000 | 1840566 | GEARBOX OIL, Oil Sample | 2018-02-16 12:37 | Closed | GBXOIL | GBXOILSAMP | FORWARD | SCLARK |  | 2018-02-26 16:16
2 | WTG-0037-NDG0-0000 | 1841382 | GEARBOX OIL, Particle counter troubleshooting | 2018-02-20 11:34 | Closed | GBXOIL | GBXPARTINS | FORWARD | SCLARK |  | 2018-03-15 09:14
2 | WTG-0J06-NDG0-0000 | 1846135 | GEARBOX OIL, Particle counter troubleshooting | 2018-02-28 14:14 | Cancelled | GBXOIL | GBXPARTINS | HIGH SHELDON | SCLARK |  | 2018-07-19 12:04
2 | WTG-0040-NDGP-0000 | 1846141 | GEARBOX OIL, Particle counter troubleshooting | 2018-02-28 14:29 | Closed | GBXOIL | GBXPARTINS | VANTAGE | MSNOW |  | 2018-07-13 13:00
1 | WTG-0061-0000 | 1847070 | GEARBOX OIL, Fix oil leak-Replace Pump to Cooler Inlet Hose | 2018-03-01 15:31 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | NHEITHOFF |  | 2018-06-20 16:05
1 | WTG-0008-0000 | 1847076 | GEARBOX OIL, Fix oil leak | 2018-03-01 12:46 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | JSTAHLECKER |  | 2019-02-08 18:10
2 | WTG-0046-NDGP-0000 | 1850049 | GEARBOX OIL, Secondary filter system element change | 2018-03-06 09:57 | Closed | GBXOIL | GBXFILTELEM | FORWARD | MSNOW |  | 2018-03-16 16:20
3 | SITE-RSW1 | 1851562 | GEARBOX OIL, Oil Sample | 2018-03-13 09:07 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | CPRUIT |  | 2018-03-20 11:29
5 | WTG-0071A-NDGP-0000 | 1851509 | Oil Cooler vent | 2018-03-12 16:54 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2018-03-28 15:20
9 | WTG-0205-NDG0-0000 | 1851507 | GEARBOX OIL, Fix oil leak | 2018-03-12 16:29 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN
1 | WTG-0017-0000 | 1852404 | EM:Gearbox Oil Leak | 2018-03-15 09:29 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | TBRAUN |  | 2019-02-22 17:21
1 | WTG-0107-0000 | 1852448 | GEARBOX OIL, Fix oil leak | 2018-03-15 13:07 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | TURKEY TRACK |  | 2018-12-11 22:57
2 | WTG-0015-NDG0-0000 | 1856807 | GEARBOX OIL, Add/Top-Off | 2018-03-29 09:37 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | MSNOW |  | 2018-05-28 19:53
2 | WTG-0036-NDG0-0000 | 1856815 | GEARBOX OIL, Add/Top-Off | 2018-03-29 09:51 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | MSNOW |  | 2018-04-24 22:50
2 | WTG-039E-NDG0-0000 | 1856818 | GEARBOX OIL, Add/Top-Off | 2018-03-29 09:53 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | MSNOW |  | 2018-04-18 16:48
2 | WTG-0077-NDG0-0000 | 1856820 | GEARBOX OIL, Sample | 2018-03-29 09:56 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | MSNOW |  | 2018-11-02 16:29
2 | WTG-0036-NDG0-0000 | 1856824 | GEARBOX OIL, Sample | 2018-03-29 10:00 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | MSNOW |  | 2018-09-10 17:56
2 | WTG-0023-NDG0-0000 | 1856826 | GEARBOX OIL, Sample | 2018-03-29 10:01 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | MSNOW |  | 2018-07-17 16:23
2 | WTG-0021-NDG0-0000 | 1856811 | GEARBOX OIL, Add/Top-Off | 2018-03-29 09:46 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | MSNOW |  | 2018-05-17 17:07
1 | WTG-0061-ND00-0000 | 1862386 | Gearbox Oil Work/Issue | 2018-04-09 17:10 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 12:09
1 | WTG-0022-ND00-0000 | 1862389 | Gearbox Oil Work/Issue | 2018-04-09 17:11 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 11:54
1 | WTG-0028-ND00-0000 | 1862393 | Gearbox Oil Work/Issue | 2018-04-09 17:13 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 11:56
9 | WTG-0038-NDG0-0000 | 1862399 | replace rotor side gearbox seal | 2018-04-09 17:35 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JUDITHGAP |  | 2019-06-11 13:49
1 | WTG-0016-0000 | 1862866 | Gearbox Oil Work/Issue | 2018-04-11 17:36 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TMORRIS |  | 2018-07-20 11:50
1 | WTG-0049-0000 | 1862983 | Gearbox Oil Work/Issue | 2018-04-09 15:40 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2018-07-20 12:00
1 | WTG-0116-NDG0-0000 | 1862823 | Gearbox Oil Work/Issue | 2018-04-11 15:26 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | FHUBBARD |  | 2018-07-20 12:40
1 | WTG-0110-ND00-0000 | 1862839 | Gearbox Oil Work/Issue | 2018-04-11 16:20 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | AVILLARREAL |  | 2018-07-20 12:38
1 | WTG-0083-ND00-0000 | 1862889 | Gearbox Oil Work/Issue | 2018-04-11 18:30 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TCARD |  | 2018-04-12 16:42
1 | WTG-0112-ND00-0000 | 1862755 | Gearbox Oil Work/Issue | 2018-04-11 12:33 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | AVILLARREAL |  | 2018-07-20 12:39
4.2 | WTG-0093-NDGP-0000 | 1862763 | Replace oil cooler duct | 2018-04-11 07:52 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCAPEN |  | 2018-04-13 06:49
1 | WTG-0111-ND00-0000 | 1862959 | Gearbox Oil Work/Issue | 2018-04-12 14:27 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BSHOOK |  | 2018-07-20 12:39
1 | WTG-0050-0000 | 1862985 | Gearbox Oil Work/Issue | 2018-04-12 15:43 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2018-07-20 12:01
1 | WTG-0069-0000 | 1864819 | GEARBOX OIL, Fix oil leak - outlet hose fitting | 2018-04-19 16:58 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE2 |  | 2019-05-31 16:10
5 | WTG-0001-NDG0-0000 | 1867126 | GEARBOX OIL, Add 5 Gallons (Amsoil) | 2018-04-26 11:59 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2018-10-12 13:19
1 | WTG-0106-NDGP-0000 | 1892826 | GEARBOX OIL, Particle counter troubleshooting | 2018-06-13 09:57 | Closed | GBXOIL | GBXPARTINS | CAMP SPRINGS II | MSNOW |  | 2018-10-31 07:57
9 | WTG-0094-NDG0-0000 | 1892816 | Replace rotor side gearbox seal | 2018-06-12 17:23 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | RCARSON |  | 2019-06-11 13:48
1 | WTG-0105-NDGP-0000 | 1917987 | gearbox pressure error | 2018-06-29 14:19 | Closed | GBXOIL |  | RONCEVAUX | RONCEVAUX |  | 2018-07-04 15:09
2 | 013D101 | 1921751 | Cooling tower gearcase 1,7 | 2018-07-06 07:48 | Closed | GBXOIL |  | NELSON | RWEIDEL |  | 2018-07-13 14:58
5 | WTG-0058-NDGP-0000 | 1923954 | Oil Pump Replacement | 2018-07-12 15:54 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2018-11-15 11:19
5 | WTG-0043-NDGP-0000 | 1923955 | Oil Pump Replacement | 2018-07-12 15:55 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2018-07-13 09:29
4 | GBX-FDMD-4144 | 1926756 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000802 | 1926757 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000761 | 1926758 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004074 | 1926759 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000907 | 1926760 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004065 | 1926761 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004023 | 1926762 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004031 | 1926763 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004059 | 1926764 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000789 | 1926765 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004067 | 1926766 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004054 | 1926767 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004005 | 1926768 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000835 | 1926769 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000837 | 1926770 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000701 | 1926771 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-FDMD-4026 | 1926772 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-JKD-W-0000747 | 1926773 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004076 | 1926774 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004010 | 1926776 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004039 | 1926777 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004028 | 1926778 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
4 | GBX-737000004085 | 1926779 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
1 | WTG-0053-0000 | 2174471 | rFSA Claim: Leaking pitch tube seals | 2020-01-17 15:14 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-22 11:30
4 | WTG-0081-NDGP-0000 | 1937976 | GEARBOX OIL, Catch tray cracked | 2018-08-16 15:11 | Closed | GBXOIL | GBXFILTELEM | FORWARD | FORWARD |  | 2018-12-18 13:17
5 | WTG-0031-0000 | 1953694 | GEARBOX OIL, Oil Sample | 2018-09-27 13:53 | Closed | GBXOIL | GBXOILSAMP | BUCKEYE | DNEWSOME |  | 2018-10-05 10:01
1 | WTG-0017-0000 | 1953678 | GEARBOX OIL, Fix oil leak | 2018-09-27 12:45 | Closed | GBXOIL | GBXOILLEAK | BETHEL | ACHAVIRA |  | 2018-09-30 08:20
1 | WTG-0035-0000 | 1954096 | GEARBOX OIL, Replace leaking hose from filter to cooler | 2018-09-28 13:24 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TCARD
1 | WTG-0084-0000 | 1958486 | GEARBOX OIL, Fix oil leak | 2018-10-05 15:51 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CWERNER |  | 2018-12-20 08:08
2 | WTG-0028-NDGP-0000 | 1959195 | Oil cooler leaking | 2018-10-08 14:49 | Closed | GBXOIL | GBXOILCOOL | FORWARD | ACASPER |  | 2023-09-11 11:34
1 | GBX-000077 | 1959353 | GEARBOX OIL, Fix oil leak | 2018-10-09 08:00 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | JFERRIS |  | 2018-11-27 16:49
1 | WCEC | 1961608 | Obtain Oil Samples | 2018-10-17 14:49 | Closed | GBXOIL | GBXOILSAMP | WOLVERINE CREEK | WOLVERINECREEK |  | 2018-10-17 16:30
1 | WTG-0128-0000 | 1962441 | GEARBOX OIL, Oil Sample | 2018-10-22 09:02 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | BISHOP HILL |  | 2018-10-30 11:49
1 | WTG-0106-0000 | 1981964 | Fix oil leak | 2018-11-06 17:43 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | SOSTERLOH
2 | WTG-0060-0000 | 1983446 | GEARBOX OIL, Add/Top-Off | 2018-11-14 09:26 | Closed | GBXOIL | GBXOILADD | BETHEL | AGALARZA |  | 2018-11-15 10:51
2 | WTG-0009-NDGP-0000 | 1989215 | GEARBOX OIL, Secondary filter system element change | 2018-11-30 11:56 | Closed | GBXOIL | GBXFILTELEM | FORWARD | SCLARK |  | 2019-01-10 16:07
5 | WTG-0014-0000 | 2006774 | GBX oil pump Making noise on NDE | 2018-12-28 12:21 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | MSTONER |  | 2019-10-28 14:58
4 | WTG-0210A-NDG0-0000 | 2009911 | GEARBOX OIL, Add/Top-Off | 2019-01-03 10:53 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2019-04-05 15:07
4 | GBX-737000004073 | 2011848 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004074 | 2011849 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004075 | 2011850 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004076 | 2011851 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-FDMD-4112 | 2011872 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-FDMD-4142 | 2011873 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-FDMD-4144 | 2011874 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-FDMD-4155 | 2011875 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000669 | 2011876 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000670 | 2011877 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000672 | 2011878 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000685 | 2011879 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
1 | WTG-0099-NDGP-0000 | 2012097 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2019-01-07 07:07 | Closed | GBXOIL | GBXOILCOOL | RONCEVAUX | RONCEVAUX |  | 2019-01-07 07:30
4 | GBX-JKD-W-0000895 | 2011916 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | WTG-0004-NDG0-0000 | 1927704 | GEARBOX OIL, Add 5 gal | 2018-07-25 12:11 | Closed | GBXOIL | GBXOILADD | FORWARD | CMITCHELL |  | 2018-12-07 10:31
1 | WTG-0011-0000 | 1929195 | Replace Oil Hose on Gearbox | 2018-07-27 11:49 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2018-09-05 16:59
1 | WTG-0098-0000 | 1929208 | GEARBOX OIL, Fix oil leak | 2018-07-27 12:21 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2018-08-22 07:35
1 | WTG-0082-0000 | 1933474 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2018-07-31 09:26 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | KMCLELAND |  | 2018-08-06 14:44
1 | WTG-0068-NDGP-0000 | 1934545 | Install secondary filtration system on gearbox oil | 2018-08-08 12:25 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2018-10-23 14:08
1 | WTG-0072-NDGP-0000 | 1934550 | Install secondary filtration system on gearbox oil | 2018-08-08 12:27 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2018-09-13 17:19
3 | WTG-0032-NDG0-0000 | 1942756 | GEARBOX OIL, Particle counter installation | 2018-08-29 14:44 | Closed | GBXOIL | GBXPARTINS | MCADOO | RPPATEL |  | 2018-09-25 18:29
1 | WTG-0028-NDGP-0000 | 1947405 | GEARBOX OIL, Particle counter installation | 2018-09-06 16:50 | Closed | GBXOIL | GBXPARTINS | STANTON | RPPATEL |  | 2019-04-05 14:53
1 | WTG-0031-NDGP-0000 | 1947424 | GEARBOX OIL, Particle counter installation | 2018-09-06 17:41 | Closed | GBXOIL | GBXPARTINS | STANTON | RPPATEL |  | 2019-01-25 07:50
1 | WTG-0063-0000 | 1950343 | GEARBOX OIL, Fix oil leak | 2018-09-18 10:10 | Closed | GBXOIL | GBXOILLEAK | BETHEL | CWADE |  | 2018-09-20 16:18
1 | WTG-0064-0000 | 1960149 | rFSA Claim- Radiator Replacement | 2018-10-11 16:59 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2019-04-05 08:06
1 | WTG-0083-0000 | 1961821 | GEARBOX OIL, Fix oil leak | 2018-10-18 17:19 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE
5 | WTG-0017-0000 | 1962918 | Add 5 gal of Amsoil | 2018-10-22 14:24 | Closed | GBXOIL | GBXOILADD | FORWARD | JJENSEMA |  | 2019-01-07 11:46
4.2 | WTG-0019A-NDGP-0000 | 1962978 | GEARBOX OIL, Replace oil cooler | 2018-10-23 07:09 | Cancelled | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2022-04-08 09:17
1 | WTG-0053-NDG0-0000 | 1968388 | Replace GB Front Seal | 2018-11-01 11:48 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | RTRITES |  | 2018-11-02 07:47
3 | WTG-0012-NDGP-0000 | 1983474 | Gearbox oil sample | 2018-11-14 10:47 | Closed | GBXOIL | GBXOILSAMP | FORWARD | KLEFFELMAN |  | 2018-11-16 14:32
2 | WTG-0031-0000 | 1983538 | GEARBOX OIL, Add/Top-Off | 2018-11-14 13:14 | Closed | GBXOIL | GBXOILADD | BETHEL | AGALARZA |  | 2018-11-15 10:51
2 | WTG-0102-0000 | 1983539 | GEARBOX OIL, Add/Top-Off | 2018-11-14 14:09 | Closed | GBXOIL | GBXOILADD | BETHEL | AGALARZA |  | 2018-11-15 10:50
1 | WTG-0G10-NDG0-0000 | 1988468 | GEARBOX OIL, Particle counter troubleshooting | 2018-11-28 11:09 | Closed | GBXOIL | GBXPARTINS | BEECH RIDGE | MSNOW |  | 2019-11-05 15:35
4 | GBX-737000003942 | 2011808 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000003947 | 2011809 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000003964 | 2011810 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000003966 | 2011811 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
1 | WTG-0154-NDG0-0000 | 2002881 | GEARBOX OIL, Particle counter installation | 2018-12-17 16:39 | Cancelled | GBXOIL | GBXPARTINS | CAMP SPRINGS II | CAMP SPRINGS |  | 2023-08-03 12:45
4 | GBX-JKD-W-0000690 | 2011880 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000691 | 2011881 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000692 | 2011882 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000699 | 2011883 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000701 | 2011884 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000702 | 2011885 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000704 | 2011886 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000707 | 2011887 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000708 | 2011888 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000770 | 2011900 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000785 | 2011901 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000786 | 2011902 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000789 | 2011903 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000802 | 2011904 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000809 | 2011905 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000816 | 2011906 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000817 | 2011907 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000818 | 2011908 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000830 | 2011909 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000835 | 2011910 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000836 | 2011911 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000838 | 2011912 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000844 | 2011913 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000866 | 2011914 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000875 | 2011915 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000907 | 2011917 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000932 | 2011918 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000999 | 2011919 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
1 | WTG-0076-0000 | 2016084 | GEARBOX OIL, Fix oil leak | 2019-01-09 11:56 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JTHOMAS |  | 2019-01-10 07:39
4 | WTG-0097-0000 | 2015866 | GEARBOX OIL, Add/Top-Off 5 gallons | 2019-01-08 09:03 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-01-10 16:39
4 | WTG-0086-NDG0-0000 | 2019584 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
1 | WTG-0177-0000 | 2017606 | Ladder Clearance Decal Installation | 2019-01-10 13:04 | Closed | GBXOIL |  | CAMP SPRINGS II | NCLOYD | 30 | 2019-10-18 08:52
4 | WTG-0082-NDG0-0000 | 2019580 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0083-NDG0-0000 | 2019581 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0084-NDG0-0000 | 2019582 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0085-NDG0-0000 | 2019583 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0087-NDG0-0000 | 2019585 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0088-NDG0-0000 | 2019586 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0092-NDG0-0000 | 2019590 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0089-NDG0-0000 | 2019587 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0090-NDG0-0000 | 2019588 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0091-NDG0-0000 | 2019589 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0010-NDG0-0000 | 2019508 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0011-NDG0-0000 | 2019509 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0003-NDG0-0000 | 2019501 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
1 | WTG-0023-NDG0-0000 | 2019497 | GEARBOX OIL, HSS Seal Repair | 2019-01-10 13:22 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MMCCABE |  | 2019-05-22 15:23
4 | WTG-0001-NDG0-0000 | 2019499 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0002-NDG0-0000 | 2019500 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0004-NDG0-0000 | 2019502 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0005-NDG0-0000 | 2019503 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0006-NDG0-0000 | 2019504 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0046-NDG0-0000 | 2019544 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0007-NDG0-0000 | 2019505 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0008-NDG0-0000 | 2019506 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0009-NDG0-0000 | 2019507 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0047-NDG0-0000 | 2019545 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0048-NDG0-0000 | 2019546 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0049-NDG0-0000 | 2019547 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
9 | WTG-0231-0000 | 2022764 | GEARBOX, Oil Change & Tower Cleaning | 2019-01-16 14:46 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | CBORER |  | 2019-09-13 17:15
1 | WTG-0102-0000 | 2024790 | GEARBOX OIL, Particle counter REMOVE | 2019-01-22 16:47 | Closed | GBXOIL | GBXPARTREM | CAMP SPRINGS II | RPPATEL |  | 2021-12-20 07:29
4 | GBX-000007 | 2027422 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | WTG-0090-NDG0-0000 | 2025394 | 5 gallons oil needed | 2019-01-24 14:14 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2019-06-17 16:14
4 | GBX-000001 | 2027416 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000002 | 2027417 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000003 | 2027418 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000004 | 2027419 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000005 | 2027420 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000006 | 2027421 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000037 | 2027453 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000032 | 2027448 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000033 | 2027449 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000034 | 2027450 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000035 | 2027451 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000036 | 2027452 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000038 | 2027454 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000039 | 2027455 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000040 | 2027456 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000041 | 2027457 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000042 | 2027458 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
1 | WTG-0085-0000 | 2029130 | rFSA Claim: Leaking pitch tube seals | 2019-01-31 15:03 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-22 11:08
5 | WTG-003W-0000 | 2035871 | Oil pump motor coupling | 2019-02-12 19:25 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | GOLDTHWAITE |  | 2019-08-02 11:28
1 | WTG-0127-NDGP-0000 | 2039222 | Inversion needed | 2019-02-21 16:34 | Closed | GBXOIL | GBXOILCOOL | GREXP | GRAND RIDGE |  | 2019-04-04 09:54
1 | WTG-0208-0000 | 2039929 | GEARBOX OIL, Fix oil leak | 2019-02-25 08:42 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE |  | 2019-07-12 15:41
4 | WTG-0036-NDG0-0000 | 2051367 | GEARBOX OIL, Add/Top-Off 5 Gallons Amsoil | 2019-03-11 14:30 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2019-06-20 15:45
1 | WTG-0016-0000 | 2055889 | 2019 Padmount Oil Sample | 2019-03-27 15:33 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2021-09-16 10:18
1 | WTG-0060-0000 | 2055907 | GEARBOX OIL, Fix oil leak | 2019-03-27 15:50 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CWERNER
1 | WTG-0060-0000 | 2057218 | GEARBOX OIL, Fix oil leak | 2019-03-29 16:03 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | SMILLER |  | 2019-04-02 07:23
3 | WTG-0041-NDG0-0000 | 2059870 | Gearbox running too hot | 2019-04-02 08:23 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-04-16 12:04
3 | WTG-0096-NDG0-0000 | 2065925 | Gearbox running too hot | 2019-04-18 08:21 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-06-05 07:59
2 | WTG-0078-0000 | 2065836 | GEARBOX OIL, Fix oil leak | 2019-04-17 14:30 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | NHEITHOFF
1 | WTG-0051-0000 | 2068309 | GEARBOX OIL, Fix oil leak | 2019-04-25 08:18 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CWERNER
4 | WTG-0210A-0000 | 2170125 | Top off oil | 2020-01-03 14:46 | Closed | GBXOIL | GBXOILADD | FORWARD | JJENSEMA |  | 2020-01-06 16:22
5 | WTG-0065-NDGP-0000 | 2074681 | GEARBOX OIL, Pump coupler | 2019-05-07 08:44 | Closed | GBXOIL | GBXOILCOOL | FORWARD | MPEARSON |  | 2019-05-29 11:49
1 | GBX-000031 | 2076581 | GEARBOX OIL, Fix oil leak | 2019-05-13 14:43 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JUDITHGAP |  | 2019-05-14 08:10
1 | WTG-0073-0000 | 2080635 | Replace Oil Cooler Motor | 2019-05-30 08:38 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE |  | 2019-06-12 15:48
1 | WTG-0103-0000 | 2092458 | GEARBOX OIL, Replace jensen oil filter motor | 2019-06-12 16:13 | Cancelled | GBXOIL | GBXOILCOOL | PRAIRIE BREEZE | AHOFFMANN
1 | WTG-0096-0000 | 2092489 | GEARBOX OIL, Replace oil cooler fan motor | 2019-06-12 17:33 | Closed | GBXOIL | GBXOILCOOL | PRAIRIE BREEZE | CWERNER |  | 2019-06-28 14:04
2 | WTG-0024-NDGP-0000 | 2096396 | GBX oil pump/spider gear replacement | 2019-06-26 15:10 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2019-06-27 09:36
4 | WTG-0213-NDG0-0000 | 2097803 | GEARBOX OIL, Add/Top-Off +5gals | 2019-06-28 14:02 | Closed | GBXOIL | GBXOILADD | FORWARD | MPEARSON |  | 2019-08-28 15:10
1 | WTG-0010-0000 | 2101772 | WTG010 - Oil Leak In Hub | 2019-07-05 16:35 | Closed | GBXOIL |  | BUFFALO MOUNT | CRO EAST |  | 2019-09-30 09:25
1 | WTG-0053-NDGP-0000 | 2105234 | GEARBOX OIL, Replace oil cooler | 2019-07-23 08:22 | Closed | GBXOIL | GBXOILCOOL | CAMP SPRINGS I | CMORRIS |  | 2022-03-16 08:18
1 | WTG-0202-NDG0-0000 | 2105414 | GEARBOX OIL, Fix oil leak-Inlet Hose leaking | 2019-07-23 18:52 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE |  | 2019-11-11 15:33
1 | WTG-0213-0000 | 2109356 | GEARBOX OIL, Fix oil leak | 2019-08-01 07:58 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | RKUDERA |  | 2019-09-13 17:15
4 | WTG-0082-NDG0-0000 | 2109881 | Catch tray for front gear oil leak. | 2019-08-01 16:04 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2021-07-20 06:33
1 | WTG-0315-0000 | 2109937 | GEARBOX OIL, Fix oil leak | 2019-08-01 17:11 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | AHOFFMANN |  | 2020-02-17 14:53
5 | WTG-0001-NDG0-0000 | 2111306 | 5 gallons oil needed | 2019-08-05 13:26 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2020-12-01 09:44
4 | WTG-0075B-NDG0-0000 | 2111352 | GEARBOX OIL, Add about 5 Gallons of Amsoil | 2019-08-05 16:20 | Closed | GBXOIL |  | FORWARD | JLAWRENCE |  | 2019-12-13 11:30
1 | WTG-0027-NDGP-0000 | 2111361 | GEARBOX OIL, Replace oil pump | 2019-08-05 16:53 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2019-08-21 09:38
1 | WTG-0169-0000 | 2114736 | GEARBOX OIL, Secondary filter system installation | 2019-08-15 14:21 | Closed | GBXOIL | GBXFILTINS | CAMP SPRINGS II | JSANCHEZ |  | 2019-08-19 14:19
4 | WTG-0008-NDG0-0000 | 2114743 | GEARBOX OIL, Add about 5 Gallons of Amsoil | 2019-08-15 13:31 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-12-04 10:54
5 | WTG-0095-NDG0-0000 | 2116100 | GEARBOX OIL, Add 2-3 gallons of Amsoil | 2019-08-20 17:21 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-11-18 12:31
8 | WTG-0040-NDG0-0000 | 2117311 | Add oil additive to main gearbox | 2019-08-26 08:19 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-08-27 08:35
8 | WTG-0024-NDG0-0000 | 2117314 | Add oil additive to main gearbox | 2019-08-26 08:21 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-08-27 08:24
8 | WTG-0050-NDG0-0000 | 2117321 | Add oil additive to main gearbox | 2019-08-26 08:43 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-08-27 08:44
1 | WTG-0047-NDG0-0000 | 2122036 | GEARBOX OIL, Oil Sample | 2019-09-03 13:58 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS I | CAMP SPRINGS |  | 2019-09-05 09:09
2 | WTG-0312-NDGP-0000 | 2122731 | GEARBOX OIL, Oil Debris Sample | 2019-09-04 09:51 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL III | NFALASZ |  | 2019-09-12 07:33
2 | WTG-0210-0000 | 2125892 | GEARBOX OIL, Fix oil leak | 2019-09-11 07:43 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NHEITHOFF |  | 2020-03-18 08:45
5 | WTG-0049-NDG0-0000 | 2136391 | GEARBOX OIL, Add/Top-Off | 2019-10-09 13:26 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-05-26 14:18
5 | WTG-0046-NDGP-0000 | 2137891 | Oil Pump Replacement | 2019-10-17 15:50 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2019-10-18 09:49
2 | WTG-0043-0000 | 2138542 | GEARBOX OIL, Secondary filter system motor replacement | 2019-10-21 18:06 | Closed | GBXOIL | GBXFILTELEM | GUNSIGHT | DKEETON |  | 2020-01-31 17:41
9 | WTG-0218-0000 | 2225075 | GEARBOX, Oil Change | 2020-05-19 15:23 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:40
1 | WTG-0128-NDGP-0000 | 2031957 | Oil pump motor needs flipped (not leaking) | 2019-02-05 08:09 | Closed | GBXOIL | GBXOILCOOL | GREXP | GRAND RIDGE |  | 2020-04-01 14:14
5 | WTG-0050-0000 | 2032680 | Oil cooler shroud self tapping screws | 2019-02-05 17:05 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2019-04-09 15:56
1 | GBX-000021 | 2039674 | Leaking Pall filter housing | 2019-02-23 12:11 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2019-12-20 15:59
1 | WTG-0015-0000 | 2055890 | 2019 Padmount Oil Sample | 2019-03-27 15:33 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-04-18 13:38
1 | WTG-0009-0000 | 2055897 | 2019 Padmount Oil Sample | 2019-03-27 15:35 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-04-18 13:37
1 | WTG-0012-0000 | 2055893 | 2019 Padmount Oil Sample | 2019-03-27 15:34 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-04-18 13:38
1 | WTG-0010-0000 | 2055895 | 2019 Padmount Oil Sample | 2019-03-27 15:34 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-04-18 13:37
1 | WTG-0014-0000 | 2055891 | 2019 Padmount Oil Sample | 2019-03-27 15:33 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2021-09-16 10:18
1 | WTG-0011-0000 | 2055894 | 2019 Padmount Oil Sample | 2019-03-27 15:34 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-04-18 13:37
1 | WTG-0048-0000 | 2067460 | GEARBOX OIL, Fix oil leak | 2019-04-22 16:03 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CWERNER
1 | WTG-0020-0000 | 2070163 | 2019 Padmount Oil Sample | 2019-04-29 15:34 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-05-07 15:12
1 | WTG-0028-NDG0-0000 | 2077941 | gearbox inspection ,oil leak | 2019-05-20 17:18 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2019-05-23 14:26
5 | WTG-0006-0000 | 2189929 | Oil hose has cracks, should try to warranty | 2020-02-24 17:21 | Closed | GBXOIL | BLANK | UPSTREAM | PRAIRIE BREEZE2 |  | 2022-08-31 17:02
4 | WTG-0034-NDGP-0000 | 2097008 | GEARBOX OIL, Oil cooler shround needs self tappers | 2019-06-27 13:40 | Closed | GBXOIL | GBXOILCOOL | FORWARD | MPEARSON |  | 2019-11-18 12:30
1 | WTG-0080-0000 | 2102385 | Replace Gearbox Hose | 2019-07-09 15:58 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2019-08-27 15:01
1 | WTG-0083-0000 | 2103043 | GEARBOX OIL, Fix oil leak | 2019-07-12 17:41 | Closed | GBXOIL | GBXOILLEAK | BETHEL | AGALARZA |  | 2019-07-31 16:24
5 | WTG-0028-NDG0-0000 | 2109366 | Gearbox Oil Work/Issue | 2019-08-01 09:05 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | WILLOWCREEK |  | 2020-06-29 12:23
1 | WTG-0107-0000 | 2126457 | GEARBOX OIL, Fix oil leak | 2019-09-13 18:07 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2020-06-15 16:01
4 | WTG-0204A-NDG0-0000 | 2128654 | GEARBOX OIL, Add/Top-Off 5gals | 2019-09-24 17:13 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2019-12-13 11:29
3 | SYS-WTG-WIEC | 2129077 | GEARBOX OIL, Oil Sample, Semi-annual | 2019-09-25 12:17 | Closed | GBXOIL | GBXOILSAMP | WILLOW CREEK | MSTONER |  | 2019-09-25 12:22
5 | WTG-0045-NDG0-0000 | 2136403 | GEARBOX OIL, Add/Top-Off 5gals | 2019-10-09 16:36 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2020-01-17 10:14
4 | WTG-0021-0000 | 2225131 | GEARBOX OIL, Add/Top-Off | 2020-05-19 17:48 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-05-26 14:56
9 | WTG-0219-0000 | 2225076 | GEARBOX, Oil Change | 2020-05-19 15:23 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE2 | MCASPER |  | 2020-07-30 14:40
5 | WTG-0J06-NDGP-0000 | 2141848 | GEARBOX OIL, Particle counter troubleshooting | 2019-10-25 09:54 | Closed | GBXOIL | GBXPARTTS | HIGH SHELDON | MSNOW |  | 2020-03-31 12:48
5 | WTG-0016-NDGP-0000 | 2143596 | GEARBOX OIL, Floor clean up | 2019-10-29 17:49 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2020-11-20 13:39
1 | WTG-0002-0000 | 2144959 | GEARBOX OIL, Fix oil leak | 2019-10-31 13:47 | Closed | GBXOIL | GBXOILLEAK | BUFFALO MOUNT | CRO EAST | 30 | 2020-05-21 13:40
4 | WTG-0A02-NDGP-0000 | 2145573 | GEARBOX OIL, Oil Sample | 2019-11-01 11:47 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | MSNOW |  | 2020-05-18 13:06
4 | WTG-0B01-NDGP-0000 | 2145576 | GEARBOX OIL, Oil Sample | 2019-11-01 11:54 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | MSNOW |  | 2020-05-19 14:23
4 | WTG-0F03-NDGP-0000 | 2145577 | GEARBOX OIL, Oil Sample | 2019-11-01 11:55 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | MSNOW |  | 2020-06-04 13:14
4 | WTG-0006-0000 | 2146753 | GEARBOX OIL, Add about 5 gallons | 2019-11-04 13:09 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-12-13 11:27
1 | WTG-0019-NDG0-0000 | 2152804 | GEARBOX OIL, Fix oil leak | 2019-11-15 16:27 | Closed | GBXOIL | GBXOILLEAK | MCADOO | MCADOO |  | 2019-11-20 08:09
1 | WTG-0214-0000 | 2154673 | GEARBOX OIL, Fix oil leak // Misc. Repairs | 2019-11-22 19:46 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NHEITHOFF |  | 2019-12-03 15:07
3 | WTG-0039-NDG0-0000 | 2158180 | Oil sample | 2019-12-02 15:30 | Closed | GBXOIL | GBXOILSAMP | FORWARD | KLEFFELMAN |  | 2019-12-04 11:16
2 | WTG-0037-0000 | 2161546 | Oil Pump Inversion | 2019-12-09 16:19 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MMCCABE |  | 2020-06-02 15:44
1 | WTG-0072-NDGP-0000 | 2246672 | Replace GB oil pump | 2020-07-14 15:10 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2020-07-20 08:09
4 | WTG-0048-NDG0-0000 | 2185292 | GEARBOX OIL, Add/Top-Off 5 gallons | 2020-02-06 16:01 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2020-05-19 10:52
1 | WTG-0039-0000 | 2185472 | PALL Filter Housing Leak / Oil Pump Failing | 2020-02-07 12:52 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2020-04-06 13:18
2 | WTG-0071A-NDGP-0000 | 2186050 | Replace O-Rings between gbx oil pump and filter housing | 2020-02-07 11:56 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2020-02-10 15:59
5 | WTG-0096-0000 | 2258117 | Oil cooler outlet hose to gearbox manifold replacement | 2020-08-12 14:16 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2020-09-10 09:58
2 | WTG-0058-0000 | 2224991 | GEARBOX OIL, Add/Top-Off | 2020-05-19 12:25 | Closed | GBXOIL | GBXOILADD | TURKEY TRACK | JBRILEY |  | 2020-10-20 10:59
4 | WTG-0062-NDGP-0000 | 2192857 | GEARBOX OIL, Replace oil pump coupler | 2020-02-28 16:34 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2020-09-16 08:13
5 | WTG-0046-0000 | 2195567 | GEARBOX OIL, Add about 5 gallons | 2020-03-03 15:18 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-04-01 14:45
4 | WTG-0098-NDG0-0000 | 2196125 | GEARBOX OIL, Add/Top-Off | 2020-03-04 12:56 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2020-03-05 09:21
4 | WTG-0053-0000 | 2197324 | GEARBOX OIL, Add 5 Gallons | 2020-03-06 16:06 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-04-01 14:50
1 | WTG-0079-0000 | 2236930 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2020-06-19 08:44 | Closed | GBXOIL | GBXOILCOOL | TURKEY TRACK | TURKEY TRACK |  | 2021-08-09 14:41
1 | WTG-0020-0000 | 2238860 | Replace Gearbox Hose | 2020-06-26 15:20 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2020-07-08 13:16
2 | WTG-0035-NDG0-0000 | 2246043 | GEARBOX OIL, Particle counter installation | 2020-07-13 09:29 | Closed | GBXOIL | GBXPARTINS | JUDITH GAP | JUDITHGAP |  | 2020-07-15 08:18
1 | WTG-0106-0000 | 2248036 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:49 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-07-20 15:40
2 | WTG-0041A-0000 | 2248059 | Gbx oil hoses changeout | 2020-07-20 11:47 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2021-08-10 13:29
1 | WTG-0118-0000 | 2256060 | GEARBOX OIL, Fix oil leak | 2020-08-05 15:42 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2023-05-01 12:45
1 | WTG-0054-0000 | 2285202 | GEARBOX OIL, Secondary filter Motor replacement | 2020-09-16 15:24 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CHORN |  | 2023-04-04 10:55
1 | WTG-0022-NDG0-0000 | 2285823 | Front seal leaking | 2020-09-21 16:50 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JUDITHGAP |  | 2024-02-09 12:46
1 | WTG-0217-0000 | 2288251 | GEARBOX OIL, Fix oil leak | 2020-09-29 19:13 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2020-10-13 13:38
4 | WTG-0006-NDG0-0000 | 2291522 | 5 gallons oil add | 2020-10-05 10:40 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2021-02-22 11:41
1 | WTG-0026-0000 | 2292691 | Replace Oil Hose | 2020-10-07 09:26 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | BDIAZ |  | 2021-09-02 12:03
4.2 | WTG-0095-NDGP-0000 | 2293497 | GEARBOX OIL, Replace oil cooler | 2020-10-12 15:06 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JDETWILER |  | 2021-03-05 06:52
2 | WTG-0234-0000 | 2293526 | GEARBOX OIL, Fix oil leak | 2020-10-12 16:42 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NHEITHOFF |  | 2021-02-17 15:54
2 | WTG-0045-NDG0-0000 | 2296148 | GEARBOX OIL, Add/Top-Off | 2020-10-21 19:00 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2020-10-30 09:02
5 | WTG-0115-NDGP-0000 | 2310802 | GEARBOX OIL, Fix oil leak | 2020-11-09 16:17 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2020-12-17 16:26
4 | WTG-0053-0000 | 2310801 | Secondary Filter Leaking | 2020-11-09 16:17 | Cancelled | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2021-04-20 06:57
4 | WTG-0095-0000 | 2322650 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2020-12-03 17:46 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-03-01 14:54
4 | WTG-0035-0000 | 2324670 | GEARBOX OIL, Add about 5 Gallons | 2020-12-14 16:58 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-12-28 07:52
4 | WTG-0040A-0000 | 2327906 | Secondary filtration leaking | 2020-12-17 17:12 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2020-12-28 07:56
2 | WTG-0033-0000 | 2342433 | Replace blue oil hose | 2021-01-26 07:31 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2023-03-10 11:53
4 | WTG-0003A-0000 | 2342343 | Add approximately 5 gal AMS oil | 2021-01-25 13:42 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2021-06-22 06:58
1 | WTG-0013-N000-0000 | 2141865 | Gearbox Oil Work/Issue | 2019-10-25 10:57 | Closed | GBXOIL | GBXOILSAMP | JUDITH GAP | JUDITHGAP |  | 2019-10-25 15:48
2 | WTG-0042-NDG0-0000 | 2143529 | GEARBOX OIL, Fix oil leak | 2019-10-29 15:12 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | CSLY |  | 2020-03-13 09:05
2 | WTG-0076-NDGP-0000 | 2147261 | GEARBOX OIL, Particle counter troubleshooting | 2019-11-05 15:43 | Closed | GBXOIL | GBXPARTINS | STANTON | MSNOW |  | 2022-11-14 10:03
2 | GBX-000040 | 2154323 | GEARBOX OIL, Add/Top-Off | 2019-11-21 11:51 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | GOLDTHWAITE |  | 2020-01-29 15:18
1 | WTG-0I02-NDG0-0000 | 2159196 | GEARBOX OIL, Oil Sample | 2019-12-03 21:36 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | SCLARK |  | 2019-12-04 07:05
5 | WTG-0037-NDGP-0000 | 2161836 | GEARBOX OIL, Add/Top-Off 5 gals | 2019-12-10 15:26 | Closed | GBXOIL | GBXOILADD | FORWARD | MPEARSON |  | 2020-02-19 10:26
1 | WTG-0241-0000 | 2168566 | GEARBOX OIL, Fix oil leak/snowflake | 2020-01-02 12:46 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | JGILLILAN |  | 2021-08-30 15:08
1 | WTG-0055-0000 | 2171547 | GEARBOX OIL, Fix oil leak | 2020-01-06 15:16 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | BUCKEYE |  | 2020-01-07 15:28
2 | WTG-0033-NDG0-0000 | 2172370 | Gearbox running too hot | 2020-01-09 17:01 | Cancelled | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2020-01-29 14:55
2 | WTG-0087-NDGP-0000 | 2172779 | Lube pump motor bearings are going bad | 2020-01-12 14:27 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2020-01-17 10:59
2 | WTG-0001-0000 | 2172995 | GEARBOX OIL, Add/Top-Off | 2020-01-09 15:14 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | MIAMI |  | 2020-01-16 07:41
4 | WTG-0001-NDG0-0000 | 2192508 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0002-NDG0-0000 | 2192509 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0003-NDG0-0000 | 2192510 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0004-NDG0-0000 | 2192511 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0005-NDG0-0000 | 2192512 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0006-NDG0-0000 | 2192513 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0007-NDG0-0000 | 2192514 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0008-NDG0-0000 | 2192515 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0009-NDG0-0000 | 2192516 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0010-NDG0-0000 | 2192517 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0011-NDG0-0000 | 2192518 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0015-NDG0-0000 | 2192522 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0016-NDG0-0000 | 2192523 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0017-NDG0-0000 | 2192524 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0018-NDG0-0000 | 2192525 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0019-NDG0-0000 | 2192526 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
2 | GBX-000032 | 2199462 | Gbx low oil level | 2020-03-19 10:03 | Closed | GBXOIL | GBXOILADD | ORANGEVILLE | BHUNTER |  | 2020-03-24 12:30
9 | SITE-FSO | 2201357 | GEARBOX, Oil Change PBEC EXP 2020 | 2020-03-26 14:29 | Closed | GBXOIL | SVCS-GBXOILCHG | FSO | CBORER |  | 2022-12-28 16:08
4 | WTG-0036-NDG0-0000 | 2202110 | GEARBOX OIL, Add/Top-Off | 2020-03-27 21:39 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2020-07-02 09:34
1 | WTG-0036-NDGP-0000 | 2225446 | GEARBOX OIL, Replace oil cooler | 2020-05-21 17:29 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2022-01-19 12:29
3 | WTG-0081-0000 | 2246679 | Secondary filtration leak | 2020-07-14 15:07 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JJENSEMA |  | 2022-07-05 08:19
1 | WTG-0068-0000 | 2233579 | GEARBOX OIL, Particle counter installation | 2020-06-05 09:39 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | JBRILEY |  | 2020-08-26 16:34
3 | WTG-0001-NDG0-0000 | 2258692 | GBX oil pump inversion | 2020-08-14 11:14 | Closed | GBXOIL | GBXOILCOOL | GORDON BUTTE | JUDITHGAP |  | 2021-04-27 09:16
3 | WTG-0002-NDG0-0000 | 2258693 | GBX oil pump inversion | 2020-08-14 11:17 | Closed | GBXOIL | GBXOILCOOL | GORDON BUTTE | JUDITHGAP |  | 2021-11-04 11:42
4 | WTG-0060A-NDG0-0000 | 2237482 | Add 5 gallons oil | 2020-06-23 12:37 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2020-08-07 10:24
1 | WTG-0102-NDG0-0000 | 2245415 | GEARBOX OIL, Fix oil leak | 2020-07-09 13:34 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MMEADOWS |  | 2020-07-13 16:00
4.2 | WTG-0066-NDGP-0000 | 2247085 | GEARBOX OIL, Replace oil cooler | 2020-07-16 08:57 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2020-11-04 06:49
4 | WTG-0097-0000 | 2247511 | GEARBOX OIL, Fix oil leak at inspection covers | 2020-07-17 13:18 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2021-03-01 14:37
1 | WTG-0113-0000 | 2247454 | GBX Oil Hose Inspection | 2020-07-17 12:52 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-07-17 13:32
1 | WTG-0065-0000 | 2248014 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:37 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-09 15:25
1 | WTG-0094-0000 | 2248027 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:43 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-12-04 11:50
1 | WTG-0101-0000 | 2248033 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:48 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-12-11 09:46
1 | WTG-0103-0000 | 2248034 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:48 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-07-27 09:04
1 | WTG-0105-0000 | 2248035 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:49 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-07-20 15:40
1 | WTG-0096-0000 | 2248028 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:45 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-01-26 12:11
1 | WTG-0099-0000 | 2248031 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:47 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-12-04 15:55
1 | WTG-0100-0000 | 2248032 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:47 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-03-01 10:59
1 | WTG-0114-0000 | 2248041 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:50 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-12-22 13:36
1 | WTG-0003-0000 | 2258031 | GEARBOX OIL, Fix oil leak | 2020-08-12 10:32 | Closed | GBXOIL | GBXOILLEAK | BETHEL | HFLORESGONZALEZ |  | 2020-08-12 15:33
3 | WTG-0003-NDG0-0000 | 2258694 | GBX oil pump inversion | 2020-08-14 11:19 | Closed | GBXOIL | GBXOILCOOL | GORDON BUTTE | JUDITHGAP |  | 2021-08-13 10:42
4 | WTG-0063A-0000 | 2274600 | GEARBOX OIL, Add about 3 gallons | 2020-08-27 16:26 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-04-05 06:49
1 | WTG-0012-0000 | 2274559 | GEARBOX OIL, Fix oil leak | 2020-08-27 12:51 | Closed | GBXOIL | GBXOILLEAK | BETHEL | JHOOD |  | 2020-08-28 15:43
4 | WTG-0002C-NDGP-0000 | 2310795 | Secondary Filter Leaking | 2020-11-09 16:17 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2021-07-07 07:06
2 | WTG-0074-NDG0-0000 | 2312135 | GEARBOX OIL, Add/Top-Off | 2020-11-12 17:41 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2020-12-09 16:12
1 | WTG-0239-0000 | 2313428 | GEARBOX OIL, Fix oil leak | 2020-11-20 09:29 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | DGORDON |  | 2020-12-08 15:30
2 | WTG-0003-NDGP-0000 | 2320666 | GEARBOX OIL, Secondary filter system Leaking | 2020-12-01 15:16 | Closed | GBXOIL | GBXFILTINS | VANTAGE | VANTAGE |  | 2021-01-12 10:45
5 | WTG-0002C-NDG0-0000 | 2341070 | 5 gallons oil add | 2021-01-19 14:52 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2021-02-04 10:03
1 | WTG-0010-0000 | 2350318 | GEARBOX OIL, Secondary filter system installation | 2021-02-03 14:55 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | BUCKEYE |  | 2021-11-25 15:10
4 | WTG-0083-0000 | 2350357 | Leaking Secondary Pump | 2021-02-03 15:21 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2021-03-25 07:02
4 | WTG-0094-0000 | 2372123 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0070-0000 | 2354496 | Secondary Filtration Leaking | 2021-02-08 14:08 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2021-07-02 07:04
4 | SYS-WTG-BETH | 2367873 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL | GBXOILSAMP | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0089-0000 | 2372118 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0090-0000 | 2372119 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0091-0000 | 2372120 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0092-0000 | 2372121 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0093-0000 | 2372122 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0011-0000 | 2372040 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0095-0000 | 2372124 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0096-0000 | 2372125 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0097-0000 | 2372126 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0012-0000 | 2372041 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0013-0000 | 2372042 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0014-0000 | 2372043 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0015-0000 | 2372044 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0016-0000 | 2372045 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0017-0000 | 2372046 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
1 | WTG-0065-0000 | 2380594 | GEARBOX OIL, Fix oil leak | 2021-03-02 11:35 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | DTILLIS |  | 2022-04-10 15:39
4.2 | WTG-0063-0000 | 2382499 | GEARBOX OIL, Replace oil cooler | 2021-03-10 15:08 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCRESSWELL |  | 2021-09-16 15:03
2 | WTG-0028-NDG0-0000 | 2383803 | Add Amsoil | 2021-03-17 16:19 | Closed | GBXOIL | GBXOILADD | VANTAGE | CLANDERS |  | 2021-04-08 09:52
1 | WTG-0042-0000 | 2385061 | GEARBOX OIL, Fix oil leak | 2021-03-24 12:55 | Closed | GBXOIL | GBXOILLEAK | BETHEL | ZMCCASLAND |  | 2021-03-25 08:46
1 | WTG-0204-0000 | 2385795 | GEARBOX OIL, Fix oil leak | 2021-03-25 16:16 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NMCFARLAND |  | 2021-12-21 16:11
2 | WTG-0221-0000 | 2400548 | GEARBOX OIL, Fix oil leak, 1 hose | 2021-04-12 12:27 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | DGORDON |  | 2023-12-28 10:38
5 | WTG-0028-NDG0-0000 | 2401956 | Check Particle Counter Connection | 2021-04-19 13:46 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JCULLITY |  | 2021-08-02 10:09
5 | WTG-0036-NDG0-0000 | 2401957 | Check Particle Counter Connection | 2021-04-19 13:47 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JCULLITY |  | 2021-08-23 15:01
5 | WTG-0044-NDG0-0000 | 2401958 | Check Particle Counter Connection | 2021-04-19 13:47 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JCULLITY |  | 2022-05-18 08:46
5 | WTG-0087-NDG0-0000 | 2401960 | Check Particle Counter Connection | 2021-04-19 13:49 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JCULLITY |  | 2021-07-02 11:57
1 | WTG-0050-0000 | 2405177 | GEARBOX OIL, Fix oil leak | 2021-04-27 16:24 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | PMAGER |  | 2023-01-04 16:10
3 | SITE-DEUEL | 2410972 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL | SVC-GBXOILCHNG | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
5 | WTG-0075B-0000 | 2467375 | Pressure wash oil cooler | 2021-07-16 11:27 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2021-07-20 06:45
4 | WTG-0021-0000 | 2418503 | GEARBOX OIL, Add/Top-Off | 2021-05-12 10:45 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-05-13 07:12
5 | WTG-0234-0000 | 2421638 | GEARBOX OIL, Fix oil leak - Hoses/yaw flag | 2021-05-18 10:54 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NHEITHOFF |  | 2021-08-30 14:03
4 | WTG-0062-0000 | 2438267 | GEARBOX OIL, Add about 5 Gallons | 2021-06-15 11:41 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-08-19 06:48
5 | WTG-0025-0000 | 2443232 | GEARBOX OIL, Fix oil leak | 2021-06-29 13:02 | Closed | GBXOIL | GBXOILLEAK | BETHEL | BBALDERAZ |  | 2022-07-25 16:18
4 | WTG-0059A-0000 | 2465679 | Purple hose replacement | 2021-07-14 13:03 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2021-12-30 07:41
1 | WTG-0035-0000 | 2470641 | GEARBOX OIL, Secondary filter system installation | 2021-07-29 16:32 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | CROBERTS |  | 2021-10-04 09:49
2 | WTG-0107-0000 | 2471516 | GEARBOX OIL, Replace oil cooler fan duct | 2021-07-30 18:35 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCRESSWELL |  | 2021-08-25 14:03
5 | WTG-0033-0000 | 2581090 | CMS HSS Check | 2021-09-24 11:27 | Cancelled | CMS | CMSHSS | DEUEL HARVEST | CBILLIG |  | 2022-06-28 14:07
2 | WTG-0041A-0000 | 2575496 | Remove remaining pigmat after oil spill | 2021-09-07 07:02 | Closed | GBXOIL | GBXOILADD | FORWARD | JJENSEMA |  | 2021-11-18 10:01
2 | WTG-0214-0000 | 2576730 | GEARBOX OIL, Fix oil leak | 2021-09-09 08:20 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | CWERNER |  | 2022-01-10 20:26
1 | WTG-0042-0000 | 2576631 | GEARBOX OIL, Fix oil leak | 2021-09-08 12:26 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JJENSEMA |  | 2022-11-08 06:09
4.1 | WTG-0042-0000 | 2576632 | Secondary Filtration Leaking | 2021-09-08 12:38 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JJENSEMA |  | 2021-11-18 10:02
4 | WTG-0085-0000 | 2577289 | GEARBOX OIL, Secondary filter system leaking | 2021-09-10 14:00 | Closed | GBXOIL | GBXFILTELEM | FORWARD | DMONROE |  | 2022-07-05 08:29
4 | WTG-0028-NDGP-0000 | 2577837 | GEARBOX OIL, replace gear oil coupling red spider insert. | 2021-09-13 13:45 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2021-09-16 06:38
1 | WTG-0010-0000 | 2616411 | rFSA Claim- Radiator Replacement | 2021-10-13 15:54 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GBUNCH |  | 2022-01-10 15:48
5 | WTG-0012-0000 | 2616799 | Replace jensen pump seal | 2021-10-15 12:57 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2022-08-29 10:18
5 | WTG-0010-0000 | 2617756 | CMS Generator Bearing Check | 2021-10-19 10:10 | Cancelled | CMS | CMSGENB | UPSTREAM | CBILLIG |  | 2022-03-25 13:03
4 | WTG-0061-NDGP-0000 | 2930236 | Replace red spider insert. | 2022-05-11 16:29 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2022-09-16 09:44
4 | WTG-0061-NDG0-0000 | 2930237 | GEARBOX OIL, Add/Top-Off 5gals | 2022-05-11 16:35 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2022-09-16 09:44
4 | WTG-0018-0000 | 2930193 | GEARBOX OIL, Secondary filter leak | 2022-05-11 10:24 | Closed | GBXOIL | GBXFILTELEM | FORWARD | DMONROE |  | 2022-10-07 15:01
2 | GBX-000082 | 2631282 | CMS Gearbox Borescope | 2021-11-02 10:31 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2021-11-17 17:15
4 | WTG-0009-0000 | 2649001 | GEARBOX OIL, Add/Top-Off about 6-7 Gallons | 2021-11-22 11:14 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-05-10 09:32
4 | WTG-0008-0000 | 2651424 | GEARBOX OIL, Add 5 Gallons | 2021-11-29 12:48 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2021-12-02 12:45
5 | WTG-0301-0000 | 2654604 | GEARBOX OIL, Fix oil leak | 2021-12-02 16:16 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | RKUDERA |  | 2022-10-03 13:33
5 | WTG-0303-0000 | 2656450 | Leaking GBX hose | 2021-12-06 11:42 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | AHOFFMANN |  | 2022-08-31 16:59
2 | GBX-000217 | 2667974 | CMS Gearbox Borescope | 2021-12-13 09:59 | Closed | CMS | CMSGBXBORE | PRAIRIE BREEZE2 | DGORDON |  | 2022-02-10 12:00
4 | WTG-0045-0000 | 2680581 | Oil leak on secondary filter seal | 2021-12-20 14:34 | Closed | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE |  | 2022-04-10 17:25
1 | WTG-00P7-NDD0-0000 | 2890105 | CMS Generator Bearing Check | 2022-03-23 13:29 | Cancelled | CMS | CMSGENB | TATANKA RIDGE | CBILLIG |  | 2022-08-19 16:06
2 | WTG-0043-NDG0-0000 | 2687477 | CMS Gearbox Borescope | 2021-12-29 16:30 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | KSTEWART |  | 2022-06-29 08:02
2 | BRG-000107 | 2691189 | CMS Main Bearing Borescope and Purge | 2022-01-03 15:49 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | CBILLIG |  | 2022-01-21 07:48
4.2 | WTG-0060A-0000 | 2696827 | Replace oil cooler motor | 2022-01-04 15:32 | Cancelled | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2023-05-18 11:56
5 | WTG-0021-NDGP-0000 | 2376601 | GEARBOX OIL, Replace oil pump | 2021-02-25 16:50 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2023-11-16 10:13
5 | WTG-0201-NDG0-0000 | 2382507 | GEARBOX OIL, Fix oil leak | 2021-03-10 16:03 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | DTILLIS |  | 2022-09-28 14:20
1 | WTG-0104-NDGP-0000 | 2393101 | Replace hose | 2021-03-26 15:30 | Closed | GBXOIL | GBXOILCOOL | CAMP SPRINGS II | TPRIEST |  | 2021-04-02 09:34
1 | WTG-0100-0000 | 2395039 | GEARBOX OIL, Fix oil leak | 2021-03-31 17:15 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2021-06-16 08:01
5 | WTG-0012-NDG0-0000 | 2401955 | Check Particle Counter Connection | 2021-04-19 13:38 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JCULLITY |  | 2021-07-15 08:52
5 | WTG-0067-NDG0-0000 | 2401959 | Check Particle Counter Connection | 2021-04-19 13:48 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JCULLITY |  | 2021-08-23 14:59
5 | WTG-0118-NDG0-0000 | 2401961 | Check Particle Counter Connection | 2021-04-19 13:51 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JCULLITY |  | 2021-07-15 08:48
5 | WTG-0222-0000 | 2407000 | GEARBOX OIL, Fix oil leak | 2021-05-02 11:35 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NMCFARLAND |  | 2023-10-23 23:15
1 | WTG-0018-0000 | 2423170 | Oil Pump & Motor Inversion | 2021-05-24 16:57 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MCONDON |  | 2023-05-12 15:28
4 | WTG-0007-NDG0-0000 | 2438280 | GEARBOX OIL, Add/Top-Off 5 gallons | 2021-06-15 14:30 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2021-06-22 07:00
4 | WTG-0073-0000 | 2445124 | Replace lube pump coupling | 2021-06-30 12:52 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2021-07-02 07:09
4.1 | WTG-0073-NDG0-0000 | 2445127 | Moventas Hose Replacement | 2021-07-01 10:16 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2022-06-10 08:47
4 | WTG-0071A-0000 | 2464169 | Secondary filter leaking from shaft seal | 2021-07-08 14:59 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2021-07-09 08:04
4 | WTG-0089-0000 | 2571234 | GEARBOX OIL, Add/Top-Off | 2021-08-31 12:51 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2021-09-03 10:19
1 | WTG-0069-0000 | 2575860 | GEARBOX OIL, Fix oil leak | 2021-09-07 10:36 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | CWERNER |  | 2021-09-10 11:08
1 | WTG-0079-0000 | 2575861 | GEARBOX OIL, Fix oil leak | 2021-09-07 10:38 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | CWERNER |  | 2021-09-10 11:08
5 | WTG-0045-0000 | 2615506 | EM: Drive train vibration | 2021-10-08 17:14 | Closed | CMS | CMSHSS | SUNDANCE | CBILLIG |  | 2022-01-25 14:50
5 | WTG-0063-0000 | 2615491 | Nanjing HS Seal Leak | 2021-10-08 16:04 | Ready to Schedule | GBXOIL | GBXOILLEAK | UPSTREAM | CWERNER
5 | WTG-0219-0000 | 2615483 | GEARBOX OIL, Fix oil leak | 2021-10-08 15:45 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | AHOFFMANN |  | 2022-10-12 16:25
2 | WTG-0003-0000 | 2616804 | GEARBOX, Gearbox borescope Inspection | 2021-10-15 15:19 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | CBILLIG |  | 2021-12-27 09:28
2 | WTG-0024-0000 | 2616811 | MAIN BEARING, Main bearing borescope inspection | 2021-10-15 16:07 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | CBILLIG |  | 2021-11-15 09:17
9 | SITE-AIPL | 2623609 | WO for OOS Oil Changes GPWF | 2021-10-25 22:27 | Ready to Schedule | GBXOIL | GBXOILCHG | ALLIANT IPL | MCOURTNEY
1 | WTG-0038-0000 | 2624910 | GEARBOX OIL, Fix radiator leak | 2021-10-27 16:09 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2023-03-07 16:21
5 | WTG-0031-0000 | 2631411 | GEARBOX OIL, Add 3-5 Gallons | 2021-11-02 10:34 | Closed | GBXOIL | GBXOILADD | FORWARD | JJENSEMA |  | 2022-03-07 12:02
5 | BRG-000037 | 2631344 | CMS Main Bearing Check | 2021-11-02 11:24 | Closed | CMS | CMSMB | SANTA RITA EAST | CBILLIG |  | 2021-12-14 08:37
5 | BRG-000093 | 2631349 | CMS Main Bearing Check | 2021-11-02 11:50 | Closed | CMS | CMSMB | SANTA RITA EAST | CBILLIG |  | 2021-11-09 15:15
4 | WTG-0036-0000 | 2633350 | GEARBOX OIL, Secondary filter leak | 2021-11-05 14:03 | Closed | GBXOIL | GBXFILTELEM | FORWARD | DMONROE |  | 2022-04-26 09:01
2 | WTG-0059-0000 | 2635969 | CMS Gearbox Borescope | 2021-11-08 12:57 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | CBILLIG |  | 2021-12-16 14:03
5 | WTG-0016-NDG0-0000 | 2644708 | HSS inspection | 2021-11-11 14:37 | Closed | CMS | CMSHSS | BLOOMING GROVE | MWILSON |  | 2021-11-15 08:55
2 | WTG-00B8-0000 | 2645568 | CMS Main Bearing Borescope | 2021-11-16 10:42 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | CBILLIG |  | 2022-08-15 15:38
2 | WTG-0025-NDGP-0000 | 2645925 | Replace GBX Filter for Torque Maintenance | 2021-11-16 15:22 | Closed | GBXOIL | GBXFILTELEM | BLOOMING GROVE | GSUGGETT |  | 2021-11-16 15:54
2 | WTG-0028-NDGP-0000 | 2645926 | Replace GBX Filter for Torque Maintenance | 2021-11-16 15:28 | Closed | GBXOIL | GBXFILTELEM | BLOOMING GROVE | GSUGGETT |  | 2021-11-16 15:53
2 | WTG-0030-NDGP-0000 | 2645932 | Replace GBX Filter for Torque Maintenance | 2021-11-16 15:43 | Closed | GBXOIL | GBXFILTELEM | BLOOMING GROVE | GSUGGETT |  | 2021-11-16 15:53
2 | WTG-0015-NDG0-0000 | 2645929 | Gearbox Borescope Inspection | 2021-11-16 15:30 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | MFERRARO |  | 2021-11-17 13:14
1 | WTG-0007-0000 | 2647268 | GEARBOX OIL, Fix oil leak | 2021-11-19 14:48 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | FRAMIREZ |  | 2021-12-01 13:45
5 | WTG-2080-NDG0-0000 | 2947987 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-21 12:49 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-10 11:06
5 | WTG-0026-0000 | 2673005 | CMS Generator Bearing Check | 2021-12-16 10:14 | Closed | CMS | CMSGENB | SUNDANCE | CBILLIG |  | 2022-06-09 13:05
5 | WTG-0019-0000 | 2680538 | CMS Trouble Shoot (Invenergy request, non-GE) | 2021-12-20 13:00 | Closed | CMS | CMSTRBLSHOOT | BLOOMING GROVE | CBILLIG |  | 2023-03-28 13:42
4 | WTG-0060A-0000 | 2696829 | Gear oil motor and red spider coupling | 2022-01-04 15:36 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2022-01-24 09:24
4 | WTG-0018-NDGP-0000 | 2711524 | Replace Moventas GBX hose - cooler to manifold | 2022-01-05 12:16 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2022-04-10 17:26
2 | WTG-0328-0000 | 2715992 | GEARBOX OIL, Particle counter installation | 2022-01-06 14:03 | Closed | GBXOIL | GBXPARTINS | BISHOP HILL III | CBILLIG |  | 2022-08-16 15:08
2 | GBX-000236 | 2717334 | CMS Gearbox Borescope | 2022-01-10 16:10 | Closed | CMS | CMSGBXBORE | PRAIRIE BREEZE2 | DGORDON |  | 2022-02-10 11:59
2 | WTG-0047-0000 | 2803159 | CMS Gearbox Borescope | 2022-02-16 14:20 | Cancelled | CMS | CMSGBXBORE | SUNDANCE | CBILLIG |  | 2022-11-15 12:48
2 | WTG-0056-NDG0-0000 | 2803194 | GEARBOX OIL, Secondary filter system installation | 2022-02-16 15:40 | Ready to Schedule | GBXOIL | GBXFILTINS | VANTAGE | CCUSACK
1 | WTG-0005-0000 | 2804009 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2022-02-19 14:10 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | TLOONEY |  | 2022-02-28 13:26
2 | WTG-0032-0000 | 2802875 | GEARBOX OIL, Oil Sample | 2022-02-15 12:26 | Closed | GBXOIL | GBXOILSAMP | MAVERICK | JROULIER |  | 2022-04-18 16:36
5 | WTG-0028-NDG0-0000 | 2736741 | CMS HSS Check | 2022-01-24 16:36 | Closed | CMS | CMSHSS | SUNDANCE | GAXTENS |  | 2022-02-07 11:07
1 | GBX-000046 | 2740892 | GEARBOX OIL, Fix oil leak | 2022-02-01 09:54 | Closed | GBXOIL | GBXOILLEAK | MCADOO | DHALE |  | 2022-02-02 08:19
4.1 | WTG-0044-0000 | 2789059 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
2 | WTG-0312-0000 | 2717298 | CMS Gearbox Borescope | 2022-01-10 13:59 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | CBILLIG |  | 2022-02-21 11:29
1 | WTG-0074-0000 | 2717576 | GEARBOX OIL, Secondary filter system installation | 2022-01-11 16:53 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | LHATVELDT |  | 2022-01-13 10:57
4 | WTG-0096-0000 | 2718225 | GEARBOX OIL, Add/Top-Off 5 gallons | 2022-01-13 12:55 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-01-24 09:30
1 | WTG-0010-0000 | 2803956 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2022-02-18 23:10 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | TLOONEY |  | 2022-02-28 13:19
1 | WTG-0001-0000 | 2802832 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2022-02-15 09:20 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | TLOONEY |  | 2022-02-28 13:28
2 | WTG-0006-0000 | 2736989 | CMS Gearbox Borescope | 2022-01-25 10:47 | Closed | CMS | CMSGBXBORE | GORDON BUTTE | CBILLIG |  | 2022-01-28 08:05
2 | WTG-0034-0000 | 2738828 | GEARBOX Oil Hose Replacement, Purple and Yellow | 2022-01-27 16:29 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2022-02-01 13:47
1 | WTG-0078-0000 | 2763482 | GEARBOX OIL, Fix oil leak/add oil/clean nacelle | 2022-02-01 17:01 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | AHOFFMANN |  | 2022-03-08 10:12
4.1 | WTG-0031-0000 | 2789046 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0032-0000 | 2789047 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0033-0000 | 2789048 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0034-0000 | 2789049 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0035-0000 | 2789050 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0036-0000 | 2789051 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0037-0000 | 2789052 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0038-0000 | 2789053 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0039-0000 | 2789054 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0040-0000 | 2789055 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0041-0000 | 2789056 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0042-0000 | 2789057 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0043-0000 | 2789058 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0045-0000 | 2789060 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0049-0000 | 2789064 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0046-0000 | 2789061 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0047-0000 | 2789062 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0048-0000 | 2789063 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0050-0000 | 2789065 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0051-0000 | 2789066 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0052-0000 | 2789067 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0053-0000 | 2789068 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0054-0000 | 2789069 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0055-0000 | 2789070 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0059-0000 | 2789074 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0056-0000 | 2789071 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0057-0000 | 2789072 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0058-0000 | 2789073 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0060-0000 | 2789075 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0061-0000 | 2789076 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0062-0000 | 2789077 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0063-0000 | 2789078 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0064-0000 | 2789079 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0065-0000 | 2789080 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0069-0000 | 2789084 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0066-0000 | 2789081 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0067-0000 | 2789082 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0068-0000 | 2789083 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0070-0000 | 2789085 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0071-0000 | 2789086 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0072-0000 | 2789087 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0073-0000 | 2789088 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0074-0000 | 2789089 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0115-0000 | 2789130 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0112-0000 | 2789127 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0113-0000 | 2789128 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0114-0000 | 2789129 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0116-0000 | 2789131 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0117-0000 | 2789132 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0118-0000 | 2789133 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0119-0000 | 2789134 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0120-0000 | 2789135 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4 | WTG-0212-0000 | 2794003 | Secondary Filtration Leaking at the Pump | 2022-02-03 18:01 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JJENSEMA |  | 2022-07-22 08:01
2 | WTG-0004-NDB0-0000 | 2793855 | CMS Main Bearing Borescope and Purge per GE request | 2022-02-03 13:59 | Closed | CMS | CMSINSP | GOLDTHWAITE | JCULLITY |  | 2023-02-17 13:04
1 | WTG-003W-NDG0-0000 | 2794442 | CMS Gearbox Inspection per GE request | 2022-02-04 12:59 | Closed | CMS | CMSINSP | GOLDTHWAITE | JCULLITY |  | 2023-02-21 17:12
2 | WTG-0066-0000 | 2795922 | GEARBOX OIL, Fix oil leak | 2022-02-07 12:43 | Ready to Schedule | GBXOIL | GBXOILLEAK | UPSTREAM | NMCFARLAND
1 | WTG-0056-0000 | 2800083 | GEARBOX OIL, Particle counter troubleshooting | 2022-02-08 15:19 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | TBEILSMITH |  | 2022-02-15 11:35
5 | WTG-0214-0000 | 2812820 | GEARBOX OIL, Fix oil leak | 2022-03-04 16:31 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | RKUDERA |  | 2023-01-06 10:44
4 | WTG-0072A-0000 | 2815149 | Secondary filtration system, leaking | 2022-03-14 11:53 | Closed | GBXOIL | GBXFILTELEM | FORWARD | DMONROE |  | 2022-06-10 08:57
5 | WTG-0049-0000 | 2889710 | GEARBOX OIL, Add 5 Gal | 2022-03-22 15:17 | Closed | GBXOIL | GBXOILADD | FORWARD | JJENSEMA |  | 2023-03-07 11:39
4 | WTG-0210A-NDGP-0000 | 2889748 | Secondary oil pump is leaking | 2022-03-22 16:29 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2022-07-07 08:48
5 | BRG-000024 | 2907702 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-04-04 12:00 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-04-14 08:27
5 | WTG-0002-0000 | 2920032 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-04-13 09:33 | Closed | CMS | CMSTRBLSHOOT | UPSTREAM | CBILLIG |  | 2022-09-28 14:16
2 | GBX-00094 | 2922294 | CMS Gearbox Borescope | 2022-04-22 11:06 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | CBILLIG |  | 2022-05-18 13:57
1 | WTG-0021-0000 | 2923538 | GEARBOX OIL, Fix oil leak | 2022-04-26 16:26 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JJUTILA |  | 2022-04-27 09:10
4 | WTG-0038-0000 | 2925932 | GEARBOX OIL, Replace primary GBX oil filter | 2022-04-29 13:08 | Closed | GBXOIL | GBXFILTINS | FORWARD | ALANGKAU |  | 2022-06-10 11:01
4 | WTG-0047-0000 | 2925986 | GEARBOX OIL, Replace Orange Hose | 2022-04-29 14:13 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2022-09-16 09:43
1 | WTG-0047-0000 | 2927117 | GEARBOX OIL, Fix oil leak | 2022-05-02 18:09 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MLEGLEITER |  | 2023-01-09 11:58
3.1 | WTG-0010-NDG0-0000 | 3262518 | CMS sensor | 2024-01-30 14:37 | Closed | CMS | CMSINSP | ORANGEVILLE | BHUNTER |  | 2024-06-07 10:49
3.1 | WTG-0038-NDG0-0000 | 3262523 | CMS sensor | 2024-01-30 14:42 | Closed | CMS | CMSINSP | ORANGEVILLE | BHUNTER |  | 2024-09-18 15:15
9 | SITE-GOLDP | 2808338 | GEARBOX, FOUR PHASE OIL CHANGE - RENEW | 2022-02-28 12:59 | Ready to Schedule | GBXOIL | GBXOILCHG | GOLDEN PLAINS | KBJORKLUND |  | 2022-02-28 13:19
4 | WTG-0087-0000 | 2809877 | GEARBOX OIL Leak, Replace Filter Pot Drain Valve | 2022-03-01 10:14 | Closed | GBXOIL | GBXOILLEAK | FORWARD | DMONROE |  | 2022-03-18 07:03
9 | GBX-00100 | 2810277 | Plymouth SH GBX Oil Changeout | 2022-03-01 14:34 | Closed | GBXOIL | SVCS-GBXOILCHG | PLYMOUTH | ADUNBAR |  | 2022-08-06 12:34
5 | WTG-0038-0000 | 2813529 | CMS Troubleshoot (Invenergy Request non-GE) | 2022-03-08 10:20 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | CPRUIT |  | 2023-03-30 15:43
4 | WTG-0027-0000 | 2815627 | GEARBOX, Replace Yellow Hose | 2022-03-15 15:04 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2022-09-26 08:56
2 | WTG-0010-NDGP-0000 | 2904264 | GBX Oil Maintenance | 2022-03-29 12:32 | Closed | GBXOIL | ADMIN | MAVERICK | CTSOTIGH |  | 2022-04-18 16:24
2 | WTG-0048-0000 | 2904279 | Oil cooler motor bearings are failing | 2022-03-29 15:51 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2022-04-10 18:02
2 | WTG-0040-0000 | 2908364 | CMS Gearbox Borescope | 2022-04-05 09:57 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | RTRITES |  | 2022-04-15 12:07
2 | WTG-0045-0000 | 2908365 | CMS Gearbox Borescope | 2022-04-05 09:58 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | RTRITES |  | 2022-04-15 12:07
9 | WTG-0447-0000 | 2921042 | GEARBOX, OIL CHANGE | 2022-04-18 13:48 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | RTROWBRIDGE |  | 2024-06-14 09:51
4 | WTG-0012-0000 | 2924811 | GEARBOX OIL, Replace primary GBX oil filter | 2022-04-28 14:38 | Closed | GBXOIL | GBXFILTINS | FORWARD | ALANGKAU |  | 2022-08-29 10:29
2 | GBX-00036 | 2928070 | GEARBOX OIL, Particle counter troubleshooting | 2022-05-05 10:32 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | CBILLIG |  | 2022-06-24 08:34
1 | WTG-0D01-0000 | 2929381 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2022-05-09 13:13 | Closed | GBXOIL | GBXOILCOOL | HIGH SHELDON | ECOPELAND |  | 2022-05-17 13:44
5 | WTG-0057-0000 | 2929290 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-05-09 09:34 | Closed | CMS | CMSTRBLSHOOT | MAVERICK | CBILLIG |  | 2023-03-27 12:00
2 | GBX-00060 | 2931232 | CMS Gearbox Borescope | 2022-05-13 17:08 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | CBILLIG |  | 2022-05-18 13:22
5 | WTG-0004-0000 | 2931632 | Replace green hose | 2022-05-16 13:08 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-03-27 10:34
5 | WTG-0004-0000 | 2931633 | GEARBOX OIL, Add/Top-Off | 2022-05-16 13:10 | Closed | GBXOIL | GBXOILADD | FORWARD | DMONROE |  | 2022-11-08 06:13
1 | WTG-0002-TDTA-0000 | 2931837 | Replace DTA Cooling Fan | 2022-05-17 10:19 | Closed | GBXOIL | GBXOILCOOL | GRAND RIDGE | RHAYS |  | 2022-06-09 14:13
2 | WTG-0029-0000 | 3220608 | CMS Gearbox Borescope | 2023-11-07 11:34 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARRON |  | 2023-11-11 09:21
4 | WTG-0002C-0000 | 2935909 | Replace blue hose | 2022-05-19 10:41 | Closed | GBXOIL | GBXOILLEAK | FORWARD | DMONROE |  | 2023-11-14 10:59
1 | GEN-02021 | 2937192 | CMS Generator Bearing Check | 2022-05-23 10:11 | Closed | CMS | CMSGENB | TRAVERSE | CBILLIG |  | 2023-03-16 15:36
2 | GBX-00055 | 2938151 | CMS Gearbox Borescope | 2022-05-25 14:21 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2023-03-13 11:45
2 | WTG-0042-NDG0-0000 | 2938854 | CMS Gearbox Borescope | 2022-05-27 11:12 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | CBILLIG |  | 2022-07-21 11:02
2 | GBX-00083 | 2942222 | CMS Gearbox Borescope | 2022-06-06 14:43 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | CBILLIG |  | 2022-06-21 08:33
2 | WTG-0052-NDGP-0000 | 2944881 | Secondary filter system pump replacement | 2022-06-13 13:33 | Closed | GBXOIL | GBXFILTINS | VANTAGE | CCUSACK |  | 2024-05-02 10:27
4 | WTG-0233-0000 | 3037789 | GEARBOX OIL, Fix oil leak | 2022-10-24 16:05 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | THOLZ |  | 2023-05-15 12:59
1 | GBX-00007 | 2946989 | GEARBOX OIL, Particle counter installation | 2022-06-17 15:55 | Closed | GBXOIL | GBXPARTINS | SANTA RITA EAST | CBILLIG |  | 2022-06-22 08:17
2 | SITE-VWEC | 2950178 | GEARBOX OIL, Add/Top-Off | 2022-06-27 15:07 | Closed | GBXOIL | GBXOILADD | VANTAGE | CCUSACK |  | 2022-06-27 15:10
5 | WTG-0010-0000 | 2950252 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:43 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-07-08 11:17
5 | WTG-0100-0000 | 2950253 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:43 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-07-12 11:04
5 | WTG-0101-0000 | 2950254 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:43 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-08-15 11:49
5 | WTG-0017-0000 | 2950264 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-13 09:16
5 | WTG-0002-0000 | 2950265 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-01-12 10:04
5 | WTG-0020-0000 | 2950266 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-13 07:19
5 | WTG-0021-0000 | 2950267 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-12-07 10:20
5 | WTG-0022-0000 | 2950268 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-07-08 11:39
5 | WTG-0035-0000 | 2950277 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2024-09-05 07:38
5 | WTG-0036-0000 | 2950278 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-08-15 06:46
5 | WTG-0041-0000 | 2950279 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2024-08-29 07:23
5 | WTG-0001-0000 | 2950251 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:43 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-07-12 11:06
5 | WTG-0102-0000 | 2950255 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:43 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG
5 | WTG-0103-0000 | 2950256 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:43 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-08-15 11:48
5 | WTG-0011-0000 | 2950257 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:43 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-04 15:36
5 | WTG-0012-0000 | 2950258 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-08-15 11:48
5 | WTG-0013-0000 | 2950259 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-05 15:53
5 | WTG-0014-0000 | 2950260 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-08-15 11:47
5 | WTG-0015-0000 | 2950261 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-22 07:24
5 | WTG-0016-0000 | 2950263 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-25 18:39
4 | WTG-0086-0000 | 2955179 | Gearbox, Replace Blue Hose | 2022-07-06 11:47 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-08-02 09:52
5 | GBX-00079 | 2965481 | CMS HSS Check | 2022-07-22 15:02 | Closed | CMS | CMSHSS | SANTA RITA EAST | CBILLIG |  | 2022-08-26 10:53
1 | WTG-0021-0000 | 2968115 | GEARBOX OIL, Fix oil leak | 2022-07-27 14:23 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | OLAM |  | 2022-08-05 14:49
2 | WTG-0080-NDG0-0000 | 2972831 | Borescope gearbox | 2022-08-05 09:23 | Closed | CMS | CMSGBXBORE | MAVERICK | MWEBER |  | 2022-08-09 07:30
1 | WTG-0035-NDG0-0000 | 2972852 | EM: Gearbox bearing overtemperature | 2022-08-05 09:59 | Closed | GBXOIL | EM80 | BLOOMING GROVE | JDISS |  | 2022-08-22 16:01
1 | GBX-000036 | 2990754 | EM: Gearbox oil level warning | 2022-08-17 16:39 | Closed | GBXOIL | EM225 | GUNSIGHT | FMORALES |  | 2022-08-25 15:39
5 | WTG-0072-0000 | 3011631 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-02 13:01 | In Progress | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG
2 | WTG-00G2-NDD0-0000 | 3016492 | CMS Generator Bearing Check | 2022-09-12 10:12 | Cancelled | CMS | CMSGENB | TATANKA RIDGE | CBILLIG |  | 2023-03-08 11:11
1 | WTG-0078-0000 | 3018976 | GEARBOX OIL, Fix oil leak | 2022-09-15 14:13 | Closed | GBXOIL | GBXOILLEAK | GRATIOT | JCAPEN |  | 2022-09-16 10:11
2 | WTG-0129-0000 | 3018979 | GEARBOX OIL, Fix oil leak | 2022-09-15 14:15 | Closed | GBXOIL | GBXOILLEAK | GRATIOT | JCAPEN |  | 2022-10-17 12:57
2 | GBX-00067 | 3020611 | GEARBOX OIL, Particle counter troubleshooting | 2022-09-19 14:58 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | CBILLIG |  | 2022-09-27 07:40
2 | GBX-00102 | 3024818 | CMS Gearbox Borescope | 2022-09-22 10:48 | Closed | CMS | CMSGBXBORE | PLYMOUTH | CBILLIG |  | 2023-01-30 14:46
3 | 120D303 | 3026212 | Inspect fan and motor for debris build up. | 2022-09-25 20:32 | Closed | CMS |  | NELSON | LZIMMERMAN |  | 2023-04-26 15:56
2 | WTG-0028-0000 | 3027668 | CMS Gearbox Borescope | 2022-09-29 14:42 | Closed | CMS | CMSGBXBORE | UPSTREAM | CMORRISON |  | 2023-08-09 10:04
4 | WTG-0006-0000 | 3028169 | GEARBOX OIL, Fix oil leak secondary needs o ring | 2022-09-30 10:37 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2022-12-09 10:37
2 | WTG-3018-0000 | 3030416 | CMS Gearbox Borescope | 2022-10-05 18:06 | Closed | CMS | CMSGBXBORE | TRAVERSE | ALATERZA |  | 2023-02-23 07:55
1 | WTG-0038-0000 | 3031186 | Secondary oil filtration, Fix oil leak | 2022-10-07 09:37 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | TWIEDEMEIER |  | 2023-09-08 11:26
2 | GBX-00067 | 3033153 | CMS Gearbox Borescope | 2022-10-11 16:32 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | CBILLIG |  | 2022-10-27 09:22
2 | WTG-0061-0000 | 3035332 | CMS Gearbox Borescope | 2022-10-14 15:10 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | JWWILSON |  | 2022-10-17 13:38
9 | WTG-0012-0000 | 3038348 | GEARBOX, Oil Change | 2022-10-26 09:01 | Cancelled | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2023-02-08 16:04
9 | WTG-0014-0000 | 3038349 | GEARBOX, Oil Change | 2022-10-26 09:03 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2022-11-21 13:03
9 | WTG-0021-0000 | 3038350 | GEARBOX, Oil Change | 2022-10-26 09:04 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2022-11-21 13:08
9 | WTG-0025-0000 | 3038351 | GEARBOX, Oil Change | 2022-10-26 09:04 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2023-02-28 15:58
9 | WTG-0061-0000 | 3038352 | GEARBOX, Oil Change | 2022-10-26 09:05 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2022-11-30 08:44
9 | WTG-0062-0000 | 3038353 | GEARBOX, Oil Change | 2022-10-26 09:06 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2022-11-30 08:43
5 | WTG-2069-0000 | 3038407 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-10-26 12:58 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-21 14:34
9 | WTG-0011-0000 | 3041020 | GEARBOX, Oil Change | 2022-11-02 09:19 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2022-11-21 13:06
4 | WTG-0040A-0000 | 2927785 | GEARBOX OIL, Replace primary GBX oil filter | 2022-05-04 08:04 | Closed | GBXOIL | GBXFILTELEM | FORWARD | JLAWRENCE |  | 2022-08-01 09:15
1 | WTG-0061-NDG0-0000 | 2928472 | Gearbox Oil Add | 2022-05-05 16:56 | Closed | GBXOIL | BLANK | JUDITH GAP | CWERDIN |  | 2022-11-04 12:24
2 | WTG-00E1-NDB0-0000 | 2938892 | CMS Main Bearing Borescope | 2022-05-27 13:28 | Closed | CMS | CMSMBBORE | TATANKA RIDGE | CBILLIG |  | 2022-09-14 10:14
2 | WTG-0015-NDG0-0000 | 2944200 | GBX borescope | 2022-06-12 19:14 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | MWILSON |  | 2022-07-22 07:01
5 | WTG-2051-0000 | 2947966 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-21 10:16 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-13 12:18
2 | WTG-00C8-0000 | 2949430 | CMS Main Bearing Borescope | 2022-06-24 16:00 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | MMATHER |  | 2022-07-01 09:43
5 | WTG-0023-0000 | 2950269 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-18 09:30
5 | WTG-0025-0000 | 2950270 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-07-11 10:07
5 | WTG-0026-0000 | 2950271 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-18 10:18
5 | WTG-0027-0000 | 2950272 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-07-29 17:19
5 | WTG-0028-0000 | 2950273 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-10-25 10:42
5 | WTG-0030-0000 | 2950274 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2025-03-17 15:09
5 | WTG-0033-0000 | 2950275 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-08-22 12:11
5 | WTG-0034-0000 | 2950276 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-27 16:44 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2022-09-06 11:50
2 | BRG-000087 | 2953041 | CMS Main Bearing Borescope | 2022-06-30 13:03 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | CBILLIG |  | 2022-07-14 08:04
5 | GBX-00094 | 2953042 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-30 13:09 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-07-08 07:39
5 | WTG-1018-NDG0-0000 | 2972056 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-04 09:39 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-04-13 15:04
5 | WTG-0101-0000 | 2988353 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-10 10:37 | Cancelled | CMS | CMSTRBLSHOOT | DEUEL HARVEST | CBILLIG |  | 2022-09-21 11:07
2 | WTG-0030-0000 | 2990838 | CMS Gearbox Borescope | 2022-08-18 09:14 | Closed | CMS | CMSMBBORE | MCADOO | TRUDE |  | 2022-08-22 09:08
9 | WTG-0082-0000 | 3066049 | GEARBOX, Oil Change | 2023-01-09 09:24 | Closed | GBXOIL | GBXOILCHG | BETHEL | AALEMAN |  | 2023-05-08 16:26
2 | SITE-FSO | 2998347 | WEC - Upstream - Borescopes - 5 WTGs | 2022-08-23 18:06 | Closed | CMS | CMSGBXBORE | FSO | CBRIESE |  | 2024-05-10 08:49
1 | WTG-0328-0000 | 3010281 | GEARBOX OIL, Particle counter removal | 2022-08-31 15:31 | Closed | GBXOIL | GBXPARTREM | BISHOP HILL III | MBELCHER |  | 2022-08-31 15:35
1 | GBX-000036 | 3010297 | EM: Gearbox oil level warning | 2022-08-31 16:18 | Closed | GBXOIL | EM225 | GUNSIGHT | DKEETON |  | 2022-11-07 15:02
1 | WTG-0018-0000 | 3020474 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2022-09-19 08:21 | Closed | GBXOIL | GBXOILCOOL | BUCKEYE | ZNASH |  | 2023-02-13 14:47
2 | WTG-0037-0000 | 3024845 | GEARBOX OIL, Secondary oil pump leak | 2022-09-22 12:35 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | TWIEDEMEIER |  | 2022-10-11 07:58
3 | 220D305 | 3026213 | Verify fan blades are not making contact with shroud. | 2022-09-25 20:32 | Closed | CMS |  | NELSON | LZIMMERMAN |  | 2023-05-03 15:32
2 | 011D192 | 3026214 | Replace pump bearings | 2022-09-25 20:32 | Rejected | CMS |  | NELSON | LZIMMERMAN |  | 2024-05-22 13:47
2 | 011D193 | 3026215 | Replace Pump Bearings | 2022-09-25 20:32 | Rejected | CMS |  | NELSON | LZIMMERMAN |  | 2024-05-22 13:47
2 | WTG-0024-0000 | 3030501 | GEARBOX OIL, Oil Sample | 2022-10-06 09:14 | Closed | GBXOIL | GBXOILSAMP | BUCKEYE | LDURLER |  | 2023-02-23 13:53
5 | WTG-0074A-NDGP-0000 | 3030467 | Drill inspection hole for gear oil pump coupler | 2022-10-06 06:58 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-04-20 15:35
4 | WTG-0203B-0000 | 3033105 | Change GBX Desiccant | 2022-10-11 13:03 | Closed | GBXOIL | GBXOILADD | FORWARD | DMONROE |  | 2023-01-25 16:51
2 | BRG-000007 | 3033134 | CMS Main Bearing Borescope | 2022-10-11 15:51 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | CBILLIG |  | 2022-11-03 07:49
4 | WTG-0035-0000 | 3038508 | Replace Yellow Gearbox Oil Hose | 2022-10-26 15:11 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2023-04-03 16:21
2 | GBX-00076 | 3041238 | CMS Gearbox Borescope | 2022-11-02 13:34 | Closed | CMS | CMSGBXBORE | PLYMOUTH | CBILLIG |  | 2023-05-25 09:38
4 | WTG-0042-0000 | 3041245 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2022-11-02 12:32 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2022-11-08 07:58
9 | WTG-0094-0000 | 3042511 | GEARBOX, Oil Change | 2022-11-07 12:24 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-02-10 06:53
9 | WTG-0006-0000 | 3046074 | GEARBOX, Oil Change | 2022-11-16 09:47 | Closed | GBXOIL | GBXOILCHG | BETHEL | MRAHMAN |  | 2022-11-30 08:44
2 | WTG-0340-NDG0-0000 | 3052545 | CMS Main Bearing Borescope | 2022-12-01 16:31 | Closed | CMS | CMSMBBORE | BISHOP HILL III | CBILLIG |  | 2023-02-13 14:08
2 | WTG-0052-0000 | 3053803 | CMS Gearbox Borescope | 2022-12-05 14:10 | Closed | CMS | CMSGBXBORE | BETHEL | ACHAVIRA |  | 2022-12-05 22:17
2 | WTG-0010-NDB0-0000 | 3053802 | CMS Main Bearing Borescope | 2022-12-05 14:06 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | MWILSON |  | 2022-12-07 17:05
9 | WTG-0009-0000 | 3053978 | GEARBOX, Oil Change | 2022-12-06 09:22 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-02-08 14:42
9 | WTG-0110-0000 | 3054611 | GEARBOX, Oil Change | 2022-12-07 14:55 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2022-12-22 13:08
9 | WTG-0049-0000 | 3055484 | GEARBOX, Oil Change | 2022-12-12 08:33 | Closed | GBXOIL | GBXOILCHG | BETHEL | TMILLER2 |  | 2023-03-20 12:32
5 | GBX-00088 | 3056170 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-12-12 15:46 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2023-01-03 10:35
9 | WTG-0033-0000 | 3056173 | GEARBOX, Oil Change | 2022-12-12 15:58 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-03-15 15:04
9 | WTG-0036-0000 | 3056174 | GEARBOX, Oil Change | 2022-12-12 16:00 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-01-04 15:34
1 | WTG-0043-0000 | 3057504 | GEARBOX OIL, Fix oil leak | 2022-12-15 12:11 | Closed | GBXOIL | GBXOILLEAK | STANTON | JJPADILLA |  | 2022-12-15 15:33
1 | WTG-0039-0000 | 3057505 | GEARBOX OIL, Fix oil leak | 2022-12-15 12:48 | Closed | GBXOIL | GBXOILLEAK | STANTON | JJPADILLA |  | 2022-12-15 15:33
2 | WTG-0093-0000 | 3057866 | GEARBOX OIL, Add/Top-Off | 2022-12-16 14:30 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | SOTTO |  | 2023-06-16 15:36
5 | WTG-0044-0000 | 3058368 | GEARBOX OIL, Replace oil cooler plenum | 2022-12-19 15:01 | Ready to Schedule | GBXOIL | GBXOILCOOL | SUNDANCE | SDUNAVANT
2 | WTG-0032-0000 | 3061290 | CMS Main Bearing Borescope | 2022-12-29 09:49 | Closed | CMS | CMSMBBORE | GOLDTHWAITE | OLAM |  | 2023-02-21 15:58
4 | WTG-0081-0000 | 3061516 | Replace Secondary Pump Shaft Seal | 2022-12-29 16:37 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2023-01-30 11:03
2 | WTG-0093-NDB0-0000 | 3064234 | CMS Main Bearing Borescope | 2023-01-04 16:14 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | NFALASZ |  | 2023-01-20 08:57
2 | WTG-0088-NDB0-0000 | 3064235 | CMS Main Bearing Borescope | 2023-01-04 16:15 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | NFALASZ |  | 2023-01-20 08:57
9 | WTG-0083-0000 | 3066021 | GEARBOX, Oil Change | 2023-01-09 09:26 | Closed | GBXOIL | GBXOILCHG | BETHEL | NHERRERA |  | 2023-05-02 09:32
1 | WTG-0034-0000 | 3068516 | GEARBOX OIL, Fix oil leak | 2023-01-14 16:38 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | TWIEDEMEIER |  | 2023-01-19 12:38
1 | GBX-00037 | 3070626 | GEARBOX OIL, Particle counter installation | 2023-01-20 13:55 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | MWILSON |  | 2023-01-20 17:32
1 | GBX-00035 | 3070627 | GEARBOX OIL, Particle counter installation | 2023-01-20 14:03 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | MWILSON |  | 2023-01-20 17:32
2 | WTG-0304-NDB0-0000 | 3071322 | CMS Main Bearing Borescope | 2023-01-24 11:06 | Closed | CMS | CMSMBBORE | BISHOP HILL III | CBILLIG |  | 2023-01-31 15:07
2 | WTG-0110-NDG0-0000 | 3072034 | CMS Gearbox Borescope | 2023-01-25 10:52 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2023-08-17 09:24
5 | WTG-0061-NTV0-0000 | 3072196 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-25 16:12 | Closed | CMS | CMSTRBLSHOOT | BETHEL | ABARNDT |  | 2023-12-01 14:33
1 | WTG-0065-NDD0-0000 | 3072198 | CMS Generator Bearing Check | 2023-01-25 16:19 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-03-20 14:48
2 | WTG-0G10-0000 | 3074181 | GEARBOX OIL, Particle counter troubleshooting | 2023-01-31 09:48 | Closed | GBXOIL | GBXPARTTS | BEECH RIDGE | CBILLIG |  | 2023-09-12 08:30
1 | WTG-00B1-NDGP-0000 | 3078673 | poseidon gearbox sensor install | 2023-02-06 15:33 | Cancelled | GBXOIL | GBXPARTINS | COYOTE RIDGE | SVEACH |  | 2023-04-25 12:01
2 | WTG-0055-NDB0-0000 | 3078637 | CMS Main Bearing Borescope and Purge per GE request | 2023-02-06 14:37 | Closed | CMS | CMSINSP | GOLDTHWAITE | KMERRITT |  | 2023-02-21 15:49
1 | WTG-00E5-0000 | 3078690 | Poseidon Install | 2023-02-06 17:00 | Closed | GBXOIL | GBXPARTINS | TATANKA RIDGE | ECONERS |  | 2023-02-28 16:15
1 | WTG-00L1-0000 | 3078691 | Poseidon Install | 2023-02-06 17:00 | Closed | GBXOIL | GBXPARTINS | TATANKA RIDGE | ECONERS |  | 2023-02-28 16:14
1 | WTG-00H5-0000 | 3078692 | Poseidon Install | 2023-02-06 17:01 | Closed | GBXOIL | GBXPARTINS | TATANKA RIDGE | ECONERS |  | 2023-02-28 16:14
5 | WTG-0055-0000 | 3078687 | Main Bearing Inspection | 2023-02-06 16:49 | Closed | CMS | CMSMB | MAVERICK | VPHIASIRIPANYO |  | 2024-04-29 14:28
5 | WTG-0003A-0000 | 3078713 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-02-06 13:47 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-02-07 15:56
1 | WTG-00P3-0000 | 3078688 | Poseidon Install | 2023-02-06 16:58 | Closed | GBXOIL | GBXPARTINS | TATANKA RIDGE | ECONERS |  | 2023-02-28 16:15
5 | WTG-0055A-0000 | 3085915 | Add 5 gallons next visit | 2023-02-21 14:06 | Closed | GBXOIL | GBXOILADD | FORWARD | TBUYESKE |  | 2023-04-03 16:23
3 | WTG-0086-NTV0-0000 | 3085873 | CMS Trouble Shoot (Invenergy request, non-GE) WC# 7011212 | 2023-02-21 11:56 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | ABARNDT |  | 2023-07-27 10:52
1 | WTG-0039-0000 | 3080292 | Gearbox oil sample | 2023-02-10 10:47 | Closed | GBXOIL | GBXOILSAMP | MAVERICK | VPHIASIRIPANYO |  | 2023-04-07 10:20
5 | WTG-0104-0000 | 3080377 | CMS HSS Check | 2023-02-10 12:10 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-09-19 17:18
2 | WTG-0046-NDB0-0000 | 3081515 | Main Bearing Inspection | 2023-02-13 15:20 | Closed | CMS | CMSMBBORE | MAVERICK | JEROMAN |  | 2023-03-27 11:55
2 | WTG-0001-NDB0-0000 | 3083847 | CMS Main Bearing Borescope | 2023-02-14 13:57 | Closed | CMS | CMSMBBORE | MAVERICK | JEROMAN |  | 2023-03-27 11:54
3 | GEN-000004 | 3086218 | Gen Bearing Replacement | 2023-02-22 09:16 | Closed | CMS | CMSGENB | STANTON | JBANNISTER |  | 2023-03-01 08:57
4 | WTG-0016-NTV0-0000 | 3086237 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-02-22 09:42 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-02-27 12:33
5 | WTG-0087-0000 | 3086316 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-02-22 10:53 | Closed | GBXOIL | GBXOILADD | FORWARD | TBUYESKE |  | 2023-03-07 11:35
1 | WTG-1081-0000 | 3087214 | GEARBOX OIL, Fix oil leak | 2023-02-24 15:49 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | QCROUSE |  | 2023-06-05 10:27
5 | WTG-0053-0000 | 3088101 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2023-02-28 10:41 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-10-31 10:01
4 | WTG-0058-0000 | 3088103 | Replace Orange Oil Hose | 2023-02-28 12:53 | Closed | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE |  | 2023-06-09 12:39
3.1 | WTG-0007-NDB0-0000 | 3088012 | CMS Main Bearing Check | 2023-02-28 12:27 | Closed | CMS | CMSMB | BETHEL | CBILLIG |  | 2024-01-04 08:42
4 | WTG-0028-0000 | 3089158 | Replace shaft seal on secondary filter pump | 2023-03-01 14:31 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2023-06-09 12:39
1 | WTG-0019-0000 | 3089506 | GEARBOX OIL, Fix oil leak WC# 6118416 | 2023-03-02 08:55 | Closed | GBXOIL | GBXOILLEAK | THUNDERHEAD | CWERNER |  | 2023-05-15 13:02
1 | WTG-1079-0000 | 3092672 | GEARBOX OIL, Fix oil leak | 2023-03-03 07:17 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | QCROUSE |  | 2023-06-05 10:23
2 | WTG-0067-0000 | 3045578 | GEARBOX OIL, Add/Top-Off | 2022-11-14 15:38 | Cancelled | GBXOIL | GBXOILADD | JUDITH GAP | TWIEDEMEIER |  | 2023-02-17 09:47
4 | WTG-0008-0000 | 3052377 | GEARBOX OIL, Add/Top-Off about 10 gallons | 2022-12-01 13:11 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-12-19 09:47
9 | WTG-0030-0000 | 3052721 | GEARBOX, Oil Change | 2022-12-02 07:49 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2022-12-05 22:21
1 | WTG-0013-0000 | 3052566 | GEARBOX OIL Cooler, Fix oil leak | 2022-12-01 16:52 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | ZNASH |  | 2024-10-04 13:45
2 | WTG-0083-0000 | 3053240 | GEARBOX OIL, Add/Top-Off | 2022-12-02 17:33 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | SOTTO |  | 2023-06-05 16:55
5 | WTG-00B5-NDG0-0000 | 3053231 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-12-02 17:14 | Closed | CMS | CMSTRBLSHOOT | COYOTE RIDGE | WDEAS |  | 2023-09-08 11:18
1 | BRG-000071 | 3054138 | CMS Main Bearing Borescope | 2022-12-06 15:53 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | CBILLIG |  | 2022-12-09 08:40
9 | WTG-0050-0000 | 3055483 | GEARBOX, Oil Change | 2022-12-12 08:31 | Closed | GBXOIL | GBXOILCHG | BETHEL | TMILLER2 |  | 2022-12-30 12:06
9 | WTG-0057-0000 | 3056156 | GEARBOX, Oil Change | 2022-12-12 15:12 | Closed | GBXOIL | GBXOILCHG | BETHEL | MTERRONES |  | 2023-02-03 11:05
5 | WTG-0211A-NDGP-0000 | 3058520 | Replace red spider | 2022-12-20 08:34 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-07-20 11:54
4 | WTG-0211A-NDG0-0000 | 3058521 | GEARBOX OIL, Add/Top-Off 2gals | 2022-12-20 08:45 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2023-01-30 11:39
5 | WTG-0018-0000 | 3061463 | 949_Main Bearing Auto Lube Grease Level Low | 2022-12-29 15:49 | Cancelled | CMS | CMSMB | MAVERICK | BPETERMAN |  | 2023-03-21 14:45
1 | WTG-0072-0000 | 3063393 | Change Gearbox Hose | 2023-01-03 15:52 | Cancelled | GBXOIL | GBXOILLEAK | BETHEL | JGARLAND |  | 2023-10-18 10:45
9 | WTG-0077-0000 | 3064326 | GEARBOX, Oil Change | 2023-01-05 08:59 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-04-26 16:01
2 | WTG-00S6-0000 | 3134562 | CMS Main Bearing Borescope | 2023-05-31 12:48 | Closed | CMS | CMSMBBORE | TATANKA RIDGE | ABARNDT |  | 2023-07-06 10:01
1 | WTG-0019-NDGP-0000 | 3140574 | Clean Oil Cooler Radiator | 2023-06-08 11:44 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | CADAMS |  | 2023-06-08 15:14
1 | WTG-0023-0000 | 3068322 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2023-01-13 13:34 | Closed | GBXOIL | GBXOILCOOL | ORANGEVILLE | ECOPELAND |  | 2023-01-18 12:25
2 | WTG-0040-0000 | 3068492 | MB inspection | 2023-01-14 09:24 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | CCAMPBELL |  | 2023-01-20 08:56
2 | WTG-0056-0000 | 3068585 | MB INSPECTION | 2023-01-15 16:03 | Cancelled | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-04-26 07:38
2 | WTG-0074-0000 | 3068586 | MB INSPECTION | 2023-01-15 16:04 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-01-20 08:56
2 | WTG-0075-0000 | 3068587 | MB INSPECTION | 2023-01-15 16:06 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-01-20 08:56
2 | WTG-0077-0000 | 3068588 | MB INSPECTION | 2023-01-15 16:07 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-03-15 08:32
2 | WTG-0078-0000 | 3068589 | MB INSPECTION | 2023-01-15 16:07 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-03-27 12:13
1 | WTG-0027-NDGP-0000 | 3071308 | Cracked Oil Bypass Hose | 2023-01-24 09:52 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MCONDON |  | 2023-03-16 14:22
5 | WTG-0303-NT00-0000 | 3071312 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-24 10:24 | Cancelled | CMS | CMSTRBLSHOOT | BISHOP HILL III | CBILLIG |  | 2023-03-02 10:02
5 | WTG-0302-NT00-0000 | 3071314 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-24 10:26 | Cancelled | CMS | CMSTRBLSHOOT | BISHOP HILL III | CBILLIG |  | 2023-02-02 09:27
5 | WTG-0039-NDB0-0000 | 3071331 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-24 11:53 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | CBILLIG |  | 2023-07-14 09:46
5 | WTG-0042-NDB0-0000 | 3071332 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-24 11:55 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | CBILLIG |  | 2023-07-14 09:56
5 | WTG-0081-NDD0-0000 | 3071333 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-24 11:55 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | CBILLIG |  | 2024-03-07 13:01
1 | WTG-0032-0000 | 3071176 | GEARBOX OIL, Particle counter installation | 2023-01-23 15:39 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | JDISS |  | 2023-01-27 06:28
2 | WTG-0029-NDG0-0000 | 3072023 | CMS Gearbox Borescope | 2023-01-25 10:32 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2023-04-26 07:33
5 | WTG-0064-NTV0-0000 | 3073720 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-30 09:33 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-02-13 11:33
2 | WTG-0108-NDD0-0000 | 3073724 | CMS Generator Bearing Check | 2023-01-30 09:47 | Closed | CMS | CMSGENB | SANTA RITA EAST | ABARNDT |  | 2023-03-16 08:22
2 | WTG-0086-0000 | 3073730 | CMS Gearbox Borescope | 2023-01-30 09:24 | Closed | CMS | CMSGBXBORE | BETHEL | ACHAVIRA |  | 2023-01-31 10:39
5 | WTG-0040-NTV0-0000 | 3073743 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-30 10:43 | Closed | CMS | CMSTRBLSHOOT | DEUEL HARVEST | ABARNDT |  | 2023-12-27 11:27
4 | WTG-0009-0000 | 3079382 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2023-02-08 10:08 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-04-28 12:45
1 | WTG-0047-NDGP-0000 | 3085902 | GEARBOX OIL, Fix oil leak | 2023-02-20 13:39 | Closed | GBXOIL | GBXOILLEAK | VANTAGE | PMASAKI |  | 2023-02-23 15:21
5 | WTG-0090-0000 | 3085912 | GEARBOX OIL, Add/Top-Off 5 gal | 2023-02-21 12:58 | Closed | GBXOIL | GBXOILADD | FORWARD | DMONROE |  | 2023-07-20 12:04
1 | WTG-0079-NY00-0000 | 3085040 | GEARBOX OIL, Fix oil leak | 2023-02-17 15:52 | Closed | GBXOIL | GBXOILLEAK | THUNDERHEAD | CWERNER |  | 2023-11-27 15:20
5 | WTG-0006-NDG0-0000 | 3087132 | GEARBOX OIL, Particle counter troubleshooting | 2023-02-24 12:06 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-04-06 11:02
5 | WTG-0040-NDG0-0000 | 3087133 | GEARBOX OIL, Particle counter troubleshooting | 2023-02-24 12:11 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-03-27 13:54
5 | WTG-0060-NDG0-0000 | 3087135 | GEARBOX OIL, Particle counter troubleshooting | 2023-02-24 12:13 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-03-27 13:54
5 | WTG-0053-0000 | 3088100 | Replace Purple GBX Hose | 2023-02-28 10:40 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2023-10-31 10:00
5 | WTG-0009-NDG0-0000 | 3088010 | CMS HSS Check | 2023-02-28 12:23 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-11-07 16:11
5 | WTG-0007-NDG0-0000 | 3088011 | CMS HSS Check | 2023-02-28 12:27 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-11-07 09:07
9 | WTG-0A04-0000 | 3092786 | gearbox filter divider missing | 2023-03-03 10:17 | Closed | GBXOIL | SVCS-GBXOILCHG | JAYHAWK | CHORN |  | 2024-10-14 11:22
5 | WTG-0027-0000 | 3094923 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2023-03-08 14:30 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-08-07 09:21
2 | WTG-1129-NDD0-0000 | 3093477 | CMS Generator Bearing Check | 2023-03-06 09:27 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2024-02-19 14:26
2 | WTG-0012-NDG0-0000 | 3094851 | GEARBOX OIL, Add/Top-Off | 2023-03-08 12:39 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2023-06-28 16:18
1 | WTG-0012-NDGP-0000 | 3094831 | Gearbox radiator is leaking | 2023-03-08 12:26 | Ready to Schedule | GBXOIL | GBXOILCOOL | VANTAGE | PMASAKI
2 | WTG-0011-NDG0-0000 | 3094848 | GEARBOX OIL, Add/Top-Off | 2023-03-08 12:36 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2023-03-09 11:51
4 | WTG-0059A-0000 | 3101211 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-03-20 10:54 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-05-17 12:59
5 | WTG-1110-0000 | 3103414 | CMS HSS Check | 2023-03-28 08:16 | Closed | CMS | CMSHSS | TRAVERSE | HBELTRAN |  | 2023-06-05 11:30
4 | WTG-0013-0000 | 3104308 | GEARBOX OIL, Add/Top-Off 5 gallons and replace desiccant | 2023-03-28 12:39 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-10-02 11:40
5 | WTG-0019A-NDGD-0000 | 3104334 | Replace gearbox deisicant | 2023-03-28 15:35 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-04-03 16:23
1 | WTG-0029-0000 | 3104829 | CMS Main Bearing Borescope | 2023-03-29 12:51 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2023-04-17 11:32
1 | WTG-1085-0000 | 3104845 | GEARBOX OIL, Fix oil leak | 2023-03-29 13:27 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | JDKEY |  | 2023-06-05 10:34
2 | WTG-0334-NDG0-0000 | 3106481 | CMS Gearbox Borescope | 2023-03-31 14:09 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | CBILLIG |  | 2023-05-01 08:42
3.1 | WTG-0318-NDG0-0000 | 3106469 | CMS HSS Check | 2023-03-31 13:58 | Closed | CMS | CMSHSS | BISHOP HILL III | CBILLIG |  | 2023-04-13 14:35
2 | WTG-0003-0000 | 3109711 | GEARBOX OIL, Add/Top-Off | 2023-04-06 16:35 | Closed | GBXOIL | GBXOILADD | GORDON BUTTE | TWIEDEMEIER |  | 2023-08-30 12:20
3 | WTG-0001-0000 | 3110510 | CMS Trouble Shoot (Invenergy request, non-GE)/ SR# 6252998 | 2023-04-10 11:01 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2023-08-15 09:20
3 | WTG-0033-0000 | 3110514 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-10 11:05 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2023-04-20 09:14
3 | WTG-0077-0000 | 3110519 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-10 11:11 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2023-04-20 09:11
3 | WTG-0079-0000 | 3110521 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-10 11:12 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2023-04-20 09:12
5 | WTG-0032-NDD0-0000 | 3111897 | CMS Generator Bearing Check | 2023-04-11 16:02 | Closed | CMS | CMSGENB | THUNDERHEAD | CBILLIG |  | 2024-02-06 11:23
5 | WTG-0001-NDD0-0000 | 3113598 | CMS Generator Bearing Check | 2023-04-17 11:49 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-06-23 11:55
4 | WTG-0042-0000 | 3114653 | GEARBOX, winergy green hose replacement | 2023-04-19 10:22 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2023-10-23 15:16
2 | WTG-0041A-0000 | 3115231 | GEARBOX OIL, Replace seal between filter pot and bypass valve block | 2023-04-20 10:08 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2023-04-28 12:44
1 | WTG-0052-0000 | 3116897 | CMS Main Bearing Borescope | 2023-04-26 13:59 | Closed | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2023-05-18 11:30
4 | WTG-0070-0000 | 3118374 | GEARBOX OIL, Add/Top-Off 2-3 gallons | 2023-04-28 12:06 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-05-10 13:08
1 | WTG-0007-0000 | 3118413 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2023-04-28 13:52 | Closed | GBXOIL | GBXOILCOOL | UPSTREAM | THOLZ |  | 2023-06-23 10:08
4 | WTG-0048-0000 | 3118371 | Secondary Filtration System Leak | 2023-04-28 13:50 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-06-13 11:39
3 | WTG-2116-0000 | 3125671 | CMS Generator Bearing Check | 2023-05-12 11:12 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2023-05-22 12:07
1 | WTG-0088-0000 | 3125777 | GEARBOX OIL, Fix oil leak | 2023-05-12 16:31 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JTHOMAS |  | 2023-05-15 15:56
4 | WTG-0056A-NDG0-0000 | 3125676 | GEARBOX OIL, Add/Top-Off 5 gals | 2023-05-12 10:58 | Cancelled | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-05-15 07:18
1 | WTG-0022-0000 | 3125848 | GEARBOX OIL, Fix radiator leak | 2023-05-12 18:50 | Ready to Schedule | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT
1 | WTG-0086-0000 | 3127192 | GEARBOX OIL, Fix radiator leak | 2023-05-16 16:23 | In Progress | GBXOIL | GBXOILLEAK | BUCKEYE | CPOLIFKA
1 | WTG-0056-0000 | 3130032 | GEARBOX OIL, Fix radiator leak | 2023-05-19 14:56 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2024-09-20 15:19
1 | WTG-0007-0000 | 3130748 | General Inspection | 2023-05-22 16:01 | Closed | GBXOIL | GBXPARTTS | MAVERICK | JMILES |  | 2023-07-08 11:14
5 | WTG-0108-0000 | 3132468 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-25 09:16 | Closed | CMS | CMSTRBLSHOOT | DEUEL HARVEST | ABARNDT |  | 2023-08-11 09:32
3 | WTG-0019-0000 | 3132478 | CMS Trouble Shoot (Invenergy request, non-GE) / SR#6253094 | 2023-05-25 09:52 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2023-07-10 13:18
2 | WTG-00E4-NDG0-0000 | 3132525 | GEARBOX OIL, Particle counter removal | 2023-05-25 10:43 | Closed | GBXOIL | GBXPARTREM | TATANKA RIDGE | CBILLIG |  | 2023-07-24 09:32
2 | WTG-00L1-NDG0-0000 | 3132542 | GEARBOX OIL, Particle counter removal | 2023-05-25 10:44 | Closed | GBXOIL | GBXPARTREM | TATANKA RIDGE | CBILLIG |  | 2024-02-13 11:33
3.1 | WTG-0L11-NDG0-0000 | 3132543 | GEARBOX OIL, Particle counter installation | 2023-05-25 10:45 | Closed | GBXOIL | GBXPARTINS | TATANKA RIDGE | CBILLIG |  | 2023-07-24 09:32
1 | WTG-0030-0000 | 3134657 | GEARBOX OIL, Secondary filter system not working | 2023-05-31 16:18 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CPOLIFKA |  | 2024-03-14 07:46
1 | WTG-0064-0000 | 3134607 | GEARBOX OIL, Particle counter troubleshooting | 2023-05-31 14:42 | Closed | GBXOIL | GBXPARTTS | MAVERICK | JMILES |  | 2023-07-12 10:15
1 | WTG-0065-0000 | 3134667 | GEARBOX OIL, Particle counter troubleshooting | 2023-05-31 16:46 | Closed | GBXOIL | GBXPARTTS | MAVERICK | JMILES |  | 2023-07-12 10:15
1 | WTG-0086-0000 | 3150546 | Secondary oil filtration, Fix oil leak | 2023-06-29 17:04 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | SMCCLURE |  | 2023-11-06 11:11
2 | WTG-0059A-0000 | 3152633 | Winergy top box side gen fan replacement | 2023-07-05 09:18 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2023-07-17 15:21
5 | WTG-3018-0000 | 3153356 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-07-06 09:09 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-02-26 11:51
2 | 1GT2-BRG-202 | 3155245 | GT2 bearing vibration BB5 has been reading erratic. MND-20230711-0216 | 2023-07-11 12:46 | Closed | CMS |  | GRAYS HARBOR | PHUGHES |  | 2024-06-14 13:35
4 | WTG-0083-0000 | 3157466 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-07-17 14:49 | Closed | CMS | CMSTRBLSHOOT | MAVERICK | ABARNDT |  | 2023-11-09 10:57
1 | WTG-3028-0000 | 3159863 | GEARBOX OIL, Fix oil leak | 2023-07-21 12:46 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | QCROUSE |  | 2023-08-24 13:49
3 | WTG-0041-0000 | 3160647 | CMS Generator Bearing Check | 2023-07-24 13:06 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2024-01-09 10:46
2 | WTG-0082-0000 | 3160598 | CMS Main Bearing Borescope | 2023-07-24 10:33 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2023-07-27 08:52
2 | WTG-1134-0000 | 3163468 | CMS Gearbox Borescope | 2023-07-28 09:18 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2024-02-19 14:07
1 | WTG-0024-0000 | 3163541 | GEARBOX OIL, Fix oil leak | 2023-07-28 09:05 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | SMILLER |  | 2023-08-04 15:10
4.2 | WTG-0027-0000 | 3168517 | Small oil leak at flange plates between lube pump and filter pot | 2023-08-02 11:17 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2024-02-28 08:50
2 | WTG-0094-0000 | 3171353 | GEARBOX OIL, Particle counter installation | 2023-08-09 10:57 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | ABARNDT |  | 2023-08-15 06:28
2 | WTG-0001-0000 | 3171350 | GEARBOX OIL, Particle counter installation | 2023-08-09 10:54 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | ABARNDT |  | 2024-02-09 06:31
2 | WTG-0053-0000 | 3171352 | GEARBOX OIL, Particle counter installation | 2023-08-09 10:56 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | ABARNDT |  | 2024-03-29 08:34
5 | WTG-1023-0000 | 3178434 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-08-25 13:19 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
4.2 | WTG-0065-0000 | 3178468 | Moventas gasket for small inspection plate | 2023-08-25 10:32 | On Hold | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE
5 | WTG-0035-0000 | 3178435 | CMS Generator Bearing Check | 2023-08-25 13:30 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-10-05 10:31
2 | WTG-0021-0000 | 3180083 | Gen fan replacement | 2023-08-29 11:11 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-09-11 11:58
5 | WTG-0097-NALC-0000 | 3180659 | T97 CMS #3GBX sensor issues. SR# 6417524 | 2023-08-30 11:03 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | TWESTERDAHL |  | 2023-12-27 15:43
3 | WTG-1006-0000 | 3182529 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-08-31 10:37 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-01-30 13:24
3 | WTG-0008-0000 | 3185554 | CMS Generator Bearing Check | 2023-09-05 10:51 | Closed | CMS | CMSGENB | MAVERICK | ABARNDT |  | 2023-09-11 12:32
3 | WTG-0004-0000 | 3187800 | CMS Gearbox Borescope | 2023-09-08 10:15 | Closed | CMS | CMSGBXBORE | UPSTREAM | ABARNDT |  | 2023-10-23 22:34
3 | WTG-3011-0000 | 3187802 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-08 10:22 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-02-26 11:50
3 | WTG-0044-0000 | 3187717 | CMS Generator Bearing Check | 2023-09-08 09:44 | Closed | CMS | CMSGENB | UPSTREAM | ABARNDT |  | 2024-04-09 12:08
1 | WTG-0021-0000 | 3189938 | GEARBOX OIL, Fix/replace radiator | 2023-09-12 13:48 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MLEGLEITER |  | 2023-09-18 15:54
4.2 | WTG-0025-0000 | 3189968 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2023-09-12 14:41 | Cancelled | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-06-19 12:08
1 | WTG-0013-0000 | 3189858 | CMS Main Bearing Borescope | 2023-09-12 11:16 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2023-10-03 11:05
5 | WTG-2093-0000 | 3189931 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-12 13:32 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-02-13 16:34
5 | WTG-0020-0000 | 3190611 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2023-09-13 15:03 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-10-02 11:54
3 | WTG-0038-0000 | 3191426 | CMS Generator Bearing Check | 2023-09-14 11:03 | Closed | CMS | CMSGENB | UPSTREAM | LXPEREZ |  | 2024-02-13 11:58
3 | WTG-1038-0000 | 3191367 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-14 08:41 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-11-09 10:34
2 | WTG-0066-0000 | 3191500 | Replace Oil Cooler to Gearbox Manifold Hose | 2023-09-14 13:21 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2023-10-02 12:03
4 | WTG-0041A-0000 | 3094828 | GEARBOX OIL, Secondary filter system leak see comments | 2023-03-08 10:08 | Closed | GBXOIL | GBXFILTINS | FORWARD | TBUYESKE |  | 2023-04-28 12:35
3.1 | WTG-0305-NDB0-0000 | 3094862 | CMS Main Bearing Borescope | 2023-03-08 13:29 | Closed | CMS | CMSMBBORE | BISHOP HILL III | CBILLIG |  | 2023-05-01 09:58
1 | WTG-0004-0000 | 3101220 | Replace Gearbox Hose | 2023-03-20 16:22 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS |  | 2023-06-02 14:34
4 | WTG-0032-0000 | 3105530 | Gearbox, Replace Blue Hose | 2023-03-30 07:05 | Closed | GBXOIL | GBXOILCOOL | FORWARD | PPOSTHUMA |  | 2023-10-02 11:34
1 | WTG-00B1-NDB0-0000 | 3107704 | CMS Main Bearing Check/Replacement | 2023-04-03 14:38 | Closed | CMS | CMSMB | COYOTE RIDGE | CBILLIG |  | 2023-06-22 10:19
4 | WTG-0036-0000 | 3108373 | Replace Secondary Pump Shaft Seal | 2023-04-04 12:57 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2023-10-13 14:37
4 | WTG-0036-0000 | 3108374 | GEARBOX OIL, Add 5 Gallons | 2023-04-04 13:00 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-10-13 14:37
5 | WTG-0070-0000 | 3108903 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-05 09:35 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-04-10 10:40
5 | WTG-0070-0000 | 3108909 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-05 09:42 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-04-10 10:40
3 | WTG-0017-0000 | 3108969 | CMS Inspection per GE request | 2023-04-05 10:52 | Closed | CMS | CMSGENB | DEUEL HARVEST | ABARNDT |  | 2023-09-25 12:25
2 | GBX-00088 | 3109617 | CMS Gearbox Borescope | 2023-04-06 13:16 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | MWILSON |  | 2023-04-10 12:16
5 | WTG-0038-NDG0-0000 | 3115248 | CMS HSS Check | 2023-04-20 14:36 | Closed | CMS | CMSHSS | BETHEL | CBILLIG |  | 2023-08-31 11:17
2 | WTG-0118-0000 | 3115253 | CMS Generator Bearing Check | 2023-04-20 15:18 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-10-05 11:07
2 | WTG-0318-0000 | 3116596 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-25 16:12 | Closed | CMS | CMSTRBLSHOOT | BISHOP HILL III | CBILLIG |  | 2023-06-02 12:48
3 | WTG-2129-0000 | 3116894 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-26 13:44 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-01-02 16:36
5 | WTG-0020-0000 | 3124237 | CMS Generator Bearing Check | 2023-05-09 13:25 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-06-23 16:37
3 | WTG-0084-0000 | 3124175 | CMS Gearbox Borescope | 2023-05-09 10:37 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2023-09-01 07:57
5 | WTG-0055-0000 | 3127194 | GEARBOX OIL, Fix oil leak | 2023-05-16 12:14 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | JSTAHLECKER |  | 2024-01-25 10:22
2 | WTG-0047-0000 | 3127456 | GEARBOX OIL, Fix oil leak | 2023-05-17 09:52 | Closed | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE |  | 2023-05-18 12:16
1 | WTG-1005-0000 | 3130204 | GEARBOX OIL, Fix oil leak | 2023-05-20 12:30 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | ATHOMPSON |  | 2023-08-17 14:55
1 | WTG-0006-0000 | 3130793 | GEARBOX OIL, Particle counter troubleshooting | 2023-05-22 16:52 | Closed | GBXOIL | GBXPARTTS | MAVERICK | JMILES |  | 2023-07-08 11:12
1 | WTG-00E5-NDB0-0000 | 3135308 | CMS Main Bearing Borescope | 2023-06-01 12:42 | Closed | CMS | CMSMBBORE | TATANKA RIDGE | CBILLIG |  | 2023-06-06 16:21
5 | WTG-0212-0000 | 3140072 | Replace secondary filter pump shaft seal | 2023-06-07 11:31 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2023-07-17 14:38
5 | WTG-0083-NDG0-0000 | 3168524 | leak at gear oil level t fitting (See picture) | 2023-08-02 15:02 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2023-09-15 14:47
5 | WTG-0089-0000 | 3175294 | GEARBOX OIL, Add/Top-Off 3-5 Gallons | 2023-08-17 07:08 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-10-13 14:25
2 | WTG-0016-NDGP-0000 | 3180041 | Needs blue filter | 2023-08-29 12:01 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | CADAMS |  | 2023-09-29 14:51
1 | WTG-0110-0000 | 3182670 | GEARBOX OIL, Fix oil leak | 2023-08-31 12:07 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JSTEEN |  | 2023-09-08 16:07
3 | WTG-0019-0000 | 3188384 | CMS Main Bearing Borescope | 2023-09-11 08:33 | Closed | CMS | CMSMBBORE | BETHEL | ABARNDT |  | 2023-09-18 15:30
1 | WTG-0046-0000 | 3192196 | GEARBOX OIL, Fix oil leak | 2023-09-16 07:22 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | CSTRZELEC |  | 2023-09-19 12:05
1 | GBX-000001 | 3193575 | EM: Gearbox oil overtemperature | 2023-09-19 17:00 | Closed | GBXOIL | EM77 | SPRING CANYON | TZWIRN |  | 2023-10-19 10:48
4.2 | WTG-0085-0000 | 3194299 | Replace Secondary Pump Shaft Seal | 2023-09-21 07:45 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2023-12-15 10:53
2 | WTG-0007-0000 | 3194313 | GEARBOX OIL, Add/Top-Off | 2023-09-21 08:44 | Closed | GBXOIL | GBXOILADD | GORDON BUTTE | SMCCLURE |  | 2023-11-29 10:13
5 | WTG-1041-0000 | 3197321 | CMS Vibration | 2023-09-26 18:32 | Closed | CMS | CMSGENB | TRAVERSE | JMCCOY |  | 2023-11-27 13:51
3 | WTG-0120-0000 | 3198018 | CMS Gearbox Borescope | 2023-09-28 09:02 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2023-12-04 07:48
5 | WTG-0064-0000 | 3201710 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-10-04 11:15 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-10-11 10:02
1 | BLAD-47M-000172 | 3201620 | rFSA augmented labor WO | 2023-10-04 09:31 | Closed | CMS | EM177 | ORANGEVILLE | BHUNTER |  | 2023-12-01 09:28
3 | WTG-0099-0000 | 3201708 | CMS Generator Bearing Check | 2023-10-04 11:11 | Closed | CMS | CMSGENB | SANTA RITA EAST | ABARNDT |  | 2023-10-20 09:10
2 | WTG-0064-0000 | 3202381 | CMS Generator Bearing Check | 2023-10-05 10:40 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-11-07 09:42
2 | WTG-0017-0000 | 3203086 | CMS Gearbox Borescope | 2023-10-06 14:54 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | WHALL |  | 2023-10-26 14:43
3 | WTG-0017-0000 | 3209850 | CMS Generator Bearing Check | 2023-10-23 09:45 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-12-12 16:53
2 | WTG-0040-0000 | 3213226 | GEARBOX Hose Replacement | 2023-10-27 09:39 | Ready to Schedule | GBXOIL | GBXOILADD | JUDITH GAP | TWIEDEMEIER |  | 2024-02-07 11:26
1 | WTG-0079-NDGP-0000 | 3215205 | GEARBOX OIL, Secondary filter system installation | 2023-10-30 16:26 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | JSTAGNER |  | 2024-01-08 14:02
1 | WTG-0031-0000 | 3215932 | GEARBOX OIL, Oil Sample | 2023-10-31 13:55 | Closed | GBXOIL | GBXOILSAMP | WOLVERINE CREEK | ZMUELLER |  | 2023-11-02 10:25
2 | WTG-0032-0000 | 3218808 | CMS Gearbox Borescope | 2023-11-02 14:50 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | WHALL |  | 2023-11-07 14:51
2 | WTG-0066-0000 | 3218881 | GEARBOX OIL, Add/Top-Off | 2023-11-02 16:18 | Cancelled | GBXOIL | GBXOILADD | JUDITH GAP | TWIEDEMEIER |  | 2023-11-08 16:01
3 | WTG-2110-0000 | 3219100 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-03 10:16 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-11-27 17:19
3 | WTG-2118-0000 | 3222835 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-09 11:06 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-12-05 11:51
4 | WTG-0071A-NDG0-0000 | 3225302 | GEARBOX OIL, Add/Top-Off 5gals | 2023-11-13 15:10 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2024-06-10 09:46
1 | WTG-0014-0000 | 1272862 | Oil FIlter Housing Leaks | 2016-05-18 08:11 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2016-09-13 23:46
3 | WTG-0035-NDGP-0000 | 1278501 | Install Wingery oil pump inversion kit | 2016-06-01 12:10 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2016-11-17 13:57
2 | WTG-0047-0000 | 3193030 | GEARBOX OIL, Add/Top-Off | 2023-09-18 15:29 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | SOTTO |  | 2023-11-26 16:43
2 | WTG-0044-0000 | 3194167 | CMS Main Bearing Borescope | 2023-09-20 15:09 | Closed | CMS | CMSMBBORE | GRAND RIDGE | MOMILANOWSKI |  | 2023-10-09 10:30
2 | WTG-0016-NDG0-0000 | 3194338 | GEARBOX OIL, Add/Top-Off | 2023-09-21 09:32 | Closed | GBXOIL | GBXOILADD | VANTAGE | CCUSACK |  | 2023-09-22 16:08
3 | WTG-00E1-0000 | 3196615 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-25 14:58 | Closed | CMS | CMSTRBLSHOOT | COYOTE RIDGE | ABARNDT |  | 2024-09-09 13:55
4 | WTG-0030-0000 | 3196479 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-25 12:52 | Closed | CMS | CMSTRBLSHOOT | BETHEL | ABARNDT |  | 2023-11-01 16:36
3 | WTG-0055-0000 | 3196484 | CMS Generator Bearing Check | 2023-09-25 13:04 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-11-29 07:58
3 | WTG-2005-0000 | 3197103 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-26 10:48 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-11-27 17:15
1 | WTG-0096-0000 | 3200849 | CMS Gearbox Borescope | 2023-10-03 14:26 | Closed | CMS | CMSGBXBORE | BETHEL | ABARNDT |  | 2023-10-06 14:34
3 | WTG-0052-0000 | 3201728 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 11:43 | Ready to Schedule | GBXOIL | GBXPARTTS | SUNDANCE | ABARNDT
2 | WTG-0113-0000 | 3202388 | CMS Main Bearing Borescope | 2023-10-05 11:23 | Closed | CMS | CMSMBBORE | BETHEL | ABARNDT |  | 2023-10-11 13:07
1 | GBX-WIN-4806470-0020-4 | 3204537 | WTG-006 LOW OIL PRESSURE | 2023-10-10 08:58 | Closed | GBXOIL |  | BUFFALO MOUNT | VFRENCH |  | 2023-12-29 18:32
2 | WTG-0096-0000 | 3208356 | CJC Filter Internal Part replacement | 2023-10-17 17:11 | Cancelled | GBXOIL | GBXFILTELEM | GREXP | MOMILANOWSKI |  | 2024-04-30 09:52
3 | WTG-0047-0000 | 3213200 | GENERATOR, Uptower repair - Bearing replacement | 2023-10-27 08:08 | Closed | CMS | CMSGENB | UPSTREAM | LXPEREZ |  | 2024-03-22 16:24
5 | WTG-0058-0000 | 3218900 | CMS Generator Bearing Check | 2023-11-02 16:41 | Closed | CMS | CMSGENB | GRAND RIDGE | RLINN |  | 2023-11-14 11:01
2 | WTG-0066-0000 | 3223645 | GEARBOX OIL, Add/Top-Off | 2023-11-09 16:13 | Closed | GBXOIL | GBXOILADD | BUCKEYE | MSCHMITT |  | 2023-11-15 15:04
5 | WTG-0031-0000 | 1281250 | GEARBOX OIL, Fix oil leak | 2016-06-09 15:41 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MIAMI |  | 2016-11-18 11:02
1 | WTG-0066-0000 | 1282670 | Inlet hose replacement | 2016-06-16 15:10 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | RWALL |  | 2016-06-17 08:36
1 | WTG-0131-0000 | 1663997 | GEARBOX OIL, Replace oil cooler hose | 2017-01-27 11:03 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-31 07:23
1 | WTG-0134-0000 | 1663998 | GEARBOX OIL, Replace oil cooler hose | 2017-01-27 11:04 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-31 07:23
1 | WTG-0125-0000 | 1663999 | GEARBOX OIL, Replace oil cooler hose | 2017-01-27 11:04 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-31 07:24
1 | WTG-0151-0000 | 1663996 | GEARBOX OIL, Replace oil cooler hose | 2017-01-27 11:03 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-31 07:24
1 | WTG-0053-0000 | 1669637 | GEARBOX OIL, Fix oil leak - inlet hose | 2017-02-05 09:55 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2017-02-21 08:36
1 | WTG-0115-0000 | 1669638 | GEARBOX OIL, Fix oil leak - inlet hose | 2017-02-05 10:01 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2018-02-19 12:23
1 | WTG-0101-0000 | 1669639 | GEARBOX OIL, Fix oil leak - inlet hose | 2017-02-05 10:02 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2017-02-13 18:12
1 | WTG-0121-0000 | 1669640 | GEARBOX OIL, Fix oil leak - inlet hose | 2017-02-05 10:02 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2017-02-13 18:12
1 | WTG-0134-0000 | 1669641 | GEARBOX OIL, Fix oil leak - inlet hose | 2017-02-05 10:03 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2017-02-06 22:02
1 | WTG-0118-0000 | 1669642 | GEARBOX OIL, Fix oil leak - inlet hose | 2017-02-05 10:03 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2017-02-23 10:12
1 | WTG-0096-0000 | 1669643 | GEARBOX OIL, Fix oil leak - inlet hose | 2017-02-05 10:03 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2017-02-23 10:12
1 | WTG-0119-0000 | 1669644 | GEARBOX OIL, Fix oil leak - inlet hose | 2017-02-05 10:05 | Cancelled | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2017-02-05 10:38
1 | WTG-0008-0000 | 1669645 | GEARBOX OIL, Fix oil leak - inlet hose | 2017-02-05 10:05 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2017-04-03 13:59
1 | WTG-0004-0000 | 1669646 | GEARBOX OIL, Fix oil leak - inlet hose | 2017-02-05 10:05 | Cancelled | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2017-02-05 10:09
2 | WTG-0006-0000 | 1344003 | GEARBOX OIL, Fix oil leak | 2016-07-12 09:54 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2016-08-18 15:33
4 | WTG-0024-NDG0-0000 | 1595030 | Top off GBX Oil | 2016-10-28 09:35 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2016-10-31 10:47
1 | WTG-0114-NDG0-0000 | 1243228 | GEARBOX OIL, Oil Sample | 2016-02-15 17:08 | Closed | GBXOIL | GBXOILSAMP | SCEXP | STAYLOR |  | 2016-02-17 17:24
1 | WTG-0052-NDGP-0000 | 1243403 | GEARBOX OIL, Install oil cooler filter pad | 2016-02-16 14:28 | Closed | GBXOIL | GBXOILCOOL | MCADOO | RROBERTS |  | 2016-02-22 08:46
1 | WTG-0051-NDGP-0000 | 1243404 | GEARBOX OIL, Install oil cooler filter pad | 2016-02-16 14:28 | Closed | GBXOIL | GBXOILCOOL | MCADOO | RROBERTS |  | 2016-02-22 08:46
4 | WTG-0022-NDGP-0000 | 1243391 | Replace gear oil pump | 2016-02-16 13:32 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2016-02-17 11:35
2 | WTG-0120-0000 | 1607850 | GEARBOX OIL, Add/Top-Off | 2016-11-22 16:40 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JHAVENS |  | 2017-03-17 07:42
3 | WTG-0027-0000 | 1268876 | Install secondary filtration system on gearbox oil | 2016-05-03 09:56 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2016-05-06 06:52
5 | WTG-0067-0000 | 1270516 | GEARBOX OIL, Oil Sample | 2016-05-10 10:46 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-28 08:35
5 | WTG-0048-0000 | 1270517 | GEARBOX OIL, Oil Sample | 2016-05-10 10:47 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-03 15:04
1 | WTG-0003-NDGP-0000 | 1355307 | GEARBOX OIL, Oil Sample | 2016-08-01 08:10 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS I | MSNOW |  | 2016-10-04 13:16
1 | WTG-0025-0000 | 987556 | T-25 radiator leak (leaking) | 2014-04-14 16:10 | Closed | GBXOIL | GBXOILCOOL | GRAND RIDGE | SLARSEN |  | 2015-12-01 06:49
1 | WTG-0006-NDG0-0000 | 1401571 | GEARBOX OIL, Fix oil leak | 2016-08-12 18:09 | Closed | GBXOIL | GBXOILLEAK | GUNSIGHT | CHUBBARD |  | 2016-08-12 18:38
1 | WTG-0052-NDGP-0000 | 1401558 | GEARBOX OIL, Fix oil leak | 2016-08-12 16:20 | Closed | GBXOIL | GBXOILLEAK | GUNSIGHT | JELLIS |  | 2016-08-12 18:39
1 | WTG-0015-NDG0-0000 | 1095839 | GEARBOX OIL, Oil Sample-Post Internal Repair | 2015-02-19 14:23 | Closed | GBXOIL | GBXOILSAMP | SPRING CANYON | CWADE |  | 2015-02-20 08:53
3 | WTG-0025-NDGP-0000 | 1417942 | Install Winergy oil pump inversion kit | 2016-09-01 08:50 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2016-11-17 13:57
4.2 | WTG-0006-0000 | 1401326 | gearbox oil sample and Post oil change Oil sample | 2016-08-12 14:23 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-17 15:56
4.2 | WTG-0007-0000 | 1401327 | gearbox oil sample and Post oil change Oil sample | 2016-08-12 14:23 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-17 16:14
4.2 | WTG-0015-0000 | 1401344 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:27 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:57
4.2 | WTG-0016-0000 | 1401345 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:27 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:56
4.2 | WTG-0017-0000 | 1401346 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:27 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-30 16:59
4.2 | WTG-0060-0000 | 1401421 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:37 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-27 18:46
4.2 | WTG-0061-0000 | 1401424 | gearbox oil change and post oil change oil sample | 2016-08-12 14:37 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:25
4.2 | WTG-0062-0000 | 1401425 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:37 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:24
4.2 | WTG-0063-0000 | 1401426 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:38 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:24
4.2 | WTG-0064-0000 | 1401429 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:38 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:23
4.2 | WTG-0066-0000 | 1401430 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:38 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:23
4.2 | WTG-0067-0000 | 1401431 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:38 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:22
9 | WTG-0047-0000 | 1612972 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-11-29 13:55 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ | 30 | 2016-12-28 13:43
2 | WTG-0013-NDGP-0000 | 1096803 | WTG #13_Oil Cooler Leak | 2015-02-24 16:30 | Closed | GBXOIL | GBXOILCOOL | FORWARD | NZIRBEL |  | 2016-02-25 08:30
5 | WTG-0201-HPA3-0000 | 1096889 | Pitch Drive Oil Leak | 2015-02-25 08:55 | Closed | GBXOIL | GBXOILLEAK | SCEXP | CWADE |  | 2021-12-21 12:29
9 | WTG-0044-0000 | 1188574 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:34 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:46
9 | WTG-0024-0000 | 1188575 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:36 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:46
9 | WTG-0035-0000 | 1188576 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:37 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:46
4.2 | WTG-0039-NDG0-0000 | 1114210 | Pre-Gearbox Oil Change Detergent Add | 2015-03-30 12:27 | Closed | GBXOIL |  | WILLOW CREEK | FSANTIAGO |  | 2015-04-13 08:46
4.2 | WTG-0048-NDG0-0000 | 1114216 | Pre-Gearbox Oil Change Detergent Add | 2015-03-30 12:27 | Closed | GBXOIL |  | WILLOW CREEK | FSANTIAGO |  | 2015-04-17 15:00
4.2 | WTG-0006-NDG0-0000 | 1114219 | Post-Gearbox Oil Change Oil Sample | 2015-03-30 14:27 | Closed | GBXOIL |  | BISHOP HILL | FSANTIAGO |  | 2015-07-13 13:17
4.2 | WTG-0036-NDG0-0000 | 1114223 | Post-Gearbox Oil Change Oil Sample | 2015-03-30 14:27 | Closed | GBXOIL |  | BISHOP HILL | FSANTIAGO |  | 2015-07-13 13:17
1 | WTG-0028-0000 | 1162240 | change oil filter | 2015-07-21 17:04 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | RWALL |  | 2018-01-09 12:39
1 | BMEC-WTG-008 | 1162271 | WTG008: Thermoerror Oil Pump / NETCOMM | 2015-07-22 07:38 | Closed | GBXOIL |  | BUFFALO MOUNT | CPARKS |  | 2015-07-31 13:28
1 | WTG-0031-NDG0-0000 | 1193826 | Install Poseidon gearbox oil particle counter | 2015-10-27 10:02 | Closed | GBXOIL | GBXPARTINS | STANTON | MSNOW |  | 2016-02-05 15:28
1 | WTG-0008-NDGP-0000 | 1201969 | Replace leaking oil pump | 2015-11-13 13:59 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JJENSEMA |  | 2015-11-17 11:52
1 | WTG-0H09-NDG0-0000 | 1218784 | Replace Gearbox Pump Motor | 2015-12-08 07:46 | Closed | GBXOIL | GBXOILCOOL | BEECH RIDGE | JBENDER |  | 2015-12-08 13:13
2 | WTG-0017-NDGP-0000 | 1222329 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2015-12-21 06:31 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2015-12-23 14:34
5 | WTG-0021-NDG0-0000 | 1278495 | Install Wingery oil pump inversion Kit | 2016-06-01 11:52 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2016-06-09 10:18
3 | WTG-0041-NDGP-0000 | 1278503 | Install Winergy oil pump inversion kit | 2016-06-01 12:12 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2016-10-27 14:52
1 | WTG-0111-NDGP-0000 | 1642633 | Gearbox Oil Work/Issue | 2016-12-15 07:30 | Closed | GBXOIL | EM52 | RONCEVAUX | PPELLETIER |  | 2017-01-03 11:36
2 | WTG-0014-NDGP-0000 | 1273352 | Oil Pump Inversion | 2016-05-20 08:38 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | DSTEO |  | 2016-06-27 08:44
1 | WTG-0019-0000 | 1275203 | GEARBOX OIL, Oil Sample | 2016-05-26 16:35 | Closed | GBXOIL | GBXOILSAMP | MIAMI 1 | KYARNOLD |  | 2016-05-27 07:20
1 | WTG-0007-0000 | 1401894 | gearbox oil change and post oil change oil samples | 2016-08-15 16:22 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | BTAFT |  | 2016-08-17 14:16
1 | GBX-000115 | 1565329 | GEARBOX OIL, Fix oil leak | 2016-09-26 17:01 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KMCLELAND |  | 2016-10-25 07:42
1 | WTG-0089-NDGP-0000 | 1574957 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-10-01 17:25 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-05-21 21:30
4 | WTG-0089-NDG0-0000 | 1574958 | Empty 1gal use oil bucket under gearbox low speed shaft | 2016-10-01 17:28 | In Progress | GBXOIL | GBXOILLEAK | FORWARD | FORWARD
2 | WTG-0011-NDGP-0000 | 1344535 | Oil Pump Inversion | 2016-07-13 15:00 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | RBEBOUT |  | 2016-09-26 07:58
2 | WTG-0094-NDGP-0000 | 1632568 | GEARBOX OIL, Replace oil pump | 2016-12-07 16:01 | Cancelled | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2017-01-13 12:54
4.2 | WTG-0043-NDG0-0000 | 1668736 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:15 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-05-15 17:26
4.2 | WTG-0020-NDG0-0000 | 1668760 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:21 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-03-30 15:21
4.2 | WTG-0007-NDG0-0000 | 1668753 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:19 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-02 11:43
4.2 | WTG-0008-NDG0-0000 | 1668755 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:20 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-07 09:14
4.2 | WTG-0023-NDG0-0000 | 1668758 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:20 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-04-07 15:22
4.2 | WTG-0018-NDG0-0000 | 1668768 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:25 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-29 15:18
4.2 | WTG-0017-NDG0-0000 | 1668767 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:24 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-02-03 13:19
1 | GBX-000027 | 1251811 | GEARBOX OIL, Fix oil leak | 2016-03-09 16:25 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | ASCHRIMPSCHER |  | 2016-06-08 08:58
1 | WTG-0093-0000 | 1669392 | GEARBOX OIL, Fix oil leak | 2017-02-03 16:26 | Closed | GBXOIL | GBXOILLEAK | BETHEL | BBALDERAZ |  | 2017-02-07 12:39
4 | WTG-0071A-NDGP-0000 | 1258932 | Replace Gear Oil Pump | 2016-04-04 10:58 | Closed | GBXOIL | GBXOILLEAK | FORWARD | IFRANCISCO |  | 2016-04-13 12:03
1 | WTG-0031-NDGP-0000 | 1264015 | replace oil pump hose | 2016-04-26 14:04 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | ZMUELLER |  | 2016-05-02 10:41
9 | WTG-0072-0000 | 1602033 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-11-14 08:49 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS | 30 | 2017-01-03 13:29
1 | WTG-0032-NDGP-0000 | 1267375 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:26 | Closed | GBXOIL | GBXFILTELEM | GRAND RIDGE | MSNOW |  | 2017-11-09 07:52
1 | WTG-0044-NDGP-0000 | 1267378 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:34 | Closed | GBXOIL | GBXFILTELEM | GRAND RIDGE | MSNOW |  | 2017-11-03 14:42
1 | WTG-0019-NDGP-0000 | 1267395 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 08:38 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | MSNOW |  | 2016-06-22 19:50
1 | WTG-0016-NDGP-0000 | 1267396 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:39 | Closed | GBXOIL | GBXFILTELEM | TURKEY TRACK | MSNOW |  | 2016-05-18 11:48
1 | WTG-0026-NDGP-0000 | 1267397 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:39 | Closed | GBXOIL | GBXFILTELEM | TURKEY TRACK | MSNOW |  | 2016-05-18 11:47
1 | WTG-0034-NDGP-0000 | 1267398 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:39 | Closed | GBXOIL | GBXFILTELEM | TURKEY TRACK | MSNOW |  | 2016-05-18 11:47
1 | WTG-0047-NDGP-0000 | 1267399 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:40 | Closed | GBXOIL | GBXFILTELEM | TURKEY TRACK | MSNOW |  | 2016-05-18 10:12
1 | WTG-0065-NDGP-0000 | 1267400 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:40 | Closed | GBXOIL | GBXFILTELEM | TURKEY TRACK | MSNOW |  | 2016-05-18 10:04
1 | WTG-0075-NDGP-0000 | 1267401 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:41 | Closed | GBXOIL | GBXFILTELEM | TURKEY TRACK | MSNOW |  | 2016-05-18 10:04
1 | WTG-0079-NDGP-0000 | 1267402 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:41 | Closed | GBXOIL | GBXFILTELEM | TURKEY TRACK | MSNOW |  | 2016-05-18 10:04
9 | GBX-00043E | 1269046 | Radiator Oil Cooler Leak - Nanjing | 2016-05-03 22:26 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2016-07-20 13:41
1 | WTG-0035-NDGP-0000 | 1644223 | EM: Motor protection top cabinet / Oil cooler motor replacement | 2016-12-16 18:05 | Closed | GBXOIL | EM102 | FORWARD | FORWARD |  | 2017-05-01 09:35
9 | WTG-0027-0000 | 1271118 | Radiator Cooler Oil Leak Found - Nanjing | 2016-05-12 08:27 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | FANAYA |  | 2018-11-27 12:15
2 | WTG-0031-NDG0-0000 | 1657416 | GEARBOX OIL, Fix oil leak( high speed shaft leak) | 2017-01-11 15:15 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2019-07-02 16:37
4 | WTG-0090-NDGP-0000 | 1274846 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-05-25 15:02 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-05-26 13:47
1 | WTG-0012-0000 | 1344194 | GEARBOX OIL, Fix oil leak | 2016-07-12 16:33 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2017-02-16 18:14
4 | WTG-0058-NDGP-0000 | 1344199 | Gear oil pump leaking | 2016-07-12 12:16 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2016-08-12 07:43
5 | WTG-0102-NDGP-0000 | 1354311 | GEARBOX OIL, Particle counter removal | 2016-07-29 09:54 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2016-08-03 08:03
5 | WTG-0048-NDGP-0000 | 1354312 | GEARBOX OIL, Particle counter installation | 2016-07-29 09:55 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2016-08-04 09:27
5 | WTG-0011-NDG0-0000 | 1850981 | GEARBOX OIL, Add/Top-Off | 2018-03-08 14:12 | Closed | GBXOIL | GBXOILADD | FORWARD | CMITCHELL |  | 2018-05-30 09:23
1 | WTG-0106-NDG0-0000 | 1001483 | Pre-Gearbox Oil Change Detergent Add | 2014-05-08 15:51 | Closed | GBXOIL | GBXOILSAMP | GREXP | R5 |  | 2015-03-12 15:16
1 | WTG-0024-NDGP-0000 | 1622574 | GEARBOX OIL, Fix oil leak | 2016-12-05 12:55 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MIAMI |  | 2016-12-09 07:52
1 | WTG-0060-0000 | 1664182 | GEARBOX OIL, replace oil cooler hose | 2017-01-26 09:17 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | KMCLELAND |  | 2017-01-30 07:28
4.2 | WTG-0039-NDGP-0000 | 1586572 | Replace Oil Pump | 2016-10-13 08:49 | Closed | GBXOIL | GBXOILLEAK | VANTAGE | SRIGGIN |  | 2017-03-22 11:19
4 | WTG-0079-NDGP-0000 | 1586608 | Replace pump motor coupling | 2016-10-13 15:16 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2016-10-21 06:47
1 | WTG-0074-ND00-0000 | 1250366 | high speed seal replacement- T74 | 2016-03-03 12:33 | Closed | GBXOIL | GBXOILLEAK | MCADOO | LCOPELAND |  | 2016-03-25 08:45
1 | WTG-0016-NDG0-0000 | 1252122 | GEARBOX OIL, Fix oil leak | 2016-03-11 13:31 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | CMUSTAIN |  | 2018-07-07 13:41
1 | WTG-0109-0000 | 1646411 | GEARBOX OIL, Fix oil leak | 2016-12-26 17:32 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-03 15:36
4 | WTG-0065-NDG0-0000 | 1271246 | GEARBOX OIL, Fix oil leak(Inspection cover gaskets) | 2016-05-12 18:24 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2018-01-19 09:10
4.2 | WTG-0133-NDG0-0000 | 1001409 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GREXP | R5 |  | 2015-04-08 15:24
4.2 | WTG-0136-NDG0-0000 | 1001412 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GRAND RIDGE IV | R5 |  | 2015-04-07 15:26
4.2 | WTG-0138-NDG0-0000 | 1001413 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GRAND RIDGE IV | R5 |  | 2015-04-08 15:24
4.2 | WTG-0140-NDG0-0000 | 1001414 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GRAND RIDGE IV | R5 |  | 2015-04-10 14:58
2 | WTG-0052-0000 | 1261532 | Interior tower clean up | 2016-04-14 18:02 | Cancelled | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2016-11-07 12:22
4 | WTG-0203B-NDGP-0000 | 1269276 | GEARBOX OIL, Fix oil leak (Needs cleaning) | 2016-05-04 15:20 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2016-05-09 10:01
2 | WTG-0045-NDGP-0000 | 1272478 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Cancelled | GBXOIL | GBXFILTELEM | GOLDTHWAITE | RJOHNSON |  | 2017-07-31 10:55
2 | WTG-0019-NDGP-0000 | 1272479 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Cancelled | GBXOIL | GBXFILTELEM | GOLDTHWAITE | RJOHNSON |  | 2017-09-08 18:05
2 | WTG-0078-NDGP-0000 | 1272480 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Closed | GBXOIL | GBXFILTELEM | GOLDTHWAITE | RJOHNSON |  | 2017-03-01 12:39
2 | WTG-0017-NDGP-0000 | 1272481 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Cancelled | GBXOIL | GBXFILTELEM | GOLDTHWAITE | RJOHNSON |  | 2017-05-10 15:26
2 | WTG-0010-NDGP-0000 | 1272482 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Closed | GBXOIL | GBXFILTELEM | GOLDTHWAITE | RJOHNSON |  | 2017-01-11 12:18
2 | WTG-0072-NDGP-0000 | 1272483 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Closed | GBXOIL | GBXFILTELEM | GOLDTHWAITE | RJOHNSON |  | 2017-06-30 10:18
1 | WTG-0006-NDGP-0000 | 1272525 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 13:51 | Closed | GBXOIL | GBXFILTELEM | SPRING CANYON | RJOHNSON |  | 2018-08-15 21:53
1 | WTG-0031-NDGP-0000 | 1272526 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 13:51 | Closed | GBXOIL | GBXFILTELEM | SPRING CANYON | RJOHNSON |  | 2023-07-31 10:56
1 | WTG-0012-NDGP-0000 | 1272527 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 13:51 | Closed | GBXOIL | GBXFILTELEM | WOLVERINE CREEK | RJOHNSON |  | 2016-07-13 07:59
1 | WTG-0016-NDGP-0000 | 1272528 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Closed | GBXOIL | GBXFILTELEM | ORANGEVILLE | RJOHNSON |  | 2016-09-13 07:14
1 | WTG-0054-NDGP-0000 | 1272529 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Closed | GBXOIL | GBXFILTELEM | ORANGEVILLE | RJOHNSON |  | 2016-09-13 07:14
1 | WTG-0026-NDGP-0000 | 1272530 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Closed | GBXOIL | GBXFILTELEM | ORANGEVILLE | RJOHNSON |  | 2016-09-13 07:14
1 | WTG-0015-NDGP-0000 | 1272531 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Closed | GBXOIL | GBXFILTELEM | ORANGEVILLE | RJOHNSON |  | 2016-09-13 07:14
1 | WTG-0001-NDGP-0000 | 1272532 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 15:51 | Closed | GBXOIL | GBXFILTELEM | ORANGEVILLE | RJOHNSON |  | 2016-09-13 07:12
3 | WTG-0044-NDGP-0000 | 1272533 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | FORWARD | RJOHNSON |  | 2018-02-09 15:53
3 | WTG-0038-NDGP-0000 | 1272534 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | On Hold | GBXOIL | GBXFILTELEM | FORWARD | RJOHNSON
3 | WTG-0007-NDGP-0000 | 1272535 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | FORWARD | RJOHNSON |  | 2018-03-28 15:14
4 | WTG-0066-NDGP-0000 | 1272536 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | FORWARD | RJOHNSON |  | 2017-09-07 16:55
3 | WTG-0087-NDGP-0000 | 1272537 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | FORWARD | RJOHNSON |  | 2018-01-26 12:07
3 | WTG-0035-NDGP-0000 | 1272538 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | FORWARD | RJOHNSON |  | 2017-11-14 15:18
2 | WTG-0082-NDG0-0000 | 1275061 | GEARBOX OIL, Oil Sample | 2016-05-26 07:37 | Closed | GBXOIL | GBXOILSAMP | JUDITH GAP | MSNOW |  | 2016-08-29 14:54
1 | WTG-0029-0000 | 1593150 | GEARBOX OIL, Fix oil leak | 2016-10-25 15:13 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | AMITCHELL |  | 2017-03-21 17:07
1 | WTG-0121-NDG0-0000 | 1600864 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:58 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 07:51
1 | WTG-0123-NDG0-0000 | 1600865 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:58 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 09:08
1 | WTG-0124-NDG0-0000 | 1600866 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:59 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 09:11
1 | WTG-0130-NDG0-0000 | 1600867 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:59 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 09:12
1 | WTG-0131-NDG0-0000 | 1600868 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:59 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2016-11-10 12:25
1 | WTG-0133-NDG0-0000 | 1600869 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:59 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 09:12
1 | WTG-0134-NDG0-0000 | 1600870 | Fix leaks on Nanjing gearboxes | 2016-11-07 14:00 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 09:13
1 | WTG-0113-NDG0-0000 | 1600861 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:57 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 07:49
1 | WTG-0114-NDG0-0000 | 1600862 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:58 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 07:50
1 | WTG-0116-NDG0-0000 | 1600863 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:58 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 07:50
1 | WTG-0003-0000 | 1401889 | gearbox oil change and post oil change oil sample | 2016-08-15 16:08 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | BTAFT |  | 2016-08-17 14:21
1 | WTG-0004-0000 | 1401891 | gearbox oil chanage and post oil change oil sample | 2016-08-15 16:16 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | BTAFT |  | 2016-08-17 14:20
1 | WTG-0005-0000 | 1401892 | gearbox oil change and post oil chnage oil samples | 2016-08-15 16:19 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | BTAFT |  | 2016-08-17 14:17
1 | WTG-0008-0000 | 1401895 | gearbox oil chnage and post oil change oil sample | 2016-08-15 16:26 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | BTAFT |  | 2016-08-17 14:14
1 | GBX-000075 | 1283130 | EM: Gearbox oil overtemperature | 2016-06-15 06:59 | Closed | GBXOIL | EM77 | GOLDTHWAITE | JDWILLIAMS |  | 2016-06-19 23:45
1 | WTG-0084-0000 | 1411704 | GEARBOX OIL, Fix oil leak | 2016-08-29 13:23 | Closed | GBXOIL | GBXOILLEAK | MCADOO | TRUDE |  | 2016-08-31 11:25
3 | WTG-0032-NDGP-0000 | 1660910 | GEARBOX OIL, Replace oil pump | 2017-01-20 11:01 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2018-10-12 15:46
1 | WTG-0F05-NDGP-0000 | 1601329 | Replace oil cooler | 2016-11-10 07:21 | Closed | GBXOIL | GBXOILCOOL | HIGH SHELDON | RKEHL |  | 2016-11-28 12:00
1 | WTG-0046-0000 | 1595806 | GEARBOX OIL, Replace oil cooler hose | 2016-10-31 13:41 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KMCLELAND |  | 2017-03-06 08:51
2 | WTG-0044-NDGP-0000 | 1644876 | GEARBOX OIL, Particle counter troubleshooting | 2016-12-20 14:23 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2017-01-23 08:38
4.2 | WTG-0107-NDGP-0000 | 1232544 | GEARBOX OIL, pump is starting to leak | 2016-01-22 16:35 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2016-02-17 12:14
2 | WTG-0090-NDGP-0000 | 1237435 | GEARBOX OIL, Fix oil leak - Gearbox oil pump is leaking | 2016-02-02 07:53 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JJENSEMA |  | 2016-03-04 09:01
2 | WTG-0065-NDGP-0000 | 1600099 | GEARBOX OIL, Particle counter removal | 2016-11-04 11:32 | Closed | GBXOIL | GBXPARTREM | MCADOO | MSNOW |  | 2016-11-21 11:55
2 | WTG-0002-NDGP-0000 | 1642946 | GEARBOX OIL, Secondary filter system element change | 2016-12-15 12:04 | Closed | GBXOIL | GBXFILTELEM | WILLOW CREEK | MSTONER |  | 2016-12-15 12:09
1 | WTG-0032-NDG0-0000 | 1038530 | Gearbox Oil Sample (Special) | 2014-09-02 14:20 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | MCONWELL |  | 2015-03-16 12:34
2 | WTG-0067-0000 | 1346747 | GEARBOX OIL, Oil Sample | 2016-07-20 11:53 | Closed | GBXOIL | GBXOILSAMP | BUCKEYE | MLEGLEITER |  | 2016-07-22 16:28
2 | WTG-0109-NDGP-0000 | 1107226 | Change Jensen System Filter | 2015-03-11 14:31 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE | CBORER |  | 2015-08-14 15:52
1 | WTG-0058-0000 | 1118057 | Oil leak | 2015-04-03 16:58 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | JFERRIS |  | 2015-04-06 16:29
2 | WTG-0006-0000 | 1670996 | Program start PLC | 2017-02-09 14:10 | Cancelled | GBXOIL | GBXOILLEAK | JUDITH GAP | JUDITHGAP |  | 2017-05-12 15:00
1 | GBX-000125 | 1667999 | Gearbox leaking | 2017-02-02 07:57 | Cancelled | GBXOIL | GBXOILLEAK | CAL RIDGE | RWALL |  | 2017-11-09 15:42
1 | WTG-0025-NDG0-0000 | 1092666 | T25 gearbox oil leak- warranty work-Moventas | 2015-02-10 07:05 | Closed | GBXOIL | GBXOILLEAK | MCADOO | LCOPELAND |  | 2015-02-12 11:28
1 | WTG-0141-0000 | 1574127 | Replace gearbox plenum | 2016-09-30 11:30 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | JHAVENS |  | 2016-11-03 15:57
2 | WTG-0019-NDGP-0000 | 1600090 | GEARBOX OIL, Particle counter removal | 2016-11-04 10:22 | Closed | GBXOIL | GBXPARTREM | JUDITH GAP | MSNOW |  | 2016-12-02 10:20
2 | WTG-0091-NDGP-0000 | 1600091 | GEARBOX OIL, Particle counter removal | 2016-11-04 10:24 | Closed | GBXOIL | GBXPARTREM | JUDITH GAP | MSNOW |  | 2016-12-02 10:20
2 | WTG-0008-NDGP-0000 | 1600092 | GEARBOX OIL, Particle counter installation | 2016-11-04 10:26 | Closed | GBXOIL | GBXPARTINS | JUDITH GAP | MSNOW |  | 2016-12-02 10:21
2 | WTG-0072-NDGP-0000 | 1600093 | GEARBOX OIL, Particle counter installation | 2016-11-04 10:28 | Closed | GBXOIL | GBXPARTINS | JUDITH GAP | MSNOW |  | 2016-12-02 10:22
2 | WTG-0072-NDGP-0000 | 1600101 | GEARBOX OIL, Particle counter installation | 2016-11-04 11:33 | Closed | GBXOIL | GBXPARTINS | MCADOO | MSNOW |  | 2016-12-16 12:57
2 | WTG-0116-NDG0-0000 | 1600106 | GEARBOX OIL, Particle counter removal | 2016-11-04 11:52 | Closed | GBXOIL | GBXPARTREM | GREXP | MSNOW |  | 2016-11-17 15:44
2 | WTG-0044-NDGP-0000 | 1600111 | GEARBOX OIL, Particle counter installation | 2016-11-04 11:59 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2016-11-16 12:41
1 | WTG-0103-NDG0-0000 | 1038575 | Gearbox Oil Sample (Special) | 2014-09-02 14:21 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | MCONWELL |  | 2015-03-03 09:06
1 | WTG-0085-0000 | 1102445 | Filter housing lid leak | 2015-03-03 16:14 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2015-03-05 13:40
2 | WTG-0012-NDGP-0000 | 1107218 | Change Jensen System Filter | 2015-03-11 14:27 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE | CBORER |  | 2015-07-29 14:22
2 | WTG-0054-NDG0-0000 | 1138001 | GEARBOX OIL, Oil Sample | 2015-05-08 17:38 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | MSNOW |  | 2016-02-05 12:06
1 | WTG-0104-NDG0-0000 | 1137999 | Gearbox Oil Leak | 2015-05-08 17:29 | Closed | GBXOIL | GBXOILLEAK | SCEXP | CWADE |  | 2015-05-19 16:17
1 | BMEC-MCC-013 | 1149874 | WTG-013 High Gear Oil Temp | 2015-06-12 09:15 | Closed | GBXOIL |  | BUFFALO MOUNT | CPARKS |  | 2015-07-02 11:26
2 | WTG-0079-0000 | 1169972 | Exterior tower oil leak | 2015-08-06 18:10 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2016-04-18 12:41
1 | WTG-0026-0000 | 1209704 | Clean turbine from oil leak | 2015-11-24 08:29 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2016-05-23 15:41
9 | WTG-0058-0000 | 1218136 | GEARBOX, Oil Change | 2015-12-06 09:03 | Closed | GBXOIL | GBXOILCHG | BUCKEYE | CWADE |  | 2016-01-18 11:09
2 | WTG-0056A-NDGP-0000 | 1219883 | GEARBOX OIL, Replace oil motor/pump | 2015-12-14 06:56 | Closed | GBXOIL | GBXOILCOOL | FORWARD | RSOBER |  | 2015-12-17 12:50
1 | WTG-0111-0000 | 1282472 | GEARBOX OIL, Oil Sample | 2016-06-16 10:30 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | CRHODES |  | 2016-06-28 08:35
4 | WTG-0033-NDGP-0000 | 1344988 | Gear oil pump leaking | 2016-07-14 10:26 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-07-18 09:40
9 | WTG-0155-NDG0-0000 | 1242769 | Gearbox Oil Change | 2016-02-12 17:13 | Closed | GBXOIL | GBXOILCHG | MIAMI 1 | KYARNOLD |  | 2016-02-18 07:29
9 | WTG-0005-0000 | 1246942 | GEARBOX, Oil Change | 2016-02-29 15:17 | Closed | GBXOIL | GBXOILCHG | RATTLESNAKE 1 | JGASTON |  | 2016-03-25 09:54
9 | WTG-0007-0000 | 1246944 | GEARBOX, Oil Change | 2016-02-29 15:23 | Closed | GBXOIL | GBXOILCHG | RATTLESNAKE 1 | JGASTON |  | 2016-03-25 09:54
1 | WTG-0079-0000 | 1091855 | Gearbox oil level low | 2015-02-06 09:05 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JBRADDOCK |  | 2015-02-06 16:30
4 | WTG-0044-NDGP-0000 | 1640562 | GEARBOX OIL, Replace oil pump | 2016-12-10 10:56 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2017-02-09 09:55
4 | WTG-0008-NDG0-0000 | 1640677 | GEARBOX OIL, Add/Top-Off (5 gallons) | 2016-12-12 08:12 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2017-04-11 09:44
9 | WTG-0006-0000 | 1239428 | GEARBOX OIL, Secondary filter system installation | 2016-02-05 08:25 | Closed | GBXOIL | GBXFILTINS | RATTLESNAKE 1 | JGASTON |  | 2016-02-16 07:53
4 | WTG-0210A-NDGP-0000 | 1263510 | GEARBOX OIL, Replace oil cooler fan/motor/pump-Pump Leaks | 2016-04-25 14:15 | Closed | GBXOIL | GBXOILCOOL | FORWARD | CMITCHELL |  | 2016-08-30 14:29
1 | WTG-0040-0000 | 1108579 | GEARBOX OIL, Fix oil leak | 2015-03-17 09:35 | Closed | GBXOIL | GBXOILLEAK | MCADOO | JZARATE |  | 2015-03-19 08:14
1 | WTG-0117-NDG0-0000 | 1134685 | GEARBOX OIL, Oil Sample | 2015-05-01 10:11 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS II | LBENAVIDES |  | 2015-05-05 08:11
4.2 | WTG-0106-NDG0-0000 | 1001387 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GREXP | R5 |  | 2015-04-01 14:52
1 | WTG-0055-0000 | 1352600 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-07-25 13:12 | Closed | GBXOIL | GBXOILCOOL | MCADOO | BJAMESON |  | 2016-08-04 08:32
4.2 | GBX-000050 | 1164925 | WTG 50 has metal shavings in gearbox oil filter catch pan | 2015-07-30 09:49 | Closed | GBXOIL | BLANK | TURKEY TRACK | MGROTJAN |  | 2015-12-17 15:37
2 | WTG-0003-0000 | 1401741 | GEARBOX OIL, Fix oil leak | 2016-08-15 10:04 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | BUCKEYE |  | 2016-08-17 08:18
1 | WTG-0038-0000 | 1194609 | GEARBOX OIL, Fix oil leak | 2015-10-29 08:05 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JSTAGNER |  | 2015-12-09 14:47
9 | WTG-0048-0000 | 1612906 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-11-29 11:46 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ | 30 | 2016-12-28 13:44
4 | WTG-0046-NDGP-0000 | 1216191 | Gearbox particle counter removal | 2015-12-02 12:58 | Closed | GBXOIL | GBXPARTREM | TURKEY TRACK | MGROTJAN |  | 2015-12-17 08:22
1 | WTG-0172-NDG0-0000 | 1246034 | GEARBOX OIL, Oil Sample | 2016-02-26 14:45 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS II | FMORALES |  | 2016-02-29 08:19
1 | WTG-0031-NDG0-0000 | 1600851 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:31 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2016-11-18 11:01
1 | WTG-0065-NDG0-0000 | 1600852 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:55 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2016-11-10 12:26
1 | WTG-0066-NDG0-0000 | 1600853 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:55 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2016-11-10 12:27
1 | WTG-0075-NDG0-0000 | 1600854 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:55 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 09:13
1 | WTG-0082-NDG0-0000 | 1600855 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:56 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2016-11-14 07:33
1 | WTG-0083-NDG0-0000 | 1600856 | Fix leaks on Nanjing gearboxes | 2016-11-07 13:56 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-10 09:14
5 | WTG-0047-ND00-0000 | 1410660 | GEARBOX OIL, Particle counter removal | 2016-08-26 17:54 | Closed | GBXOIL | GBXPARTREM | ORANGEVILLE | MSNOW |  | 2016-09-14 10:57
1 | WTG-0137-NDGP-0000 | 1443072 | EM: Gearbox oil overtemperature | 2016-09-10 11:10 | Closed | GBXOIL | EM77 | WAKE 1 | IMORALES |  | 2016-11-07 16:18
2 | WTG-0014-NDG0-0000 | 1570178 | GEARBOX OIL, Add/Top-Off | 2016-09-28 15:33 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | RCARSON |  | 2016-10-05 09:17
4 | WTG-0041A-NDG0-0000 | 1606690 | GEARBOX OIL, Add/Top-Off | 2016-11-21 09:48 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2016-11-29 10:37
2 | WTG-0088-NDGP-0000 | 1606702 | GEARBOX OIL, Particle counter installation | 2016-11-21 10:41 | Closed | GBXOIL | GBXPARTINS | MCADOO | MGIVENS |  | 2016-11-22 10:52
1 | GBX-000104 | 1606707 | EM: Gearbox oil pressure too low | 2016-11-21 12:46 | Closed | GBXOIL | EM52 | PRAIRIE BREEZE | JFERRIS |  | 2016-11-30 17:09
2 | WTG-0039-NDGP-0000 | 1649569 | Gearbox Oil Secondary Filter System Element Change | 2016-12-28 09:23 | Closed | GBXOIL | GBXFILTELEM | WILLOW CREEK | MSTONER | 1 | 2017-01-04 11:56
4.2 | WTG-0087-NDGP-0000 | 1545241 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-09-21 11:36 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2016-11-04 06:53
1 | WTG-0074-NDG0-0000 | 1656826 | GEARBOX OIL, Fix oil leak | 2017-01-09 11:13 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | CAL RIDGE |  | 2017-01-12 07:06
1 | WTG-0034-ND00-0000 | 1600315 | GEARBOX OIL, Add/Top-Off | 2016-11-04 17:16 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | SPRINGCANYON |  | 2016-11-15 16:18
4 | WTG-0052-T000-0000 | 1261335 | drain oil from yaw deck catch ring | 2016-04-13 14:05 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | MMAGER |  | 2016-07-29 14:48
4.2 | WTG-0129-NDG0-0000 | 1001406 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GREXP | R5 |  | 2015-02-25 14:43
1 | WTG-0072-0000 | 1643185 | Inlet hose replacement | 2016-12-15 14:40 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | RWALL |  | 2017-04-03 14:02
9 | WTG-0083-0000 | 1188560 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:06 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
9 | WTG-0087-0000 | 1188563 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:13 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
2 | WTG-0002-NDGP-0000 | 1107216 | Change Jensen System Filter | 2015-03-11 14:19 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE | CBORER |  | 2015-03-16 17:30
2 | WTG-0006-NDGP-0000 | 1107217 | Change Jensen System Filter | 2015-03-11 14:27 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE | CBORER |  | 2015-04-02 11:07
1 | WTG-0155-NDGP-0000 | 1093048 | Offline Filter Installation | 2015-02-11 09:03 | Closed | GBXOIL | GBXFILTINS | MIAMI 1 | LPORTER |  | 2015-02-17 16:22
1 | WTG-0154-NDG0-0000 | 1112312 | Oil sample | 2015-03-25 15:53 | Closed | GBXOIL | GBXOILSAMP | MIAMI 1 | LPORTER |  | 2015-03-30 15:50
1 | WTG-0076-0000 | 1147156 | GEARBOX OIL, Oil Samples for Engineering | 2015-06-03 15:31 | Closed | GBXOIL | GBXOILSAMP | GREXP | JWARREN |  | 2015-06-03 15:36
2 | WTG-0052-N000-0000 | 1152272 | Replace Gear Oil Pump | 2015-06-22 09:39 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | SRIGGIN |  | 2015-06-23 06:48
1 | WTG-0033-0000 | 1153950 | GEARBOX OIL, Fix oil leak | 2015-06-28 20:15 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | CWADE |  | 2015-07-07 14:43
1 | WTG-0006-NDGP-0000 | 1160874 | GEARBOX OIL, Replace oil cooler fan/motor/pump (motor) and inversion | 2015-07-09 09:44 | Closed | GBXOIL | GBXOILCOOL | GRAND RIDGE | NSCHAEFER |  | 2015-07-13 10:13
1 | WTG-0006-NDGP-0000 | 1160882 | GEARBOX OIL, Replace oil cooler (radiator) | 2015-07-09 09:52 | Closed | GBXOIL | GBXOILCOOL | GRAND RIDGE | NSCHAEFER |  | 2015-07-13 09:57
1 | WTG-0071-0000 | 1167662 | GEARBOX OIL, Oil Sample | 2015-08-03 15:17 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | KCOOPER |  | 2015-08-06 10:36
1 | WTG-0037-0000 | 1092726 | Gearbox Oil Sample (Special) | 2015-02-10 09:14 | Closed | GBXOIL | GBXOILSAMP | MCADOO | FSANTIAGO |  | 2015-02-17 15:39
1 | WTG-0040-0000 | 1167616 | GEARBOX OIL, Fix oil leak | 2015-08-03 14:21 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | CCOTTINGHAM |  | 2018-11-13 15:57
1 | WTG-0091-0000 | 1186803 | WTG 91 gearbox oil leak- warranty claim | 2015-10-01 12:37 | Closed | GBXOIL | GBXOILLEAK | MCADOO | LCOPELAND |  | 2016-03-30 08:02
1 | GBX-000107 | 1191824 | EM: Gearbox oil overtemperature | 2015-10-18 19:38 | Closed | GBXOIL | EM77 | PRAIRIE BREEZE | BDOZLER |  | 2015-10-19 17:07
9 | WTG-0031-0000 | 1177653 | Install AMSOIL Labels on DTA & Gearbox of Turbines that have been converted | 2015-09-01 11:26 | Closed | GBXOIL | GBXOILCHG | GOLDTHWAITE | DDIAZ |  | 2016-12-13 10:14
9 | WTG-0086-0000 | 1177654 | Install AMSOIL Labels on DTA & Gearbox of Turbines that have been converted | 2015-09-01 11:26 | Closed | GBXOIL | GBXOILCHG | GOLDTHWAITE | DDIAZ |  | 2016-06-14 16:26
1 | GBX-000039 | 1180806 | GEARBOX OIL, Oil Sample | 2015-09-11 08:19 | Closed | GBXOIL | GBXOILSAMP | FORWARD | ACARR |  | 2015-09-15 07:57
9 | WTG-0026-0000 | 1188566 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:21 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:46
9 | WTG-0038-0000 | 1188569 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:26 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:46
9 | WTG-0058-0000 | 1188570 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:27 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:46
9 | WTG-0061-0000 | 1188571 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:29 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:46
2 | WTG-0108-NDGP-0000 | 1107225 | Change Jensen System Filter | 2015-03-11 14:30 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE | CBORER |  | 2015-08-14 15:52
1 | WTG-0068-NDGP-0000 | 1616858 | GEARBOX OIL, Oil Sample | 2016-12-02 09:31 | Closed | GBXOIL | GBXOILSAMP | CAL RIDGE | MSNOW |  | 2017-06-14 10:21
1 | WTG-0002-NDGP-0000 | 1189134 | GEARBOX OIL, Fix oil leak | 2015-10-05 20:34 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CHADDIX |  | 2017-04-18 17:19
2 | WTG-0010-NDGP-0000 | 1228744 | Gearbox needed 5 gallons of oil | 2016-01-05 12:01 | Closed | GBXOIL | GBXOILADD | FORWARD | ACASPER |  | 2016-01-06 14:48
1 | WTG-0012-0000 | 1228789 | Install secondary filtration system on gearbox oil | 2016-01-05 13:30 | Cancelled | GBXOIL | GBXFILTINS | WOLVERINE CREEK | DSTEO | 1 | 2016-07-12 09:29
1 | WTG-0060-0000 | 1171801 | GEARBOX OIL,pump inversion needed (leaking) | 2015-08-14 15:30 | Closed | GBXOIL | GBXOILCOOL | GRAND RIDGE | MJACOBS |  | 2015-12-10 15:49
4 | WTG-0205-NDGP-0000 | 1267480 | GBX Oil Pump Replacement | 2016-05-02 10:41 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JJENSEMA |  | 2016-05-05 09:30
2 | WTG-0081-0000 | 1317338 | Radiator Cooler Oil Leak Found - Nanjing | 2016-06-29 08:12 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CRWADE |  | 2017-10-25 09:52
1 | WTG-0120-0000 | 1660002 | Needs pump inversion (not leaking) | 2017-01-17 13:07 | Cancelled | GBXOIL | GBXOILCOOL | GREXP | MFERRARO |  | 2023-06-29 13:12
2 | WTG-0047-0000 | 1070545 | Pall Housing Change | 2014-12-06 08:55 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JBRADDOCK |  | 2016-07-15 09:06
1 | WTG-0036-NDG0-0000 | 1091512 | Post Gearbox Oil Sample | 2015-02-04 15:03 | Closed | GBXOIL | GBXOILSAMP | GRAND RIDGE | BBROWN |  | 2015-02-04 15:07
1 | SCEXP | 1676799 | dispose of incorrect o rings | 2017-02-27 16:41 | Closed | GBXOIL | GBXOILLEAK | SCEXP | CMUSTAIN |  | 2017-02-27 16:44
1 | WTG-0037-0000 | 1685391 | GEARBOX OIL, Oil Sample | 2017-03-21 14:40 | Closed | GBXOIL | GBXOILSAMP | PRAIRIE BREEZE | NHEITHOFF |  | 2017-03-29 17:21
1 | WTG-0047-0000 | 1685392 | GEARBOX OIL, Oil Sample | 2017-03-21 14:40 | Closed | GBXOIL | GBXOILSAMP | PRAIRIE BREEZE | NHEITHOFF |  | 2017-03-29 17:21
2 | WTG-0082-NDGP-0000 | 1696225 | Oil cooler motor bearing is bad | 2017-04-17 13:50 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2017-06-14 12:02
1 | WTG-0060-0000 | 1696211 | GEARBOX OIL, Oil Sample | 2017-04-17 16:13 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | RATTLESNAKE |  | 2017-04-19 09:19
1 | WTG-0106-0000 | 1705854 | GEARBOX OIL, Fix oil leak | 2017-05-05 09:04 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | IAREBALO |  | 2017-05-22 11:09
1 | WTG-0021-0000 | 1706678 | GBX hose needs replace. Pump to cooler side. | 2017-05-08 16:02 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH |  | 2017-05-10 11:05
1 | WTG-0015-NS00-0000 | 1706707 | Oil leak on radiator plug. | 2017-05-08 17:14 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE2 |  | 2017-08-24 15:49
3 | WTG-0031-NDGP-0000 | 1706960 | GEARBOX OIL, Replace oil pump | 2017-05-09 17:10 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2017-05-10 08:19
3 | WTG-0011-NDG0-0000 | 2256959 | gearbox coupler inspection port | 2020-08-07 17:01 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2020-09-02 08:23
4 | WTG-0024-NDG0-0000 | 1740062 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:10 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-07-18 16:33
1 | WTG-0075-NDGP-0000 | 1139060 | Needs pump inversion ( leaking) | 2015-05-13 15:08 | Closed | GBXOIL | GBXOILLEAK | GREXP | JDISS |  | 2015-12-18 15:21
1 | WTG-0036-0000 | 1140722 | Replace Gear Pump Motor | 2015-05-21 10:03 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | SRIGGIN |  | 2015-05-22 09:58
4 | WTG-0010-NDGP-0000 | 1147397 | Leaky gearbox oil pump | 2015-06-04 12:50 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | PMASAKI |  | 2015-06-04 13:56
9 | WTG-0073-0000 | 1153859 | Radiator Cooler Oil Leak Found- Winenergy | 2015-06-26 17:26 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2016-07-20 13:41
1 | WTG-0040A-NDGP-0000 | 1161122 | GEARBOX OIL, Fix oil leak, OIL PUMP LEAK | 2015-07-14 11:25 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ACARR |  | 2015-07-17 10:50
1 | WTG-0014-ND00-0000 | 1169550 | GEARBOX OIL, Fix oil leak | 2015-08-05 09:53 | Closed | GBXOIL | GBXOILLEAK | MCADOO | IMORALES |  | 2015-08-20 10:57
1 | WTG-0041-NDGP-0000 | 1190913 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2015-10-13 11:51 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | SBURGESS |  | 2015-10-22 15:09
1 | WTG-0010-NDGP-0000 | 1210809 | GEARBOX OIL, Particle counter troubleshooting | 2015-11-30 09:47 | Closed | GBXOIL | GBXPARTINS | STANTON | MSNOW |  | 2016-01-18 13:59
1 | WTG-0027-NDGP-0000 | 1093542 | Offline Filter Installation | 2015-02-13 16:19 | Closed | GBXOIL | GBXFILTINS | MIAMI 1 | LPORTER |  | 2015-02-17 13:11
1 | WTG-0065-0000 | 1118712 | gearbox oil cooler leaking | 2015-04-08 08:09 | Closed | GBXOIL | GBXOILLEAK | MCADOO | JZARATE |  | 2015-04-08 15:04
1 | GBX-000005 | 1118079 | oil sample | 2015-04-03 19:38 | Closed | GBXOIL | GBXOILSAMP | PRAIRIE BREEZE | JFERRIS |  | 2015-04-06 16:35
3 | WTG-0081-0000 | 1300078 | Install secondary filtration system on gearbox oil | 2016-06-24 12:14 | Closed | GBXOIL | GBXFILTINS | GOLDTHWAITE | JDWILLIAMS | 1 | 2016-11-10 13:49
1 | WTG-0049-NDGP-0000 | 1243175 | GEARBOX OIL, Install oil cooler filter pad | 2016-02-15 13:57 | Closed | GBXOIL | GBXOILCOOL | MCADOO | RROBERTS |  | 2016-02-22 08:46
1 | WTG-0204A-NDGP-0000 | 1159596 | GEARBOX OIL, Fix oil leak | 2015-07-07 10:16 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ACARR |  | 2015-07-09 07:28
1 | WTG-0047-0000 | 1162731 | GEARBOX OIL, Fix oil leak | 2015-07-24 15:53 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | CCOTTINGHAM |  | 2015-12-07 18:15
1 | WTG-0030-0000 | 1182682 | GEARBOX OIL, Oil Sample | 2015-09-24 14:59 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | SEVANS |  | 2015-09-30 14:54
1 | WTG-0047-NDGP-0000 | 1252701 | Winergy Gearbox Oil Pump and Motor Inversion Kit | 2016-03-15 13:00 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MMCCABE |  | 2016-03-22 06:44
4 | WTG-0012-NDG0-0000 | 1252698 | GEARBOX OIL, Replace oil pump | 2016-03-15 14:26 | Closed | GBXOIL | GBXOILCOOL | FORWARD | ACASPER |  | 2016-03-18 10:21
2 | WTG-0065-NDGP-0000 | 1259688 | GEARBOX OIL, Particle counter installation | 2016-04-05 10:01 | Closed | GBXOIL | GBXPARTINS | MCADOO | MSNOW |  | 2016-04-25 10:47
1 | WTG-0113-0000 | 1234750 | Gearbox Oil Work/Issue | 2016-01-29 15:07 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | SLILL |  | 2016-02-01 11:04
1 | WTG-0113-0000 | 1234751 | GEARBOX OIL, Fix oil leak | 2016-01-29 15:08 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2016-02-01 11:05
3 | WTG-0033-NDGP-0000 | 1676243 | GEARBOX OIL, Replace oil pump | 2017-02-24 13:00 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2018-02-20 13:15
3 | WTG-0086-NDGP-0000 | 1676244 | GEARBOX OIL, Replace oil pump | 2017-02-24 13:01 | Cancelled | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2018-11-15 16:39
1 | WTG-0116-0000 | 1676316 | GEARBOX OIL, Replace oil cooler hose | 2017-02-25 12:20 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-02-27 11:31
1 | GBX-000003 | 1681571 | GEARBOX OIL, Oil Sample | 2017-03-03 13:25 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS I | BWORLEY |  | 2017-03-03 16:20
1 | WTG-0021-0000 | 1682221 | Gearbox overtemp | 2017-03-06 15:25 | Closed | GBXOIL | GBXOILCOOL | CAL RIDGE | RWALL |  | 2017-04-03 14:00
4 | WTG-0058-NDGP-0000 | 1684687 | GEARBOX OIL, Replace oil motor/pump coupler | 2017-03-17 10:34 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-03-24 12:23
2 | WTG-0052-NDGP-0000 | 1685904 | GEARBOX OIL, Replace oil cooler | 2017-03-23 14:54 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2017-06-30 16:36
4.2 | WTG-0086-NDGP-0000 | 1687726 | Replace Heat Exchanger | 2017-03-29 14:51 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2017-04-03 06:59
4 | WTG-0009-NDGP-0000 | 1691112 | GEARBOX OIL, Replace pump | 2017-04-04 11:52 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-04-11 09:59
4.2 | WTG-0006-NDGP-0000 | 1692525 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2017-04-04 12:49 | Closed | GBXOIL | GBXOILCOOL | FORWARD | CMITCHELL |  | 2017-07-11 11:16
4 | WTG-0026-NDGP-0000 | 1693192 | Replace oil pump seal | 2017-04-06 08:29 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | WOLVERINECREEK |  | 2017-04-06 11:00
3 | WTG-0072-NDGP-0000 | 1693677 | GEARBOX OIL, Replace oil pump | 2017-04-07 11:47 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2018-10-01 15:40
2 | WTG-0022-NDGP-0000 | 1694229 | GEARBOX OIL, Replace Radiator | 2017-04-10 13:35 | Closed | GBXOIL | GBXOILCOOL | TURKEY TRACK | JBRILEY |  | 2017-05-15 15:50
1 | WTG-0002-NDGP-0000 | 1697111 | GEARBOX OIL, Fix oil leak | 2017-04-21 15:13 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | ALUNA |  | 2017-04-30 13:28
1 | WTG-0011-NDGP-0000 | 1697123 | GEARBOX OIL, Fix oil leak | 2017-04-21 15:25 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JMORENO |  | 2017-04-30 13:28
1 | WTG-0007-NDGP-0000 | 1697292 | Gearbox Oil Work/Issue | 2017-04-24 07:49 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | DSLITTLE |  | 2017-05-22 11:09
1 | WTG-0076-0000 | 1698803 | GEARBOX OIL, Fix oil leak | 2017-04-25 12:01 | Closed | GBXOIL | GBXOILLEAK | MCADOO | BJAMESON |  | 2017-05-02 09:55
1 | WTG-0014-0000 | 1700356 | Gearbox Oil Secondary Filter System Element Change | 2017-04-28 16:36 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | BUCKEYE | 1 | 2017-06-14 14:24
4 | WTG-0205-NDG0-0000 | 1700154 | GEARBOX OIL, Add/Top-Off 5 gals | 2017-04-28 10:52 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2018-01-03 14:20
5 | WTG-0060-0000 | 1703714 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:11 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | RTROBERTS |  | 2017-05-22 11:09
5 | WTG-0072-0000 | 1703722 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:19 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | RTROBERTS |  | 2017-09-07 12:15
1 | WTG-0091-NDGP-0000 | 1703734 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:28 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | IMORALES |  | 2017-05-22 11:09
1 | WTG-0083-0000 | 1703723 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:20 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | IAREBALO |  | 2017-05-22 11:09
1 | WTG-0050-0000 | 1703991 | GEARBOX OIL, Fix oil leak | 2017-05-02 15:51 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JJOHNSON |  | 2017-05-22 11:09
1 | WTG-0E07-NDGP-0000 | 1704755 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2017-05-03 12:24 | Closed | GBXOIL | GBXOILCOOL | BEECH RIDGE | KDEMPSEY |  | 2017-05-04 07:55
1 | WTG-0072-0000 | 1705621 | GEARBOX OIL, Fix oil leak | 2017-05-04 13:10 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | IAREBALO |  | 2017-05-22 11:09
4 | WTG-0047-NDG0-0000 | 1706067 | GEARBOX OIL, Add/Top-Off. 5gal | 2017-05-05 12:49 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2017-06-21 10:26
1 | WTG-0059-NDGP-0000 | 1706155 | GEARBOX OIL, Fix oil leak | 2017-05-05 16:12 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDKEY |  | 2017-05-22 11:09
1 | WTG-0140-0000 | 1706140 | GEARBOX OIL, Fix oil leak | 2017-05-05 15:56 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | RTROBERTS |  | 2017-05-22 11:09
1 | WTG-0130-0000 | 1706081 | GEARBOX OIL, Fix oil leak | 2017-05-05 14:39 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | LBENAVIDES |  | 2017-05-22 11:09
1 | WTG-0129-0000 | 1706107 | GEARBOX OIL, Fix oil leak | 2017-05-05 15:26 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDEWEESE |  | 2017-05-22 11:08
3 | WTG-0027-NDGP-0000 | 1708670 | Install low oil cut out/ Oil Sample Valve | 2017-05-17 16:57 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-06-08 09:53
1 | WTG-0218-0000 | 1709199 | GEARBOX OIL, Fix oil leak, shaft seal | 2017-05-20 08:12 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2019-12-23 15:42
2 | WTG-0022-0000 | 1709816 | GEARBOX OIL, Secondary filter system installation | 2017-05-23 08:32 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | BUCKEYE |  | 2017-06-14 14:18
1 | WTG-0006-NDG0-0000 | 1709819 | GEARBOX OIL, Fix oil leak | 2017-05-23 08:47 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | BWHEELER |  | 2017-05-31 10:08
1 | SITE-HSEC | 1710827 | GEARBOX OIL, Oil Sample CT-320 | 2017-05-25 12:16 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2017-05-30 10:01
3 | WTG-0017-NDG0-0000 | 2256960 | gearbox coupler inspection port | 2020-08-07 17:02 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2020-12-17 16:58
2 | WTG-0038-0000 | 1822615 | Add Oil to Gearbox | 2017-12-17 16:35 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-10 09:06
5 | WTG-0026-NDGP-0000 | 1717854 | Replace Diode Suppressor on oil pump contactor | 2017-06-07 13:49 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | MSTONER |  | 2017-08-14 15:21
2 | WTG-0015-NDGP-0000 | 1728632 | GBX Oil Filter Housing needs replacement | 2017-06-07 17:19 | Closed | GBXOIL | GBXFILTELEM | GOLDTHWAITE | JDWILLIAMS |  | 2018-02-07 14:52
1 | WTG-0016-NDG0-0000 | 1734722 | GEARBOX OIL, Fix oil leak | 2017-06-09 15:50 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | NHEITHOFF |  | 2017-08-29 16:43
2 | WTG-0017-NDGP-0000 | 1734714 | GEARBOX OIL, Replace oil cooler | 2017-06-09 15:14 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2018-04-13 13:45
1 | WTG-0006-NDGP-0000 | 1736327 | Gearbox Oil Work/Issue | 2017-06-14 16:31 | Closed | GBXOIL | GBXPARTREM | JUDITH GAP | JUDITHGAP |  | 2018-02-27 08:30
1 | WTG-0073-0000 | 1736486 | GEARBOX OIL, Fix oil leak | 2017-06-14 10:57 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KMCLELAND |  | 2017-06-16 07:25
2 | WTG-0082-0000 | 1737085 | Gearbox low on oil | 2017-06-19 07:50 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | FANAYA |  | 2017-10-19 09:49
1 | WTG-0058-0000 | 1737170 | GEARBOX OIL, Fix oil leak | 2017-06-19 14:35 | Closed | GBXOIL | GBXOILLEAK | STANTON | DKEETON |  | 2017-06-21 17:39
5 | WTG-0053-NDGP-0000 | 1737111 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2017-06-19 10:41 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-06-26 15:22
1 | WTG-0048-0000 | 1738691 | GEARBOX OIL, Fix oil leak | 2017-06-23 15:35 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | DANDERSON |  | 2017-08-22 15:12
1 | WTG-0070-0000 | 1738555 | Gearbox oil overtemp | 2017-06-23 06:57 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | CBENNETT |  | 2017-06-23 08:32
1 | WTG-0069-0000 | 1739437 | GEARBOX OIL, Fix oil leak | 2017-06-26 17:16 | Closed | GBXOIL | GBXOILLEAK | BETHEL | ACHAVIRA |  | 2017-06-28 17:24
1 | WTG-0063-NDG0-0000 | 1740031 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 16:52 | Cancelled | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-06-27 16:54
4 | WTG-0005-NDG0-0000 | 1740037 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 16:59 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-07-28 09:01
4 | WTG-0006-NDG0-0000 | 1740038 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 16:59 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-07-07 15:52
4 | WTG-0007-NDG0-0000 | 1740040 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 16:59 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-08-09 06:53
4 | WTG-0002-NDG0-0000 | 1740054 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:04 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-07-28 17:16
4 | WTG-0040-NDG0-0000 | 1740079 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:14 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-07 07:38
4 | WTG-0044-NDG0-0000 | 1740082 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:14 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-10-02 07:25
4 | WTG-0049-NDG0-0000 | 1740085 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:15 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-07-07 11:24
4 | WTG-0065-NDG0-0000 | 1740099 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:18 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2018-06-07 15:30
4 | WTG-0017-NDG0-0000 | 1740048 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:01 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-09-11 19:29
4 | WTG-0018-NDG0-0000 | 1740049 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:02 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-07-17 13:34
4 | WTG-0019-NDG0-0000 | 1740050 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:02 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-07-17 13:33
4 | WTG-0020-NDG0-0000 | 1740051 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:02 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-07-17 15:35
4 | WTG-0015-NDG0-0000 | 1740052 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:03 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-08-03 07:52
4 | WTG-0025-NDG0-0000 | 1740063 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:10 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-10-04 17:45
4 | WTG-0051-NDG0-0000 | 1740086 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:16 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-17 07:40
4 | WTG-0052-NDG0-0000 | 1740087 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:16 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-20 09:19
4 | WTG-0054-NDG0-0000 | 1740089 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:16 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-12-05 07:40
4 | WTG-0032-NDG0-0000 | 1740071 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:12 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-10-02 07:25
4 | WTG-0034-NDG0-0000 | 1740073 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:12 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-03 07:52
4 | WTG-0036-NDG0-0000 | 1740075 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:13 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-03 07:52
4 | WTG-0037-NDG0-0000 | 1740076 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:13 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-07-19 17:07
4 | WTG-0039-NDG0-0000 | 1740078 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:13 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-06 09:16
4 | WTG-0048-NDG0-0000 | 1740084 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:15 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-07-10 18:19
4 | WTG-0066-NDG0-0000 | 1740101 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:19 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-12-08 07:43
4 | WTG-0059-NDG0-0000 | 1740094 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:17 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-12-04 07:37
4 | WTG-0061-NDG0-0000 | 1740096 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:18 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-12-22 08:10
4 | WTG-0062-NDG0-0000 | 1740097 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:18 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-12-07 07:36
4 | WTG-0014-NDG0-0000 | 1740046 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:01 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-09-11 08:42
4 | WTG-0016-NDG0-0000 | 1740047 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:01 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-08-03 07:53
4 | WTG-0009-NDG0-0000 | 1740053 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:04 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-07-19 17:08
4 | WTG-0022-NDG0-0000 | 1740061 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:10 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-07-07 15:52
4 | WTG-0027-NDG0-0000 | 1740065 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:11 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-07-12 16:49
4 | WTG-0038-NDG0-0000 | 1740077 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:13 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-07-28 09:00
4 | WTG-0042-NDG0-0000 | 1740081 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:14 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-08 07:38
4 | WTG-0058-NDG0-0000 | 1740093 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:17 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-12-05 07:40
4 | WTG-0045-NDG0-0000 | 1740083 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:15 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-10 07:50
4 | WTG-0055-NDG0-0000 | 1740090 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:17 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-30 09:07
4 | WTG-0057-NDG0-0000 | 1740092 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:17 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-08-07 16:16
4 | WTG-0064-NDG0-0000 | 1740098 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:18 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-12-07 07:36
4 | WTG-0067-NDG0-0000 | 1740100 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:19 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2018-06-12 07:58
4 | WTG-0023-NDG0-0000 | 1740102 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:20 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-07-05 16:11
4 | WTG-0047-NDG0-0000 | 1740103 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:21 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-13 07:37
4 | WTG-0060-NDG0-0000 | 1740095 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:18 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-07-13 16:12
4 | WTG-0026-NDG0-0000 | 1740064 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:11 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-08-03 07:52
4 | WTG-0029-NDG0-0000 | 1740068 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:11 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-07 07:38
4 | WTG-0035-NDG0-0000 | 1740074 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:13 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-03 07:52
4 | WTG-0050-NDG0-0000 | 1740104 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:22 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-16 07:39
4 | WTG-0041-NDG0-0000 | 1740080 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:14 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-07 07:38
4 | WTG-0021-NDG0-0000 | 1740060 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:10 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-09-19 08:40
4 | WTG-0028-NDG0-0000 | 1740067 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:11 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-07-24 16:55
4 | WTG-0030-NDG0-0000 | 1740069 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:12 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-10-02 07:26
4 | WTG-0031-NDG0-0000 | 1740070 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:12 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-03 07:52
4 | WTG-0033-NDG0-0000 | 1740072 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:12 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-11-03 07:52
4 | WTG-0053-NDG0-0000 | 1740088 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:16 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-07-14 14:44
4 | WTG-0056-NDG0-0000 | 1740091 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 17:17 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CMORRIS |  | 2017-12-05 07:40
4.2 | WTG-0115-0000 | 1760066 | GEARBOX, Amsoil Change | 2017-08-11 14:33 | Closed | GBXOIL | GBXOILCHG | CAMP SPRINGS II | AMAXWELL |  | 2018-03-02 08:49
4.2 | WTG-0128-0000 | 1760069 | GEARBOX, Amsoil Change | 2017-08-11 14:37 | Closed | GBXOIL | GBXOILCHG | CAMP SPRINGS II | AMAXWELL |  | 2017-09-21 18:12
4.2 | WTG-0136-0000 | 1760070 | GEARBOX, Amsoil Change | 2017-08-11 14:38 | Closed | GBXOIL | GBXOILCHG | CAMP SPRINGS II | AMAXWELL |  | 2018-03-23 18:41
5 | WTG-0049-0000 | 1760017 | GEARBOX OIL, Check Nanjing replacement hose condition | 2017-08-11 14:07 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | AMAXWELL |  | 2017-11-14 07:20
1 | WTG-0087-NDGP-0000 | 1763870 | Install secondary filtration system on gearbox oil | 2017-08-18 14:47 | Closed | GBXOIL | GBXFILTINS | MCADOO | RROBERTS | 1 | 2017-09-13 16:39
2 | WTG-0078-0000 | 1766296 | GEARBOX OIL, Secondary filter system element change | 2017-08-28 14:29 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-08-30 07:15
1 | WTG-0317-0000 | 1775488 | GEARBOX OIL, Fix oil leak | 2017-09-19 09:19 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | CBORER |  | 2017-09-22 16:35
1 | WTG-0225-0000 | 1775526 | GEARBOX OIL, Fix oil leak | 2017-09-19 09:32 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | CBORER |  | 2017-09-22 16:35
1 | WTG-0022-NDG0-0000 | 1776467 | GEARBOX OIL, Particle counter installation | 2017-09-20 15:35 | Closed | GBXOIL | GBXPARTINS | MCADOO | TRUDE |  | 2017-09-22 10:24
1 | WTG-0024-NDG0-0000 | 1799691 | GEARBOX OIL, Oil Sample | 2017-11-09 15:25 | Closed | GBXOIL | GBXOILSAMP | ORANGEVILLE | MSNOW |  | 2018-06-19 10:00
5 | WTG-0063A-NDGP-0000 | 2191558 | Replace lube pump insert/coupler | 2020-02-27 16:42 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2020-08-19 11:34
4.2 | WTG-0009-NDGP-0000 | 1745936 | Rplace Gearbox Oil Filter | 2017-07-07 08:54 | Closed | GBXOIL | GBXOILSAMP | WOLVERINE CREEK | WOLVERINECREEK |  | 2018-05-07 16:57
1 | WTG-0035-NDG0-0000 | 1850607 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2018-03-07 14:34 | Closed | GBXOIL | GBXOILCOOL | MCADOO | MCADOO |  | 2018-03-16 14:36
2 | WTG-0077-NDGP-0000 | 1746902 | GEARBOX OIL, Replace oil pump | 2017-07-10 14:43 | Cancelled | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2017-11-10 15:27
1 | WTG-0050-NDGP-0000 | 1749102 | GEARBOX OIL, Replace oil cooler hose | 2017-07-18 08:55 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | JHAVENS |  | 2017-07-19 07:26
1 | WTG-0001-NT00-0000 | 1751341 | Install Contactor for Secondary Oil Pump | 2017-07-24 16:50 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2017-07-25 10:51
2 | WTG-0076-NDGP-0000 | 1751417 | GEARBOX OIL, Particle counter installation | 2017-07-25 08:47 | Closed | GBXOIL | GBXPARTINS | GREXP | MSNOW |  | 2017-08-01 07:49
4.2 | WTG-0086-NDGP-0000 | 1753358 | Replace Heat Exchanger | 2017-07-26 13:57 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2017-07-27 08:39
4 | WTG-0075B-NDG0-0000 | 1753876 | GEARBOX OIL, Add/Top-Off | 2017-07-27 12:22 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2017-08-01 11:04
2 | WTG-0100-0000 | 1753894 | Oil Leak | 2017-07-27 16:06 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CSIPE |  | 2018-05-03 17:09
2 | WTG-0014-NDGP-0000 | 1754694 | Gearbox Oil Secondary Filter System Element Change | 2017-07-31 10:22 | Closed | GBXOIL | GBXFILTELEM | WOLVERINE CREEK | RBEBOUT | 1 | 2017-08-01 08:21
1 | WTG-0003-0000 | 1758298 | Clean up oil | 2017-08-04 10:48 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2018-04-11 14:34
2 | WTG-0074-NDGP-0000 | 1758234 | Gearbox Oil Secondary Filter System Element Change | 2017-08-01 12:59 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GBOTT | 1 | 2017-08-07 07:06
1 | WTG-0005-0000 | 1758302 | Need to replace oil cooler boot | 2017-08-04 13:37 | Closed | GBXOIL | GBXOILCOOL | CAL RIDGE | MWINGLER |  | 2017-08-16 20:31
2 | WTG-0024-NDG0-0000 | 1758174 | GEARBOX OIL, Add/Top-Off | 2017-08-04 10:45 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JFREEMAN |  | 2017-12-21 09:00
1 | WTG-0093-NDGP-0000 | 1759112 | Needs Pump Inversion | 2017-08-07 15:43 | Cancelled | GBXOIL | GBXOILLEAK | GREXP | JDISS |  | 2023-06-29 13:12
1 | WTG-0093-NDGP-0000 | 1759113 | GEARBOX OIL, Secondary filter system installation | 2017-08-07 15:51 | Closed | GBXOIL | GBXFILTINS | GREXP | JDISS |  | 2017-08-16 07:30
9 | WTG-0058-0000 | 1759789 | rFSA Claim - Pitch Tube Replacement by GE | 2017-08-10 13:36 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CSEIDER |  | 2017-09-12 13:21
9 | WTG-0014-0000 | 1759792 | rFSA Claim - Pitch Tube Replacement by GE | 2017-08-10 14:00 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CSEIDER |  | 2017-09-12 13:21
2 | WTG-0092-NDGP-0000 | 1759814 | GEARBOX OIL, Replace oil pump motor | 2017-08-10 15:22 | Cancelled | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2017-11-30 08:54
9 | WTG-0122-NDG0-0000 | 1759858 | GEARBOX, Oil Change | 2017-08-10 16:25 | Cancelled | GBXOIL | GBXOILCHG | CAMP SPRINGS II | JSULLIVAN |  | 2017-08-24 14:34
9 | WTG-0128-NDG0-0000 | 1759859 | GEARBOX, Oil Change | 2017-08-10 16:27 | Cancelled | GBXOIL | GBXOILCHG | CAMP SPRINGS II | JSULLIVAN |  | 2017-08-24 14:34
9 | WTG-0156-NDG0-0000 | 1759864 | GEARBOX, Oil Change | 2017-08-10 16:35 | Cancelled | GBXOIL | GBXOILCHG | CAMP SPRINGS II | JSULLIVAN |  | 2017-08-24 14:33
9 | WTG-0003-NDG0-0000 | 1759854 | GEARBOX, Oil Change | 2017-08-10 16:19 | Cancelled | GBXOIL | GBXOILCHG | CAMP SPRINGS I | JSULLIVAN |  | 2017-08-24 14:36
9 | WTG-0009-NDG0-0000 | 1759856 | GEARBOX, Oil Change | 2017-08-10 16:21 | Cancelled | GBXOIL | GBXOILCHG | CAMP SPRINGS I | JSULLIVAN |  | 2017-08-24 14:35
9 | WTG-0115-NDG0-0000 | 1759857 | GEARBOX, Oil Change | 2017-08-10 16:23 | Cancelled | GBXOIL | GBXOILCHG | CAMP SPRINGS II | JSULLIVAN |  | 2017-08-24 14:35
9 | WTG-0006-NDG0-0000 | 1759855 | GEARBOX, Oil Change | 2017-08-10 16:20 | Cancelled | GBXOIL | GBXOILCHG | CAMP SPRINGS I | JSULLIVAN |  | 2017-08-24 14:35
4 | WTG-0058-NDGP-0000 | 1763063 | Need band for oil cooler vent tube. | 2017-08-16 16:46 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2018-04-23 14:18
2 | WTG-0120-0000 | 1763026 | GEARBOX OIL, Secondary filter system element change | 2017-08-16 09:54 | Closed | GBXOIL | GBXFILTELEM | BISHOP HILL | ARUSHING |  | 2017-09-28 09:35
1 | WTG-0132-0000 | 1763027 | GEARBOX OIL, Secondary filter system installation | 2017-08-16 10:58 | Closed | GBXOIL | GBXFILTINS | BISHOP HILL | ARUSHING |  | 2017-09-28 09:35
1 | WTG-0030-0000 | 1769586 | GEARBOX OIL, Fix oil leak | 2017-09-02 10:36 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | BUCKEYE |  | 2017-09-30 10:48
1 | WTG-0002-0000 | 1772856 | GEARBOX OIL, Fix oil leak | 2017-09-08 12:24 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | MKRINGS |  | 2019-03-11 18:02
1 | WTG-0025-0000 | 1774294 | Replace Gearbox Hose | 2017-09-14 07:45 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2017-09-14 16:39
9 | WTG-0045-0000 | 1775008 | TERP GBX Oil Change | 2017-09-15 15:22 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE | AMELENGU | 1 | 2017-10-31 16:57
1 | WTG-0302-0000 | 1775486 | GEARBOX OIL, Fix oil leak | 2017-09-19 09:06 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | CBORER |  | 2017-09-22 16:35
1 | GBX-000113 | 1777229 | Replace oil cooler inlet hose | 2017-09-25 09:53 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | LPORTER |  | 2017-09-27 07:32
1 | WTG-0117-0000 | 1776863 | GEARBOX OIL, Fix oil leak | 2017-09-22 15:06 | Closed | GBXOIL | GBXOILLEAK | BETHEL | BETHEL |  | 2017-10-17 09:31
5 | WTG-0055A-NDG0-0000 | 1778936 | GEARBOX OIL, Add/Top-Off 5 gal | 2017-09-26 08:05 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2018-01-18 14:07
1 | WTG-0025-0000 | 1779809 | Gearbox Inspection | 2017-09-29 09:08 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | SMCCLEARY |  | 2017-11-28 15:44
1 | WTG-0032-0000 | 1782872 | GEARBOX OIL, Fix oil leak | 2017-10-02 14:25 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CWERNER
5 | WTG-0043-0000 | 1785539 | GEARBOX OIL, Particle counter installation | 2017-10-09 16:06 | Closed | GBXOIL | GBXPARTINS | GUNSIGHT | CMORRIS |  | 2018-06-21 17:08
5 | WTG-0048-0000 | 1785540 | GEARBOX OIL, Particle counter installation | 2017-10-09 16:09 | Closed | GBXOIL | GBXPARTINS | GUNSIGHT | CMORRIS |  | 2018-10-29 17:17
1 | WTG-0J05-NDGP-0000 | 1786163 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2017-10-11 11:21 | Closed | GBXOIL | GBXOILCOOL | BEECH RIDGE | KDEMPSEY |  | 2017-10-19 08:46
1 | WTG-0001-NDGP-0000 | 1786207 | Need to replace seal on top of off line filter | 2017-10-11 15:40 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | MFERRARO |  | 2018-11-13 12:55
5 | WTG-0094-0000 | 1788612 | GEARBOX OIL, Secondary filter system element change | 2017-10-19 14:29 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-10-24 11:12
5 | WTG-0095-0000 | 1788613 | GEARBOX OIL, Secondary filter system element change | 2017-10-19 14:30 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-10-24 11:12
5 | WTG-0097-0000 | 1788614 | GEARBOX OIL, Secondary filter system element change | 2017-10-19 14:30 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-10-24 11:12
4 | WTG-0024-NDGP-0000 | 1788641 | leaking secondary pump | 2017-10-19 15:54 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2018-06-18 12:54
2 | WTG-0017-0000 | 1793628 | GBX Filter Housing Leak Clean Up | 2017-10-27 15:47 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE | 30 | 2018-05-28 19:49
5 | WTG-0038-0000 | 1796047 | Replace Blue Oil Cooler Sox | 2017-10-31 14:39 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | MSTONER |  | 2018-02-14 09:47
2 | WTG-0155-0000 | 1799200 | GEARBOX OIL, Add/Top-Off | 2017-11-07 13:28 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JFREEMAN |  | 2017-11-08 14:59
2 | WTG-0128-0000 | 1799203 | GEARBOX OIL, Add/Top-Off | 2017-11-07 17:30 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JFREEMAN |  | 2017-11-08 15:00
2 | WTG-0008-0000 | 1809420 | Add Oil to Gearbox | 2017-12-08 09:11 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NSCHMEIDLER |  | 2017-12-20 10:33
2 | WTG-0106-0000 | 1814399 | Add Oil to Gearbox | 2017-12-14 09:59 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:49
2 | WTG-0039-0000 | 1814400 | Add Oil to Gearbox | 2017-12-21 10:04 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:49
2 | WTG-0111-0000 | 1814402 | Add Oil to Gearbox | 2017-12-15 10:10 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:47
2 | WTG-0085-0000 | 1814405 | Add Oil to Gearbox | 2017-12-16 10:14 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:43
1 | WTG-0032-0000 | 1814502 | GEARBOX OIL, Oil Sample | 2017-12-21 16:01 | Closed | GBXOIL | GBXOILSAMP | CAL RIDGE | JLAPPIN |  | 2017-12-22 14:52
2 | WTG-0086-0000 | 1814507 | Add Oil to Gearbox | 2017-12-18 16:33 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:42
2 | WTG-0092-0000 | 1814508 | Add Oil to Gearbox | 2017-12-18 16:35 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:41
2 | WTG-0056-0000 | 1814509 | Add Oil to Gearbox | 2017-12-19 16:37 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:40
4 | WTG-0029A-NDG0-0000 | 1967634 | GEARBOX OIL, Add/Top-Off 7 Gallons | 2018-10-31 15:05 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2019-03-08 14:49
1 | WTG-0025-NDG0-0000 | 1833515 | GEARBOX OIL, Particle counter installation | 2018-01-30 15:39 | Closed | GBXOIL | GBXPARTINS | MCADOO | RROBERTS |  | 2018-01-30 15:42
3 | WTG-0004-NDG0-0000 | 2258695 | GBX oil pump inversion | 2020-08-14 11:20 | Closed | GBXOIL | GBXOILCOOL | GORDON BUTTE | JUDITHGAP |  | 2021-08-13 10:42
2 | WTG-0007-NDGP-0000 | 1841378 | GEARBOX OIL, Fix oil leak | 2018-02-20 10:54 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | WILLOWCREEK |  | 2018-09-05 17:00
5 | WTG-0044-0000 | 1851560 | GEARBOX OIL, Fix oil leak secondary filtration o-ring | 2018-03-13 08:19 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | CJERNIGAN |  | 2019-03-11 08:09
5 | WTG-0205-NDGP-0000 | 1851508 | GEARBOX OIL, Fix oil leak on secondary filter | 2018-03-12 16:35 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2018-03-16 16:24
1 | WTG-0010-0000 | 1852916 | Gbx hose leak | 2018-03-19 15:20 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CRWADE |  | 2018-05-31 20:23
2 | WTG-0015-NDG0-0000 | 1856830 | GEARBOX OIL, Sample | 2018-03-29 10:02 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | MSNOW |  | 2018-09-10 17:46
1 | WTG-0079-ND00-0000 | 1862655 | Gearbox Oil Work/Issue | 2018-04-10 17:20 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TCARD |  | 2018-07-20 12:26
1 | WTG-0109-ND00-0000 | 1862958 | Gearbox Oil Work/Issue | 2018-04-12 14:02 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BSHOOK |  | 2018-07-20 12:37
1 | WTG-0108-ND00-0000 | 1863079 | Gearbox Oil Work/ Issue | 2018-04-13 08:46 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BSHOOK
1 | WTG-0078-0000 | 1865827 | Nacelle Belly Needs Cleaned | 2018-04-23 15:08 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON
4 | WTG-0097-NDGP-0000 | 1865836 | GEARBOX OIL, oil pump replacement | 2018-04-23 16:22 | Closed | GBXOIL | GBXOILCOOL | FORWARD | MPEARSON |  | 2018-05-02 10:23
4 | WTG-0029A-0000 | 1876468 | Replace Oil filter o-ring | 2018-05-23 10:54 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2019-03-08 14:46
1 | WTG-0178-NDGP-0000 | 1892829 | GEARBOX OIL, Particle counter troubleshooting | 2018-06-13 10:00 | Closed | GBXOIL | GBXPARTINS | CAMP SPRINGS II | MSNOW |  | 2018-12-17 16:33
4 | WTG-0038-NDG0-0000 | 1799533 | Gaskets for gearbox inspection covers. | 2017-11-09 07:38 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2018-03-02 16:13
1 | WTG-0062-0000 | 1801547 | PALL filter housing leak | 2017-11-16 12:09 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JRODGERS |  | 2018-03-19 08:41
1 | WTG-0062-0000 | 1801548 | Thermal bypass block leaking | 2017-11-16 12:10 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JRODGERS |  | 2018-03-19 08:41
1 | WTG-0094-NDG0-0000 | 1802092 | Gearbox Oil Work/Issue | 2017-11-20 12:59 | Closed | GBXOIL | EM225 | RONCEVAUX | RONCEVAUX |  | 2017-11-27 08:08
2 | WTG-0004-0000 | 1809419 | Add Oil to Gearbox | 2017-12-08 09:08 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NSCHMEIDLER |  | 2017-12-20 10:33
2 | WTG-0033-0000 | 1809711 | Add Oil to Gearbox | 2017-12-10 07:02 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NSCHMEIDLER |  | 2018-02-07 12:59
2 | WTG-0034-0000 | 1809712 | Add Oil to Gearbox | 2017-12-10 07:02 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NSCHMEIDLER |  | 2018-01-09 12:56
1 | SITE-VWEC | 1813150 | Hydraulic Oil Samples | 2017-12-15 10:52 | Closed | GBXOIL | GBXOILSAMP | VANTAGE | SRIGGIN |  | 2017-12-18 09:32
1 | WTG-0030-NDBS-0000 | 1813151 | Hydraulic Oil Samples | 2017-12-15 10:52 | Closed | GBXOIL |  | VANTAGE | SRIGGIN |  | 2017-12-18 09:32
1 | WTG-0041-NDBS-0000 | 1813152 | Hydraulic Oil Samples | 2017-12-15 10:52 | Closed | GBXOIL |  | VANTAGE | SRIGGIN |  | 2017-12-18 09:32
1 | WTG-0055-NDBS-0000 | 1813153 | Hydraulic Oil Samples | 2017-12-15 10:52 | Closed | GBXOIL |  | VANTAGE | SRIGGIN |  | 2017-12-18 09:32
4 | WTG-0098-NDGP-0000 | 1813298 | GEARBOX OIL, leak between pump and filter flange | 2017-12-16 05:41 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2018-02-02 10:29
2 | WTG-0075-0000 | 1814406 | Add Oil to Gearbox | 2017-12-16 10:18 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:43
4.2 | WTG-0131-NDGP-0000 | 1819953 | Install new O-ring on secondary filter housing | 2018-01-03 10:34 | Closed | GBXOIL | GBXOILLEAK | GRATIOT | GRATIOT |  | 2018-01-25 09:13
2 | WTG-0021-NDGP-0000 | 1820261 | GEARBOX OIL, Oil Sample | 2018-01-03 14:17 | Closed | GBXOIL | GBXOILSAMP | VANTAGE | MSNOW |  | 2018-04-16 09:35
2 | WTG-0033-NDGP-0000 | 1820262 | GEARBOX OIL, Oil Sample | 2018-01-03 14:20 | Closed | GBXOIL | GBXOILSAMP | VANTAGE | MSNOW |  | 2018-04-16 09:35
2 | WTG-0044-NDGP-0000 | 1820263 | GEARBOX OIL, Oil Sample | 2018-01-03 14:21 | Closed | GBXOIL | GBXOILSAMP | VANTAGE | MSNOW |  | 2018-04-16 09:36
2 | WTG-0059-NDGP-0000 | 1820264 | GEARBOX OIL, Oil Sample | 2018-01-03 14:22 | Closed | GBXOIL | GBXOILSAMP | VANTAGE | MSNOW |  | 2018-04-16 09:36
2 | WTG-0203B-TT00-0000 | 1821785 | Clean oil on tower decks | 2018-01-08 17:25 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2018-01-12 15:01
2 | WTG-0068-0000 | 1821740 | Add Oil to Gearbox | 2018-01-08 16:22 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:07
2 | WTG-0076-0000 | 1821741 | Add Oil to Gearbox | 2018-01-08 16:26 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:05
1 | WTG-0010-0000 | 1822866 | rFSA Claim for Pitch Tube Leak and UEA replacement | 2018-01-10 10:15 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2018-01-16 09:33
4 | WTG-0053-NDG0-0000 | 1826563 | Add 5 gallons Castrol oil | 2018-01-18 15:05 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2018-10-02 10:43
2 | WTG-0J07-NDG0-0000 | 1826650 | GEARBOX OIL, Particle counter installation | 2018-01-19 09:26 | Closed | GBXOIL | GBXPARTINS | BEECH RIDGE | SCLARK |  | 2018-02-26 14:49
1 | WTG-0080-0000 | 1830273 | Thermal bypass cap leaking | 2018-01-23 12:30 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2018-08-10 16:44
4 | WTG-0061-NDG0-0000 | 1832463 | GEARBOX OIL, Fix oil leak. Put pail under gearbox planetary | 2018-01-29 18:32 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2019-02-27 16:15
2 | WTG-0A14-NDGP-0000 | 1837990 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:11 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-03-30 07:13
2 | WTG-0F08-NDGP-0000 | 1837996 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:23 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-06-13 11:36
2 | WTG-0G05-NDGP-0000 | 1837998 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:25 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-06-15 12:21
4 | WTG-0044-0000 | 1838054 | GEARBOX OIL, Fix oil leak/Clean decks | 2018-02-05 16:32 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2018-10-05 09:28
2 | WTG-0J01-NDGP-0000 | 1838005 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:32 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-03-05 08:03
2 | WTG-0B07-NDGP-0000 | 1837994 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:20 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-05-07 07:50
2 | WTG-0G17-NDGP-0000 | 1838001 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:29 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-06-29 08:25
1 | WTG-0106-NDG0-0000 | 1844820 | gearbox hose leak | 2018-02-27 07:55 | Closed | GBXOIL |  | RONCEVAUX | RONCEVAUX |  | 2018-03-29 08:22
1 | WTG-0025-NDG0-0000 | 1846134 | GEARBOX OIL, Particle counter troubleshooting | 2018-02-28 14:10 | Closed | GBXOIL | GBXPARTINS | MCADOO | MSNOW |  | 2018-03-16 14:35
1 | WTG-0088-NDGP-0000 | 1846137 | GEARBOX OIL, Particle counter troubleshooting | 2018-02-28 14:18 | Closed | GBXOIL | GBXPARTINS | MCADOO | MSNOW |  | 2018-03-01 11:03
1 | WTG-0072-NDGP-0000 | 1846139 | GEARBOX OIL, Particle counter troubleshooting | 2018-02-28 14:23 | Closed | GBXOIL | GBXPARTINS | MCADOO | MSNOW |  | 2018-03-01 11:02
5 | WTG-0026-NDGP-0000 | 1846432 | Oil Pump Replacement | 2018-02-28 17:09 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2018-05-29 14:02
4 | WTG-0041A-NDG0-0000 | 1852266 | GEARBOX OIL, Add/Top-Off | 2018-03-14 12:13 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2018-03-16 16:27
4.2 | WTG-0078-NDGP-0000 | 1853754 | Replace Gearbox Heat Exchanger | 2018-03-23 07:33 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2018-04-04 07:23
2 | WTG-0023-NDG0-0000 | 1856812 | GEARBOX OIL, Add/Top-Off | 2018-03-29 09:48 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | MSNOW |  | 2018-07-17 08:23
2 | WTG-0030-NDG0-0000 | 1856813 | GEARBOX OIL, Add/Top-Off | 2018-03-29 09:49 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | MSNOW |  | 2018-05-14 15:20
2 | WTG-0077-NDG0-0000 | 1856819 | GEARBOX OIL, Add/Top-Off | 2018-03-29 09:54 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | MSNOW |  | 2018-11-02 16:29
2 | WTG-0021-NDG0-0000 | 1856828 | GEARBOX OIL, Sample | 2018-03-29 10:02 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | MSNOW |  | 2018-09-10 17:48
2 | WTG-0039-NDG0-0000 | 1856816 | GEARBOX OIL, Add/Top-Off | 2018-03-29 09:52 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | MSNOW |  | 2018-04-21 22:14
2 | WTG-039E-NDG0-0000 | 1856821 | GEARBOX OIL, Sample | 2018-03-29 09:58 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | MSNOW |  | 2018-09-10 17:51
2 | WTG-0039-NDG0-0000 | 1856823 | GEARBOX OIL, Sample | 2018-03-29 09:59 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | MSNOW |  | 2018-09-10 17:49
2 | WTG-0060-NDGP-0000 | 1859535 | l secondary filtration system need O-ring | 2018-04-03 14:51 | Closed | GBXOIL | GBXFILTELEM | TURKEY TRACK | TURKEY TRACK | 1 | 2018-10-27 21:42
1 | WTG-0028-NDG0-0000 | 1861804 | EM: Gearbox oil overtemperature | 2018-04-06 13:15 | Closed | GBXOIL | EM77 | RATTLESNAKE 1 | TCARD |  | 2018-04-16 12:12
2 | WTG-0019-0000 | 1861887 | Replace drain valve on bottom of oil filter canister | 2018-04-06 15:10 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | JURSUA |  | 2018-04-10 16:16
1 | WTG-0105-ND00-0000 | 1862832 | Gearbox Oil Work/ Issue | 2018-04-11 14:06 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | AVILLARREAL
1 | WTG-0001-ND00-0000 | 1862663 | Gearbox Oil Work/Issue | 2018-04-10 16:57 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TMORRIS |  | 2018-07-20 11:45
1 | WTG-0100-ND00-0000 | 1862835 | Gearbox Oil Work/ Issue | 2018-04-11 15:34 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | AVILLARREAL
1 | WTG-0004-0000 | 1862868 | GEARBOX OIL, Fix oil leak | 2018-04-11 17:38 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BDIAZ |  | 2018-04-12 15:58
1 | WTG-0004-0000 | 1862869 | GEARBOX OIL, Fix oil leak | 2018-04-11 17:38 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BDIAZ |  | 2018-04-12 15:58
1 | WTG-0004-0000 | 1862870 | GEARBOX OIL, Fix oil leak | 2018-04-11 17:38 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BDIAZ |  | 2018-04-12 15:57
1 | WTG-0004-0000 | 1862871 | Gearbox Oil Work/Issue | 2018-04-11 17:38 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BDIAZ |  | 2018-07-20 11:46
1 | WTG-0087-ND00-0000 | 1862885 | Gearbox Oil Work/Issue | 2018-04-11 17:45 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TCARD |  | 2018-07-20 12:35
1 | WTG-0103-ND00-0000 | 1862834 | Gearbox Oil Work/ Issue | 2018-04-11 15:33 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | AVILLARREAL
1 | WTG-0092-ND00-0000 | 1862883 | Gearbox Oil Work/Issue | 2018-04-11 17:42 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TCARD |  | 2018-07-20 12:37
1 | WTG-0093-0000 | 1862888 | GEARBOX OIL, Fix oil leak/replace oil filter housing | 2018-04-11 18:08 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | AHOFFMANN |  | 2018-05-04 16:57
1 | WTG-0113-ND00-0000 | 1862840 | Gearbox Oil Work/Issue | 2018-04-11 16:22 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | AVILLARREAL |  | 2018-07-20 12:40
1 | WTG-0073-ND00-0000 | 1863425 | Gearbox Oil Work/Issue | 2018-04-13 16:23 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TCARD |  | 2018-07-20 12:21
5 | WTG-0058-NDGP-0000 | 1863345 | Oil Pump Replacement | 2018-04-13 12:28 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | SENGLAND |  | 2018-07-12 10:15
1 | WTG-0054-NDGP-0000 | 1863333 | EM: Gearbox oil overtemperature | 2018-04-13 12:04 | Closed | GBXOIL | EM77 | GUNSIGHT | JELLIS |  | 2018-04-13 17:02
1 | WTG-0021-0000 | 1864277 | rFSA Claim for leaking Pitch Tube Seals | 2018-04-18 10:49 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2018-05-16 09:16
2 | WTG-0052-N000-0000 | 1865058 | Install secondary oil filtration system | 2018-04-20 14:58 | Closed | GBXOIL | GBXFILTINS | GRAND RIDGE | MFERRARO |  | 2018-09-17 13:56
5 | WTG-0212-NDGP-0000 | 1866585 | GEARBOX OIL, Add/Top-Off 5 gals | 2018-04-25 17:33 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2018-07-02 15:16
2 | WTG-0052-NDGP-0000 | 1871255 | Secondary oil sytem oil pump leaking | 2018-05-03 11:31 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | JUDITHGAP |  | 2018-08-08 08:04
1 | WTG-0042-0000 | 1871789 | GEARBOX OIL, Oil Sample | 2018-05-04 14:40 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | BISHOP HILL |  | 2018-05-09 08:06
2 | WTG-0032-0000 | 2032442 | GEARBOX OIL, Fix oil leak | 2019-02-05 13:32 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | UPSTREAM |  | 2020-06-03 10:41
2 | WTG-0024-0000 | 1874837 | Add Gearbox oil | 2018-05-13 16:52 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | GOLDTHWAITE |  | 2018-05-17 14:49
2 | WTG-0021-NDGP-0000 | 1874986 | GEARBOX OIL, Oil Sample | 2018-05-16 10:58 | Closed | GBXOIL | GBXOILSAMP | VANTAGE | MSNOW |  | 2018-05-29 10:54
4 | WTG-0043-NDG0-0000 | 1887701 | GEARBOX OIL, Add/Top-Off 5 gals | 2018-06-05 19:23 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2018-06-12 11:17
1 | WTG-0024-0000 | 1887687 | GEARBOX OIL, Fix oil leak | 2018-06-05 17:55 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS |  | 2018-06-06 18:09
1 | WTG-0165-NDGP-0000 | 1892828 | GEARBOX OIL, Particle counter troubleshooting | 2018-06-13 10:00 | Closed | GBXOIL | GBXPARTINS | CAMP SPRINGS II | MSNOW |  | 2019-03-12 09:52
1 | WTG-0112-NDGP-0000 | 1892830 | GEARBOX OIL, Particle counter troubleshooting | 2018-06-13 10:01 | Closed | GBXOIL | GBXPARTINS | BISHOP HILL | MSNOW |  | 2019-01-02 09:45
1 | WTG-0076-NDGP-0000 | 1892831 | GEARBOX OIL, Particle counter troubleshooting | 2018-06-13 10:02 | Closed | GBXOIL | GBXPARTINS | GREXP | MSNOW |  | 2018-11-27 16:19
1 | WTG-0111-0000 | 1892706 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2018-06-12 15:32 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | KMCLELAND |  | 2018-09-06 09:17
2 | WTG-0088-NDGP-0000 | 1893369 | GEARBOX OIL, Particle counter troubleshooting | 2018-06-14 10:40 | Closed | GBXOIL | GBXPARTINS | MCADOO | MSNOW |  | 2018-07-05 11:53
1 | WTG-0045-0000 | 1894023 | rFSA claim for Gearbox front seal | 2018-06-18 15:13 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2018-11-27 15:27
4 | WTG-0035-0000 | 1921744 | GEARBOX OIL, Add 5 Gal or Less | 2018-07-06 06:43 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2018-11-13 12:01
2 | 013D110 | 1921756 | oil change cooling tower 10 gearbox | 2018-07-06 08:01 | Closed | GBXOIL |  | NELSON | RWEIDEL |  | 2018-07-29 12:57
5 | WTG-0225-0000 | 1922147 | GEARBOX OIL, add oil | 2018-07-06 16:57 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE3 |  | 2019-06-28 14:03
1 | WTG-0032-NDGP-0000 | 1925741 | GEARBOX OIL, Oil Sample | 2018-07-18 09:14 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | MSNOW |  | 2018-11-13 12:34
9 | WTG-0065-0000 | 1925751 | GEARBOX, Oil Change | 2018-07-18 10:04 | Closed | GBXOIL | GBXOILCHG | GOLDTHWAITE | GOLDTHWAITE |  | 2018-07-18 10:22
2 | WTG-0034-NDGP-0000 | 1925448 | Gearbox oil Secondary Filter System Element Change | 2018-07-17 08:36 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | JUDITHGAP |  | 2018-07-18 10:17
5 | WTG-0J07-NDG0-0000 | 1925990 | GEARBOX OIL, Particle counter removal | 2018-07-19 12:02 | Closed | GBXOIL | GBXPARTREM | BEECH RIDGE | SCLARK |  | 2018-09-05 12:50
1 | SITE-CREC | 1926405 | Clean clogged door filters from OT towers | 2018-07-21 11:16 | Cancelled | GBXOIL | BLANK | CAL RIDGE | JCANN
4 | GBX-FDMD-4142 | 1926755 | OIL SAMPLES, WTG Major A Gen Align PM w/ M2 | 2018-07-23 14:24 | Closed | GBXOIL |  | BUCKEYE | SBROWNING |  | 2020-06-01 11:20
9 | WTG-0126-0000 | 1929734 | GEARBOX, Oil Change | 2018-07-30 09:40 | Closed | GBXOIL | GBXOILCHG | BISHOP HILL | BISHOP HILL |  | 2018-08-03 08:19
9 | WTG-0132-0000 | 1929736 | GEARBOX, Oil Change | 2018-07-30 09:45 | Closed | GBXOIL | GBXOILCHG | BISHOP HILL | BISHOP HILL |  | 2018-08-03 08:19
9 | WTG-0133-0000 | 1929739 | GEARBOX, Oil Change | 2018-07-30 09:47 | Closed | GBXOIL | GBXOILCHG | BISHOP HILL | BISHOP HILL |  | 2018-08-03 08:19
1 | GBX-000043 | 1930547 | EM: Gearbox oil overtemperature | 2018-07-30 16:11 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | GOLDTHWAITE |  | 2018-11-02 16:26
2 | WTG-0033-NDG0-0000 | 1932035 | GEARBOX OIL, Oil Sample | 2018-08-01 14:26 | Closed | GBXOIL | GBXOILSAMP | FORWARD | SCLARK |  | 2018-11-13 12:02
2 | WTG-0059A-NDGP-0000 | 1937952 | GEARBOX OIL, Replace oil cooler | 2018-08-16 15:08 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2019-03-08 14:47
4 | WTG-0086-NDG0-0000 | 1940066 | GEARBOX OIL, Add About 6 Gallons | 2018-08-21 15:38 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-01-02 09:38
4 | WTG-0053-0000 | 1954252 | Secondary filtration needs poppet fitting | 2018-09-28 14:15 | Closed | GBXOIL | GBXFILTINS | FORWARD | JLAWRENCE |  | 2019-01-30 14:04
1 | WTG-0117-N000-0000 | 1959150 | GEARBOX OIL, Secondary filter needs o-ring | 2018-10-08 16:09 | Cancelled | GBXOIL | GBXFILTINS | GREXP | GRAND RIDGE |  | 2023-06-29 13:12
1 | WTG-0071-0000 | 1959100 | rFSA Claim- Radiator Replacement | 2018-10-08 14:31 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2019-02-15 13:53
1 | WTG-0040-0000 | 1960696 | rFSA Claim: Pitch Tube Seals Leak | 2018-10-15 11:59 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-21 17:49
1 | WTG-0064-0000 | 1963032 | GEARBOX OIL, Fix oil leak | 2018-10-23 10:20 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CBORER
2 | WTG-0030-NDG0-0000 | 1983159 | GEARBOX OIL, Add/Top-Off 10 gals | 2018-11-13 07:56 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2018-11-16 14:31
1 | WTG-0044-0000 | 1984911 | GEARBOX OIL, Fix oil leak | 2018-11-21 08:09 | Closed | GBXOIL | GBXOILLEAK | BISHOP HILL | ASTAHL |  | 2019-04-04 10:13
2 | WTG-0008-NDGP-0000 | 1992557 | gearbox cooler to pump hose replacement | 2018-12-05 15:37 | Closed | GBXOIL |  | JUDITH GAP | JUDITHGAP |  | 2019-01-29 08:34
5 | WTG-0054-0000 | 2187248 | Oil cooler outlet hose replacement (gen side) | 2020-02-13 12:05 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2020-06-08 17:02
4 | GBX-JKD-W-0000709 | 2011889 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000710 | 2011890 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000721 | 2011891 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000722 | 2011892 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000723 | 2011893 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000751 | 2011896 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000761 | 2011897 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000767 | 2011898 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000768 | 2011899 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004019 | 2011818 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004039 | 2011829 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004041 | 2011830 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004042 | 2011831 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004043 | 2011832 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004044 | 2011833 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004047 | 2011834 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004052 | 2011835 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004053 | 2011836 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004054 | 2011837 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004058 | 2011838 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004059 | 2011839 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004061 | 2011840 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004062 | 2011841 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004063 | 2011842 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004065 | 2011843 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004067 | 2011844 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004070 | 2011845 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004071 | 2011846 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004072 | 2011847 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | WTG-0108-NDG0-0000 | 2019606 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
1 | WTG-0219-0000 | 1892544 | GEARBOX OIL, Fix oil leak | 2018-06-12 08:21 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE3 |  | 2018-11-06 17:19
5 | WTG-0007-NDGP-0000 | 1915188 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2018-06-25 17:50 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | WILLOWCREEK |  | 2019-07-30 15:51
2 | WTG-0036-0000 | 1921735 | GEARBOX OIL, Add/Top-Off | 2018-07-06 06:39 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2018-07-31 09:28
4 | WTG-0034-0000 | 1921736 | GEARBOX OIL, Add 5 Gal or less | 2018-07-06 06:40 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2018-11-13 12:00
2 | WTG-0072-NDG0-0000 | 1923823 | GEARBOX OIL, Particle counter troubleshooting | 2018-07-12 11:39 | Closed | GBXOIL | GBXPARTTS | MCADOO | NFALASZ |  | 2018-11-05 11:06
1 | WTG-0025-NDG0-0000 | 1925434 | GEARBOX OIL, Fix oil leak | 2018-07-17 07:53 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | REVERETT |  | 2018-08-02 00:44
1 | WTG-0119-NDG0-0000 | 1926456 | GEARBOX OIL, Fix oil leak | 2018-07-22 11:57 | Closed | GBXOIL | GBXOILLEAK | GREXP | MKNOX |  | 2020-01-29 10:31
1 | WTG-0007-0000 | 1926372 | Gearbox Radiator clean/Pressure Wash | 2018-07-20 17:36 | Closed | GBXOIL | GBXOILCOOL | RATTLESNAKE 1 | TMORRIS |  | 2018-07-23 14:39
1 | WTG-0102-NDGP-0000 | 1932022 | GEARBOX OIL, Particle counter troubleshooting | 2018-08-01 14:09 | Closed | GBXOIL | GBXPARTTS | CAMP SPRINGS II | MSNOW |  | 2018-10-30 08:32
1 | WTG-0110-0000 | 1933997 | GEARBOX OIL, Particle counter troubleshooting | 2018-08-06 16:50 | Closed | GBXOIL | GBXPARTTS | TURKEY TRACK | JBRILEY |  | 2018-11-13 09:31
4 | WTG-0086-NDGP-0000 | 1940067 | Replace breather hose on oil filter pot | 2018-08-21 15:43 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2019-01-02 09:39
1 | GBX-000019 | 1941608 | EM: Gearbox oil pessure too low | 2018-08-27 17:49 | Closed | GBXOIL | EM52 | BISHOP HILL | KCOOPER |  | 2018-10-10 08:56
1 | GBX-000108 | 1949586 | Gbx overtemp | 2018-09-13 17:42 | Closed | GBXOIL | EM77 | PRAIRIE BREEZE | JFERRIS |  | 2018-09-24 16:13
1 | WTG-0014-0000 | 1956751 | TIL201407221r0 - Nanjing/Pall Oil Cooler Retrofit | 2018-10-02 16:17 | Closed | GBXOIL | GBXOILCOOL | BUCKEYE | NSCHMEIDLER | 1 | 2018-10-05 08:59
1 | WTG-0042-0000 | 1960699 | Mechanical Oil Pump Leak | 2018-10-15 12:23 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2020-05-01 16:25
1 | WTG-0009-0000 | 1960953 | GEARBOX OIL, Fix oil leak | 2018-10-16 14:39 | Closed | GBXOIL | GBXOILLEAK | BETHEL | BETHEL |  | 2018-10-18 15:42
1 | WTG-0201-NDG0-0000 | 1963520 | GEARBOX OIL, Fix oil leak | 2018-10-24 14:35 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | JFERRIS |  | 2018-12-07 14:55
1 | WTG-0012-0000 | 1982454 | Fix oil leak, Valve Replacement | 2018-11-08 16:27 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MMCCABE |  | 2019-01-15 17:11
4 | WTG-0040A-0000 | 1983296 | GEARBOX OIL, Add/Top-Off 5 gal | 2018-11-13 12:58 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2018-11-14 09:48
4 | WTG-0040A-0000 | 1983297 | Secondary filter pump leak | 2018-11-13 13:30 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2022-05-10 09:24
1 | WTG-0081-0000 | 1984114 | clean tower | 2018-11-16 15:59 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON
1 | WTG-0099-0000 | 1988403 | Replace GB pump motor | 2018-11-27 08:35 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | KMCLELAND |  | 2018-11-30 12:27
1 | WTG-0022-NDD0-0000 | 1995166 | GEARBOX OIL, Particle counter installation | 2018-12-12 17:23 | Closed | GBXOIL | GBXPARTINS | GREXP | RPPATEL |  | 2019-02-04 15:00
1 | WTG-0007-NDG0-0000 | 1995168 | GEARBOX OIL, Particle counter installation | 2018-12-12 17:41 | Closed | GBXOIL | GBXPARTINS | GUNSIGHT | RPPATEL |  | 2019-01-17 19:01
1 | WTG-0035-NDG0-0000 | 1995172 | GEARBOX OIL, Particle counter installation | 2018-12-12 17:44 | Closed | GBXOIL | GBXPARTINS | GUNSIGHT | RPPATEL |  | 2019-01-18 15:08
4 | GBX-JKD-W-0000747 | 2011894 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-JKD-W-0000748 | 2011895 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004020 | 2011819 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004023 | 2011820 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004027 | 2011821 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004028 | 2011822 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004029 | 2011823 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004030 | 2011824 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004031 | 2011825 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004033 | 2011826 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004036 | 2011827 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004038 | 2011828 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | WTG-0105-NDG0-0000 | 2019603 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0106-NDG0-0000 | 2019604 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0107-NDG0-0000 | 2019605 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0109-NDG0-0000 | 2019607 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0110-NDG0-0000 | 2019608 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0111-NDG0-0000 | 2019609 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0112-NDG0-0000 | 2019610 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0113-NDG0-0000 | 2019611 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0114-NDG0-0000 | 2019612 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0115-NDG0-0000 | 2019613 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0119-NDG0-0000 | 2019617 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0116-NDG0-0000 | 2019614 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0117-NDG0-0000 | 2019615 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0118-NDG0-0000 | 2019616 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0120-NDG0-0000 | 2019618 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
1 | WTG-0011-0000 | 2019858 | PALL Filter Housing Leak | 2019-01-10 15:58 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2020-01-23 14:29
5 | WTG-0065-NDG0-0000 | 2022802 | GEARBOX Cover stud needs replacemnet/repair | 2019-01-16 16:17 | Closed | GBXOIL | GBXOILLEAK | FORWARD | MPEARSON |  | 2019-05-29 11:47
4.2 | WTG-0061-NDGP-0000 | 2024803 | GEARBOX OIL, Replace oil cooler | 2019-01-22 13:19 | Ready to Schedule | GBXOIL | GBXOILCOOL | FORWARD | MPEARSON
5 | WTG-0053-NDGP-0000 | 2172608 | Replaced lube pump spider | 2020-01-10 10:07 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2020-01-17 10:42
1 | WTG-0057-0000 | 2024849 | PALL Filter Housing Leak | 2019-01-23 09:49 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2019-04-18 13:40
4 | WTG-0089-NDG0-0000 | 2025154 | Add 10 gallons oil | 2019-01-23 16:12 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2019-01-24 10:17
4 | WTG-0055A-0000 | 2025158 | GEARBOX OIL, Add/Top-Off | 2019-01-23 15:21 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-01-30 14:12
2 | WTG-0038-0000 | 2026814 | GEARBOX OIL, Add/Top-Off | 2019-01-28 12:10 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2019-03-12 08:44
4 | GBX-000050 | 2027466 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
1 | WTG-0015-0000 | 2023206 | GEARBOX OIL, Replace leaking Hose | 2019-01-18 16:08 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | CPRUIT
5 | WTG-0061-NDGP-0000 | 2024841 | GEARBOX OIL, Add | 2019-01-23 08:59 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2019-02-27 16:20
4 | GBX-000031 | 2027447 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000043 | 2027459 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000044 | 2027461 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000045 | 2027462 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000046 | 2027463 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000047 | 2027464 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000048 | 2027465 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000012 | 2027427 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000009 | 2027424 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000010 | 2027425 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000011 | 2027426 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000013 | 2027428 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000017 | 2027433 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000014 | 2027429 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000015 | 2027430 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000016 | 2027431 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000018 | 2027434 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000019 | 2027435 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000020 | 2027436 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | SYS-WTG-WIEC | 2027410 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL | GBXOILSAMP | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000008 | 2027423 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
2 | WTG-0023A-NDGP-0000 | 2038997 | Oil pump leak | 2019-02-20 17:03 | Closed | GBXOIL | GBXOILLEAK | FORWARD | MPEARSON |  | 2019-03-12 12:28
1 | WTG-0026-0000 | 2050389 | GEARBOX OIL, Secondary filter system (oil cutout contactor fix) | 2019-03-06 15:12 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | BUCKEYE |  | 2019-08-21 10:39
1 | WTG-0J02-NDG0-0000 | 2052113 | GEARBOX OIL, Particle counter installation | 2019-03-13 14:03 | Closed | GBXOIL | GBXPARTINS | BEECH RIDGE | RPPATEL |  | 2023-01-10 08:59
5 | WTG-0013-NDGP-0000 | 2055583 | GEARBOX OIL, Install new (yellow) particulate trap on next filter change | 2019-03-26 17:41 | Cancelled | GBXOIL | GBXOILCOOL | GRAND RIDGE | GRAND RIDGE |  | 2023-06-29 13:13
2 | WTG-0040-NDGP-0000 | 2063746 | GEARBOX OIL, Fix oil leak | 2019-04-08 13:07 | Closed | GBXOIL | GBXOILLEAK | VANTAGE | SENGLAND |  | 2020-09-22 17:20
5 | GBX-000021 | 2063806 | GEARBOX OIL, Fix oil leak | 2019-04-08 16:48 | Cancelled | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE
2 | WTG-0004-NDGP-0000 | 2064400 | GEARBOX OIL, Replace oil pump coupler | 2019-04-10 17:43 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2019-04-15 15:23
3 | WTG-0097-NDG0-0000 | 2066507 | GEARBOX OIL, Add/Top-Off | 2019-04-19 17:06 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2019-05-08 08:08
1 | WTG-0085-NDG0-0000 | 2068815 | GEARBOX OIL, Particle counter removal | 2019-04-25 17:17 | Closed | GBXOIL | GBXPARTREM | GREXP | RPPATEL |  | 2019-07-09 14:54
1 | WTG-0021-0000 | 2070164 | 2019 Padmount Oil Sample | 2019-04-29 15:34 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-05-07 15:12
4 | WTG-0038-NDGP-0000 | 2071458 | replace hose from oil filter to oil cooler | 2019-05-01 08:05 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2019-08-16 14:56
1 | WTG-0103-NDG0-0000 | 2074499 | oil pump inversion | 2019-05-06 15:06 | Cancelled | GBXOIL | GBXOILLEAK | GREXP | GRAND RIDGE |  | 2023-06-29 13:16
1 | WTG-0H10-NDG0-0000 | 2075745 | GEARBOX OIL, Fix oil leak | 2019-05-09 12:10 | Closed | GBXOIL | GBXOILLEAK | BEECH RIDGE | BEECHRIDGE |  | 2020-08-12 10:36
1 | WTG-0060-0000 | 2077867 | Oil leak from radiator plug and oil filter housing. | 2019-05-20 14:12 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2019-10-17 16:18
1 | WTG-0004-NDG0-0000 | 2080831 | Joint sealant leak ,GEARBOX OIL, Fix oil leak | 2019-05-30 13:52 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | JGILLILAN |  | 2021-08-30 15:13
1 | WTG-0029-0000 | 2153594 | Drain oil catch basin | 2019-11-20 16:58 | Closed | GBXOIL | BLANK | JUDITH GAP | JUDITHGAP |  | 2020-08-24 08:28
1 | WTG-039E-0000 | 2096277 | PALL Filter Housing Leak | 2019-06-26 09:44 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2019-11-21 14:56
1 | WTG-0031-NDG0-0000 | 2102217 | GEARBOX OIL, Particle counter installation | 2019-07-09 10:47 | Cancelled | GBXOIL | GBXPARTINS | FORWARD | SCLARK |  | 2020-02-06 15:59
3 | WTG-0157-NDGP-0000 | 2104368 | GEARBOX OIL, Replace oil pump | 2019-07-18 20:21 | Closed | GBXOIL | GBXOILCOOL | CAMP SPRINGS II | CAMP SPRINGS |  | 2022-12-20 10:45
2 | WTG-0141-NDGP-0000 | 2104369 | GEARBOX OIL, Replace oil cooler | 2019-07-18 20:25 | Closed | GBXOIL | GBXOILCOOL | CAMP SPRINGS II | CAMP SPRINGS |  | 2021-04-12 09:19
2 | WTG-0157-NDBS-0000 | 2104365 | Replace and pump on hydralic staion | 2019-07-18 20:04 | Closed | GBXOIL | GBXOILLEAK | CAMP SPRINGS II | CAMP SPRINGS |  | 2020-06-02 09:43
2 | WTG-0035-NDGP-0000 | 2106996 | o ring fail | 2019-07-26 13:45 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2019-07-30 09:54
1 | WTG-0027-0000 | 2107641 | 2019 Padmount Oil Sample | 2019-07-29 09:45 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2020-08-03 16:06
1 | WTG-0029-0000 | 2107643 | 2019 Padmount Oil Sample | 2019-07-29 09:45 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-21 17:45
8 | WTG-0004-NDG0-0000 | 2117184 | Add oil additive to main gearbox | 2019-08-24 06:00 | Closed | GBXOIL | GBXOILCHG | MARSH HILL | CSLY |  | 2019-08-29 20:18
8 | WTG-0009-NDG0-0000 | 2117312 | Add oil additive to main gearbox | 2019-08-26 08:20 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-08-27 08:11
8 | WTG-0035-NDG0-0000 | 2117313 | Add oil additive to main gearbox | 2019-08-26 08:21 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-08-27 08:26
8 | WTG-0008-NDG0-0000 | 2117315 | Add oil additive to main gearbox | 2019-08-26 08:21 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-08-27 08:08
8 | WTG-0039-NDG0-0000 | 2117316 | Add oil additive to main gearbox | 2019-08-26 08:22 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-08-27 08:27
8 | WTG-0043-NDG0-0000 | 2117323 | Add oil additive to main gearbox | 2019-08-26 08:44 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-08-27 08:39
8 | WTG-0044-NDG0-0000 | 2117327 | Add oil additive to main gearbox | 2019-08-26 08:45 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-08-27 08:42
8 | WTG-0030-NDG0-0000 | 2117330 | Add oil additive to main gearbox | 2019-08-26 08:46 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-09-30 14:48
2 | WTG-0013-NDG0-0000 | 2118565 | gearbox running too hot | 2019-08-27 18:02 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-08-29 08:15
2 | WTG-0029-NDG0-0000 | 2118571 | gearbox running too hot | 2019-08-27 18:33 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-08-29 17:53
1 | WTG-0308-NDG0-0000 | 2126377 | GEARBOX OIL, Fix oil leak | 2019-09-13 13:36 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | JFERRIS |  | 2020-02-07 16:16
1 | WTG-0109-NDGP-0000 | 2126485 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2019-09-14 09:03 | Closed | GBXOIL | GBXOILCOOL | CAMP SPRINGS II | CAMP SPRINGS |  | 2019-09-17 08:57
4 | GBX-000021 | 2027437 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
1 | WTG-0101-0000 | 2054110 | GEARBOX OIL, Secondary filter system installation | 2019-03-25 07:50 | Closed | GBXOIL | GBXFILTINS | CAMP SPRINGS II | JSANCHEZ |  | 2020-03-11 09:18
3 | WTG-0011-NDG0-0000 | 2059869 | Gearbox running too hot | 2019-04-02 08:22 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-08-06 08:12
3 | WTG-0042-NDG0-0000 | 2059871 | Gearbox running too hot | 2019-04-02 08:23 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-04-16 12:04
1 | WTG-0052-NDG0-0000 | 2065299 | GEARBOX OIL, Replace oil filter housing | 2019-04-15 12:59 | Closed | GBXOIL | GBXOILCOOL | UPSTREAM | JGILLILAN |  | 2021-09-06 22:26
1 | WTG-0213-NDG0-0000 | 2068807 | GEARBOX OIL, Particle counter troubleshooting | 2019-04-25 16:48 | Cancelled | GBXOIL | GBXPARTTS | FORWARD | RPPATEL |  | 2019-11-05 15:39
1 | WTG-0024-0000 | 2070167 | 2019 Padmount Oil Sample | 2019-04-29 15:35 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-05-07 15:11
1 | WTG-0022-0000 | 2070165 | 2019 Padmount Oil Sample | 2019-04-29 15:34 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-05-07 15:12
1 | WTG-0023-0000 | 2070166 | 2019 Padmount Oil Sample | 2019-04-29 15:34 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-05-07 15:11
1 | WTG-0025-0000 | 2070168 | 2019 Padmount Oil Sample | 2019-04-29 15:35 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-05-07 15:11
2 | WTG-0046-0000 | 2079147 | GEARBOX OIL, REPLACE GBX HOSES | 2019-05-24 08:58 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2019-09-20 14:45
4.2 | GBX-000004 | 2103821 | GEARBOX OIL, Add/Top-Off | 2019-07-16 12:06 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | WOLVERINECREEK |  | 2019-10-22 17:00
4 | WTG-0074A-NDG0-0000 | 2106396 | 5 gallon oil add | 2019-07-25 11:02 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2019-07-26 11:29
4 | WTG-0057-NDGP-0000 | 2110674 | Secure oil cooler vent tube | 2019-08-02 17:25 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2019-08-16 15:14
2 | WTG-0032-NDGP-0000 | 2116406 | GEARBOX OIL, Replace oil pump | 2019-08-22 09:09 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2019-08-26 09:26
8 | WTG-0059-NDG0-0000 | 2117322 | Add oil additive to main gearbox | 2019-08-26 08:44 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-08-27 08:46
8 | WTG-0033-NDG0-0000 | 2117324 | Add oil additive to main gearbox | 2019-08-26 08:44 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-09-30 14:48
8 | WTG-0022-NDG0-0000 | 2117326 | Add oil additive to main gearbox | 2019-08-26 08:45 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-09-30 14:48
8 | WTG-0042-NDG0-0000 | 2117328 | Add oil additive to main gearbox | 2019-08-26 08:45 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-09-30 14:48
8 | WTG-0005-NDG0-0000 | 2117185 | Add oil additive to main gearbox | 2019-08-24 06:00 | Closed | GBXOIL | GBXOILCHG | MARSH HILL | CSLY |  | 2019-08-29 20:19
8 | WTG-0027-NDG0-0000 | 2117310 | Add oil additive to main gearbox | 2019-08-26 08:18 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-08-27 08:24
8 | WTG-0023-NDG0-0000 | 2117348 | Add oil additive to main gearbox | 2019-08-26 08:55 | Cancelled | GBXOIL | GBXOILCHG | ORANGEVILLE | BEUSCHER |  | 2019-10-01 12:51
8 | WTG-0020-NDG0-0000 | 2117247 | Add oil additive to main gearbox | 2019-08-25 06:00 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | CSLY |  | 2019-08-27 08:22
5 | WTG-0203B-NDG0-0000 | 2136404 | GEARBOX OIL, Add/Top-Off 5gals | 2019-10-09 16:37 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2020-01-10 10:13
1 | WTG-0051-0000 | 2139710 | rFSA Claim: Leaking pitch tube seals | 2019-10-22 15:44 | Cancelled | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-22 10:46
1 | WTG-0012-0000 | 2139686 | GEARBOX OIL, Fix oil leak | 2019-10-18 12:57 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | ECOPELAND |  | 2019-10-23 12:00
5 | WTG-0117-NDGP-0000 | 2146740 | Oil cooler plug leaks | 2019-11-04 15:56 | Closed | GBXOIL | GBXOILLEAK | SCEXP | CMUSTAIN |  | 2021-11-30 14:57
5 | WTG-0G10-NDG0-0000 | 2147257 | GEARBOX OIL, Particle counter troubleshooting | 2019-11-05 15:33 | Closed | GBXOIL | GBXPARTREM | BEECH RIDGE | MSNOW |  | 2020-06-23 09:39
5 | WTG-0213-NDG0-0000 | 2147258 | GEARBOX OIL, Particle counter removal | 2019-11-05 15:36 | Ready to Schedule | GBXOIL | GBXPARTREM | FORWARD | MSNOW
2 | WTG-0082-NDG0-0000 | 2147260 | GEARBOX OIL, Particle counter installation | 2019-11-05 15:40 | Cancelled | GBXOIL | GBXPARTINS | FORWARD | MSNOW |  | 2019-11-08 16:06
1 | WTG-0128-0000 | 2152575 | ELECINST Environmental Work Order - PM | 2019-11-13 10:41 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | BBRASWELL |  | 2019-11-19 14:37
1 | WTG-0337-0000 | 2152370 | GEARBOX OIL, Fix oil leak | 2019-11-13 10:21 | Closed | GBXOIL | GBXOILLEAK | BISHOP HILL III | BISHOP HILL |  | 2019-12-04 13:43
1 | WTG-0204-0000 | 2153372 | GEARBOX OIL, Fix oil leak, filter to pump gasket | 2019-11-19 15:43 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | AHOFFMANN |  | 2020-06-11 16:32
1 | WTG-0066-0000 | 2160497 | GEARBOX OIL, Fix oil leak | 2019-12-06 09:28 | Closed | GBXOIL | GBXOILLEAK | BETHEL | AGALARZA |  | 2019-12-20 10:31
1 | WTG-0084-NDGP-0000 | 2163174 | Small oil leak in oil cooler | 2019-12-16 18:27 | Closed | GBXOIL | GBXOILCOOL | GREXP | GRAND RIDGE |  | 2020-04-22 16:07
1 | WTG-0010-0000 | 2164280 | WTG010 - Low Gear Oil Level | 2019-12-21 06:19 | Closed | GBXOIL | GBXOILLEAK | BUFFALO MOUNT | SBAY |  | 2020-05-21 11:54
1 | WTG-0319-0000 | 2164524 | GEARBOX OIL, Fix oil leak | 2019-12-23 11:20 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | JSTAHLECKER |  | 2020-11-13 15:21
1 | WTG-0206-NDGP-0000 | 2165881 | GEARBOX OIL, Fix oil leak | 2019-12-27 14:40 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | CHADDIX |  | 2020-03-11 12:19
4 | SYS-WTG-BETH | 2171886 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL | GBXOILSAMP | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
2 | WTG-0028-NDG0-0000 | 2172603 | GEARBOX OIL, Add/Top-Off/replace cooler hose | 2020-01-10 15:56 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | GOLDTHWAITE |  | 2020-01-23 14:35
1 | WTG-0019-NDG0-0000 | 2172628 | GEARBOX OIL, Particle counter installation | 2020-01-10 17:16 | Closed | GBXOIL | GBXPARTINS | WILLOW CREEK | WILLOWCREEK |  | 2020-01-24 13:08
5 | WTG-0219-0000 | 2177490 | GEARBOX OIL, Replace oil filter housing | 2020-01-27 17:17 | Closed | GBXOIL | GBXOILCOOL | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2022-11-15 16:38
1 | WTG-0085-0000 | 2188617 | PALL Filter Housing Leak | 2020-02-17 16:12 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2021-10-14 16:44
1 | WTG-0009-0000 | 2191492 | Gearbox Oil leak inspection | 2020-02-26 11:46 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | TURKEY TRACK |  | 2020-03-01 09:53
4 | WTG-0117-NDG0-0000 | 2192624 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
1 | WTG-0180-0000 | 2132433 | Install secondary filtration system on gearbox oil | 2019-10-01 08:59 | Closed | GBXOIL | GBXFILTINS | CAMP SPRINGS II | CMORRIS | 1 | 2019-10-21 09:28
1 | WTG-0237-0000 | 2137561 | Radiator GEARBOX OIL, Fix oil leak/Radiator | 2019-10-16 12:50 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NHEITHOFF |  | 2021-08-30 15:12
4.2 | WTG-0301-NDGP-0000 | 2137812 | GEARBOX OIL, Oil Sample | 2019-10-17 12:10 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL III | TCASTEEL |  | 2019-11-06 12:29
4.2 | WTG-0302-NDGP-0000 | 2137813 | GEARBOX OIL, Oil Sample | 2019-10-17 12:14 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL III | TCASTEEL |  | 2019-11-06 12:29
2 | WTG-0112-0000 | 2148131 | GEARBOX OIL, Oil Sample | 2019-11-08 10:15 | Closed | GBXOIL | GBXOILSAMP | SANTA RITA EAST | JGASTON |  | 2019-12-02 11:03
1 | WTG-0312-0000 | 2161571 | GEARBOX OIL, Fix oil leak | 2019-12-09 17:49 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | DTILLIS |  | 2020-11-13 15:21
1 | WTG-0230-0000 | 2163789 | GEARBOX OIL, Fix oil leak | 2019-12-19 15:56 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NSCHINDLER |  | 2020-02-07 16:06
2 | WTG-0013-NDG0-0000 | 2165036 | Add 10 gallons Amsoil | 2019-12-27 12:22 | Closed | GBXOIL | GBXOILADD | VANTAGE | VANTAGE |  | 2020-03-02 10:48
1 | WTG-0224-NDGP-0000 | 2170198 | Rexroth cool inlet hose GEARBOX OIL, Fix oil leak | 2020-01-04 12:44 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | JGILLILAN |  | 2020-11-12 15:34
1 | WTG-0057-0000 | 2175285 | GEARBOX OIL, Fix oil leak | 2020-01-22 14:03 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH |  | 2020-01-23 14:32
1 | WTG-0048-0000 | 2178832 | GEARBOX OIL, Particle counter troubleshooting | 2020-01-29 09:51 | Closed | GBXOIL | GBXPARTTS | GUNSIGHT | DKEETON |  | 2020-01-29 16:27
1 | WTG-0043-0000 | 2178833 | GEARBOX OIL, Particle counter troubleshooting | 2020-01-29 09:51 | Closed | GBXOIL | GBXPARTTS | GUNSIGHT | DKEETON |  | 2020-01-29 16:16
2 | WTG-0005-NDG0-0000 | 2186675 | Troubleshhooting Oil Leak Uptower | 2020-02-10 07:36 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JROGERS |  | 2020-02-25 07:21
4 | WTG-0072A-NDGP-0000 | 2186678 | GEARBOX OIL, Fix oil leak of CC Jensen | 2020-02-11 10:24 | Closed | GBXOIL | GBXOILLEAK | FORWARD | MPEARSON |  | 2020-08-07 10:16
4.2 | WTG-0066-0000 | 2188623 | Replace gbx hose | 2020-02-17 14:54 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2020-04-01 14:24
4 | WTG-0105-NDG0-0000 | 2192612 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0106-NDG0-0000 | 2192613 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0107-NDG0-0000 | 2192614 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0108-NDG0-0000 | 2192615 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0109-NDG0-0000 | 2192616 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0110-NDG0-0000 | 2192617 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0111-NDG0-0000 | 2192618 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0112-NDG0-0000 | 2192619 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0113-NDG0-0000 | 2192620 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0114-NDG0-0000 | 2192621 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0115-NDG0-0000 | 2192622 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0116-NDG0-0000 | 2192623 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0118-NDG0-0000 | 2192625 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0119-NDG0-0000 | 2192626 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0120-NDG0-0000 | 2192627 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0049-NDG0-0000 | 2192556 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0050-NDG0-0000 | 2192557 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0051-NDG0-0000 | 2192558 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0052-NDG0-0000 | 2192559 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0056-NDG0-0000 | 2192563 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0053-NDG0-0000 | 2192560 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0054-NDG0-0000 | 2192561 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0055-NDG0-0000 | 2192562 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0057-NDG0-0000 | 2192564 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0058-NDG0-0000 | 2192565 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0059-NDG0-0000 | 2192566 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0060-NDG0-0000 | 2192567 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0061-NDG0-0000 | 2192568 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0062-NDG0-0000 | 2192569 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0066-NDG0-0000 | 2192573 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0063-NDG0-0000 | 2192570 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0064-NDG0-0000 | 2192571 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0065-NDG0-0000 | 2192572 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0067-NDG0-0000 | 2192574 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0068-NDG0-0000 | 2192575 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0069-NDG0-0000 | 2192576 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0070-NDG0-0000 | 2192577 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0071-NDG0-0000 | 2192578 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0072-NDG0-0000 | 2192579 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0076-NDG0-0000 | 2192583 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0073-NDG0-0000 | 2192580 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0074-NDG0-0000 | 2192581 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0075-NDG0-0000 | 2192582 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0077-NDG0-0000 | 2192584 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0078-NDG0-0000 | 2192585 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0061-0000 | 2194727 | GEARBOX OIL, Add 5 Gallons | 2020-03-02 14:06 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-09-30 12:12
5 | WTG-0047-0000 | 2194726 | GEARBOX OIL, Add about 2 Gallons | 2020-03-02 14:01 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-09-30 12:12
4.2 | WTG-0074-0000 | 2198392 | Oil Cooler Leak | 2020-03-12 14:59 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2020-07-16 07:57
4 | WTG-0031-NDGP-0000 | 2199351 | GEARBOX OIL, Oil cooler shroud needs self tapping screws | 2020-03-18 11:50 | Closed | GBXOIL | GBXOILCOOL | FORWARD | MPEARSON |  | 2020-06-26 13:49
4 | WTG-0050-NDGD-0000 | 2221937 | GEARBOX OIL, Add/Top-Off | 2020-05-11 13:37 | Closed | GBXOIL | GBXOILADD | FORWARD | MPEARSON |  | 2020-09-30 12:18
4 | WTG-0018-0000 | 2227492 | GEARBOX OIL, Replace oil cooler pump | 2020-05-27 13:30 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2020-05-28 08:08
1 | WTG-0052-0000 | 2231508 | GEARBOX OIL, Replaced return hose ,(brake side hose ) | 2020-06-01 15:50 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | ZMILLER |  | 2020-10-20 15:53
1 | WTG-0306-0000 | 2247037 | GEARBOX OIL, Fix oil leak | 2020-07-15 16:26 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | AHOFFMANN |  | 2021-08-30 15:03
1 | GBX-000211 | 2233317 | GEARBOX OIL, Oil Sample | 2020-06-04 10:45 | Closed | GBXOIL | GBXOILSAMP | SCEXP | CMUSTAIN |  | 2020-11-03 10:54
4 | WTG-0060A-NDGP-0000 | 2237481 | Drill coupler inspection hole in gear oil pump flange | 2020-06-23 10:55 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2020-09-02 13:05
4 | WTG-0065-NDG0-0000 | 2237353 | Oil cooler inlet to gbx oil filter outlet hose replacement | 2020-06-22 14:21 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2020-06-26 14:29
4 | WTG-0090-0000 | 2197925 | GEARBOX OIL, Add 5 gallons | 2020-03-10 15:53 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-04-01 15:16
1 | WTG-0078-NDGP-0000 | 2199475 | GEARBOX OIL, Fix oil leak | 2020-03-19 13:12 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JUDITHGAP |  | 2020-03-20 11:47
1 | WTG-0079-NDGP-0000 | 2199476 | GEARBOX OIL, Fix oil leak | 2020-03-19 13:14 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JUDITHGAP |  | 2020-03-20 11:47
1 | WTG-0075-0000 | 2199925 | GEARBOX OIL, Fix oil leak | 2020-03-20 16:45 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | CDEVOLL |  | 2020-03-30 10:41
1 | WTG-0020-0000 | 2208053 | GEARBOX OIL, Fix oil leak | 2020-04-13 10:28 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | RKUDERA |  | 2021-12-21 16:13
4 | WTG-0087-0000 | 2221928 | Bring plug for lube pump inspection retro | 2020-05-11 12:36 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2020-10-12 11:18
2 | WTG-0048-NDG0-0000 | 2224838 | Replace oil cooler outlet hose to gearbox inlet (yellow hose) | 2020-05-18 11:55 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2020-10-29 10:21
2 | WTG-0025-0000 | 2238883 | GEARBOX OIL, Fix oil leak - Pitch Tube Seal WC # 3806716 | 2020-06-26 17:59 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | NHEITHOFF |  | 2022-08-31 17:02
4 | WTG-0036-0000 | 2240186 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2020-06-29 13:27 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2020-08-20 06:36
2 | WTG-0082-NDGP-0000 | 2244438 | Replace oil pump coupler | 2020-07-07 12:19 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2020-12-07 18:02
1 | WTG-0017-0000 | 2244634 | Gearbox Leak and clean up | 2020-07-07 15:33 | Closed | GBXOIL | GBXOILLEAK | GUNSIGHT | DKEETON |  | 2020-07-09 16:28
2 | WTG-0060-NDG0-0000 | 2246663 | Add 10 gallons Amsoil | 2020-07-14 13:04 | Closed | GBXOIL | GBXOILADD | VANTAGE | VANTAGE |  | 2020-09-01 09:46
1 | WTG-0080-0000 | 2248025 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:41 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-07-30 14:06
1 | WTG-0097-0000 | 2248029 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:46 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-12-09 17:31
1 | WTG-0056-0000 | 2248008 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:35 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-11-10 13:53
1 | WTG-0057-0000 | 2248009 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:36 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-15 07:49
1 | WTG-0072-0000 | 2248019 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:39 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-11-04 08:55
1 | WTG-0073-0000 | 2248020 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:40 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-11-10 13:53
1 | WTG-0090-0000 | 2248026 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:42 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-01-26 15:03
1 | WTG-0022-0000 | 2247982 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:26 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-09-23 11:08
1 | WTG-0005-0000 | 2247969 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:17 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-07-31 15:38
1 | WTG-0017-0000 | 2247978 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:25 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-08-14 15:26
1 | WTG-0018-0000 | 2247979 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:26 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-09-02 09:44
1 | WTG-0020-0000 | 2247980 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:26 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-09-14 16:24
1 | WTG-0021-0000 | 2247981 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:26 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-09-04 10:33
1 | WTG-0023-0000 | 2247983 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:27 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-09-17 13:57
1 | WTG-0025-0000 | 2247984 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:27 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-01-28 15:28
1 | WTG-0026-0000 | 2247985 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:27 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-03-17 09:01
1 | WTG-0028-0000 | 2247986 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:28 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-09-24 16:08
1 | WTG-0047-0000 | 2248000 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:33 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-07 14:24
1 | WTG-0052-0000 | 2248004 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:34 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-11-09 08:50
1 | WTG-0049-0000 | 2248001 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:33 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-03-01 10:54
1 | WTG-0050-0000 | 2248002 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:33 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-30 15:17
1 | WTG-0051-0000 | 2248003 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:34 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-08 14:47
1 | WTG-0053-0000 | 2248005 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:34 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-21 14:44
1 | WTG-0054-0000 | 2248006 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:35 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-13 15:54
1 | WTG-0071-0000 | 2248018 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:38 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-11-10 13:53
1 | WTG-0067-0000 | 2248015 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:37 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-11-04 08:55
1 | WTG-0069-0000 | 2248016 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:38 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-30 15:18
1 | WTG-0070-0000 | 2248017 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:38 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-11-10 13:53
1 | WTG-0111-0000 | 2248038 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:50 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-12-21 15:56
1 | WTG-0077-0000 | 2248024 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:41 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-11-19 14:19
1 | WTG-0098-0000 | 2248030 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:47 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-04-13 17:50
1 | WTG-0107-0000 | 2248037 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:49 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-12-14 15:31
1 | WTG-0112-0000 | 2248039 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:50 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-12-21 13:31
1 | WTG-0113-0000 | 2248040 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:50 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-12-22 13:36
1 | WTG-0115-0000 | 2248042 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:51 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-12-23 14:09
1 | WTG-0117-0000 | 2248043 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:51 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-12-23 14:09
1 | WTG-0120-0000 | 2248044 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:51 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-12-29 14:21
1 | WTG-0059-0000 | 2248010 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:36 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-11-09 08:50
1 | WTG-0060-0000 | 2248011 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:36 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-19 08:07
1 | WTG-0061-0000 | 2248012 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:37 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-21 14:44
1 | WTG-0075-0000 | 2248022 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:40 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-11-09 08:49
1 | WTG-0055-0000 | 2248007 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:35 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-08-12 15:33
1 | WTG-0062-0000 | 2248013 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:37 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-08 14:47
1 | WTG-0074-0000 | 2248021 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:40 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-04-28 12:45
1 | WTG-0076-0000 | 2248023 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:41 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-11-24 12:33
4 | WTG-0057-0000 | 2255250 | GEARBOX OIL, Add about 3 gallons | 2020-08-04 18:25 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-08-07 10:43
3 | WTG-0001-NDG0-0000 | 2256958 | gearbox coupler inspection port | 2020-08-07 16:58 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2020-08-17 17:06
3 | WTG-0029-NDG0-0000 | 2256961 | gearbox coupler inspection port | 2020-08-07 17:02 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2020-08-24 08:28
4 | WTG-0211A-0000 | 2258546 | Secondary filter pump leak | 2020-08-13 16:21 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2021-07-28 07:38
4 | WTG-0204A-0000 | 2259952 | GEARBOX OIL, Add/Top-Off | 2020-08-19 16:27 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-08-25 12:04
1 | WTG-0126-NDG0-0000 | 2274386 | oil pump inversion | 2020-08-26 12:34 | Closed | GBXOIL | GBXOILLEAK | GREXP | GRAND RIDGE |  | 2022-03-22 11:16
1 | WTG-0128-0000 | 2275121 | GEARBOX OIL, Secondary filter system installation | 2020-08-28 11:10 | Cancelled | GBXOIL | GBXFILTINS | GREXP | GRAND RIDGE |  | 2023-06-29 13:16
5 | WTG-0083-NDG0-0000 | 2282381 | GEARBOX OIL, Add/Top-Off 5 gals | 2020-09-03 14:26 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2020-09-16 08:17
2 | WTG-0060A-NDG0-0000 | 2285062 | Drain 10 gallons/Add 10 gallons per sample results | 2020-09-15 11:54 | Closed | GBXOIL | GBXOILADD | FORWARD | JWERNER |  | 2022-01-24 09:01
5 | WTG-0204-0000 | 2286866 | Install secondary filtration system on gearbox oil | 2020-09-25 16:53 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | LHINKLE |  | 2024-07-16 15:12
5 | WTG-0205-0000 | 2286867 | Install secondary filtration system on gearbox oil | 2020-09-25 16:53 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | LHINKLE |  | 2024-07-16 15:12
5 | WTG-0216-0000 | 2286904 | Install secondary filtration system on gearbox oil | 2020-09-26 07:58 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-06-25 13:49
5 | WTG-0218-0000 | 2286905 | Install secondary filtration system on gearbox oil | 2020-09-26 07:58 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-12-04 11:18
5 | WTG-0219-0000 | 2286906 | Install secondary filtration system on gearbox oil | 2020-09-26 07:59 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-08-15 12:29
4 | WTG-0050-0000 | 2286843 | GEARBOX OIL, Fix oil leak | 2020-09-25 14:38 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2021-04-23 07:53
5 | WTG-0220-0000 | 2286907 | Install secondary filtration system on gearbox oil | 2020-09-26 07:59 | Ready to Schedule | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2
5 | WTG-0222-0000 | 2286908 | Install secondary filtration system on gearbox oil | 2020-09-26 08:00 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-05-10 13:13
4 | WTG-0236-0000 | 2286924 | Install secondary filtration system on gearbox oil | 2020-09-26 08:06 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-08-15 12:29
4 | WTG-0237-0000 | 2286925 | Install secondary filtration system on gearbox oil | 2020-09-26 08:06 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-08-15 12:29
4 | WTG-0238-0000 | 2286926 | Install secondary filtration system on gearbox oil | 2020-09-26 08:07 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-07-09 13:03
5 | WTG-0232-0000 | 2286920 | Install secondary filtration system on gearbox oil | 2020-09-26 08:05 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2025-05-13 07:46
4 | WTG-0239-0000 | 2286927 | Install secondary filtration system on gearbox oil | 2020-09-26 08:07 | Ready to Schedule | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2
5 | WTG-0211-0000 | 2286899 | Install secondary filtration/needs fitting/needs breather cap | 2020-09-26 07:57 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-02-28 15:26
5 | WTG-0212-0000 | 2286900 | Install secondary filtration system on gearbox oil | 2020-09-26 07:57 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-08-15 12:29
5 | WTG-0213-0000 | 2286901 | Install secondary filtration system on gearbox oil | 2020-09-26 07:57 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-07-16 15:12
5 | WTG-0214-0000 | 2286902 | Install secondary filtration system on gearbox oil | 2020-09-26 07:58 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-08-15 12:29
5 | WTG-0215-0000 | 2286903 | Install secondary filtration system on gearbox oil | 2020-09-26 07:58 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-12-04 11:20
5 | WTG-0208-0000 | 2286870 | Install secondary filtration system on gearbox oil | 2020-09-25 16:54 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | LHINKLE |  | 2023-10-23 23:15
2 | WTG-0227-0000 | 2324366 | Tower Cleaning & Needs radiator replaced | 2020-12-11 12:32 | Ready to Schedule | GBXOIL | GBXOILCOOL | PRAIRIE BREEZE2 | RKUDERA
1 | GBX-000001 | 2259961 | EM: Gearbox oil overtemperature | 2020-08-19 17:01 | Closed | GBXOIL | EM77 | VANTAGE | VANTAGE |  | 2020-08-20 09:56
1 | WTG-0005-0000 | 2285079 | Replace Moventas gearbox oil pump hose | 2020-09-15 15:07 | Closed | GBXOIL | GBXOILLEAK | STANTON | JBYNUM |  | 2022-10-31 08:59
5 | WTG-0223-0000 | 2286909 | Install secondary filtration system on gearbox oil | 2020-09-26 08:01 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-08-15 12:29
5 | WTG-0224-0000 | 2286910 | Install secondary filtration system on gearbox oil | 2020-09-26 08:01 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-06-25 13:49
5 | WTG-0233-0000 | 2286921 | Install secondary filtration system on gearbox oil | 2020-09-26 08:05 | Ready to Schedule | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2
5 | WTG-0234-0000 | 2286922 | Install secondary filtration system on gearbox oil | 2020-09-26 08:06 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-08-15 12:29
5 | WTG-0235-0000 | 2286923 | Install secondary filtration system on gearbox oil | 2020-09-26 08:06 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-08-15 12:29
5 | WTG-0231-0000 | 2286919 | Install secondary filtration system on gearbox oil | 2020-09-26 08:05 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-06-05 13:31
4.2 | WTG-0087-NDGP-0000 | 2286838 | GEARBOX OIL, Replace oil cooler | 2020-09-25 15:07 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCRESSWELL |  | 2020-12-14 07:16
4.2 | WTG-0088-NDGP-0000 | 2286839 | GEARBOX OIL, Replace oil cooler | 2020-09-25 15:12 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCRESSWELL |  | 2020-12-17 06:57
4 | WTG-0240-0000 | 2286928 | Install secondary filtration system on gearbox oil | 2020-09-26 08:08 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-07-09 13:03
4 | WTG-0241-0000 | 2286929 | Install secondary filtration system on gearbox oil | 2020-09-26 08:08 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-08-15 12:29
5 | WTG-0206-0000 | 2286868 | Install secondary filtration system on gearbox oil | 2020-09-25 16:54 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | LHINKLE |  | 2023-10-23 23:15
5 | WTG-0207-0000 | 2286869 | Install secondary filtration system on gearbox oil | 2020-09-25 16:54 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | LHINKLE |  | 2024-08-15 12:30
5 | WTG-0203-0000 | 2286865 | Install secondary filtration system on gearbox oil | 2020-09-25 16:52 | Ready to Schedule | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | LHINKLE |  | 2021-05-13 15:32
5 | WTG-0209-0000 | 2286871 | Install secondary filtration system on gearbox oil | 2020-09-25 16:55 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | LHINKLE |  | 2024-07-30 10:47
5 | WTG-0210-0000 | 2286872 | Install secondary filtration system on gearbox oil | 2020-09-25 16:55 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | LHINKLE |  | 2024-08-15 12:29
5 | WTG-0202-0000 | 2286863 | Install secondary filtration/needs whole rexroth system | 2020-09-25 16:50 | Ready to Schedule | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | LHINKLE
4 | WTG-0028-0000 | 2286842 | GEARBOX OIL, Add about 3 gallons | 2020-09-25 12:50 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-04-23 07:52
5 | WTG-0230-0000 | 2286918 | Install secondary filtration system on gearbox oil, Needs replaced | 2020-09-26 08:05 | Waiting for Parts | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2
1 | WTG-0002-0000 | 2288960 | GBX Suction Hose Replacement | 2020-09-30 17:24 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MMCCABE |  | 2021-06-23 09:48
4 | WTG-0090-0000 | 2288855 | Replace gearbox hose (orange) | 2020-09-30 13:26 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2021-04-15 07:07
4 | WTG-0090-0000 | 2288856 | Replace O-rings on flange between gear oil pump and filter pot | 2020-09-30 13:36 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2022-02-21 07:59
4.2 | WTG-0090-NDGP-0000 | 2292156 | GEARBOX OIL, Replace oil cooler | 2020-10-06 09:29 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JDETWILER |  | 2020-12-21 07:10
1 | WTG-0003-NDGP-0000 | 2337456 | GEARBOX OIL, Fix oil leak | 2021-01-11 16:49 | Closed | GBXOIL | GBXOILLEAK | VANTAGE | VANTAGE |  | 2021-01-12 10:46
1 | WTG-0004-0000 | 2337457 | GEARBOX, Replace oil suction hose | 2021-01-11 16:45 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | BSMITH |  | 2021-03-23 14:43
1 | WTG-0132-0000 | 2294507 | GEARBOX OIL, Fix oil leak | 2020-10-14 14:21 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | WAKE |  | 2020-10-15 14:55
1 | WTG-0148-0000 | 2294509 | GEARBOX OIL, Fix oil leak | 2020-10-14 14:35 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | WAKE |  | 2020-10-15 14:54
1 | WTG-0092-0000 | 2294599 | GEARBOX OIL, Fix oil leak | 2020-10-15 08:13 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | WAKE |  | 2020-11-30 15:06
1 | WTG-0080-0000 | 2294600 | GEARBOX OIL, Fix oil leak | 2020-10-15 08:15 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | WAKE |  | 2020-11-18 09:31
1 | WTG-0128-0000 | 2294598 | GEARBOX OIL, Fix oil leak | 2020-10-15 08:11 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | WAKE |  | 2020-11-24 16:24
1 | WTG-0016-NDG0-0000 | 2295304 | GEARBOX OIL, Particle counter installation | 2020-10-16 15:44 | Closed | GBXOIL | GBXPARTINS | GRAND RIDGE | GRAND RIDGE |  | 2020-10-22 14:59
4 | WTG-0211A-NDG0-0000 | 2320731 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2020-12-02 06:19 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2021-07-28 07:39
1 | WTG-0327-0000 | 2323832 | GEARBOX OIL, Radiator hose | 2020-12-09 07:36 | Cancelled | GBXOIL | GBXOILLEAK | BISHOP HILL III | BISHOP HILL |  | 2022-01-31 13:56
4 | WTG-0040A-0000 | 2329096 | GEARBOX OIL, Add/Top-Off about 7 gallons | 2020-12-22 15:12 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-03-01 14:55
1 | WTG-0005-0000 | 2337953 | GEARBOX OIL, Fix oil leak | 2021-01-13 12:04 | Closed | GBXOIL | GBXOILLEAK | BETHEL | AGALARZA |  | 2021-01-25 08:55
4 | WTG-0089-0000 | 2346185 | Gearbox oil pump is leaking | 2021-01-29 12:48 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2022-02-22 07:26
4 | WTG-0059A-0000 | 2349467 | Secondary Filtration Leaking | 2021-02-02 17:12 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2021-07-14 13:48
3 | WTG-0096-0000 | 3493442 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-01-13 13:18 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | BAZEFIELD |  | 2025-01-27 12:57
1 | WTG-0072-0000 | 2381630 | GEARBOX OIL, Fix oil leak | 2021-03-05 14:53 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | DTILLIS |  | 2021-09-10 11:10
1 | WTG-0035-0000 | 2401688 | Inspect for oil leak | 2021-04-16 15:53 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | WOLVERINECREEK |  | 2021-06-29 14:27
1 | WTG-0120-0000 | 2402491 | GEARBOX OIL, Fix oil leak | 2021-04-22 15:16 | Closed | GBXOIL | GBXOILLEAK | BETHEL | TENGELBRECHT |  | 2021-04-26 15:33
4 | WTG-0043-NDGP-0000 | 2405590 | GEARBOX OIL, Secondary oil filter leak | 2021-04-28 10:50 | Closed | GBXOIL | GBXFILTINS | FORWARD | KLEFFELMAN |  | 2022-03-18 06:52
4 | WTG-0043-NDG0-0000 | 2405591 | GEARBOX OIL, Add/Top-Off | 2021-04-28 10:55 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2021-04-29 07:04
4 | WTG-0210A-NDG0-0000 | 2410610 | GEARBOX OIL, Add/Top-Off 5gals | 2021-05-06 15:39 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2021-07-26 07:45
4 | WTG-0013-0000 | 2410552 | GEARBOX OIL, Add/Top-Off about 5 Gallons | 2021-05-06 15:28 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-05-13 07:10
4 | WTG-0072A-0000 | 3055005 | GEARBOX OIL, Add/Top-Off 5gallons | 2022-12-08 14:07 | Closed | GBXOIL | GBXOILADD | FORWARD | DMONROE |  | 2022-12-19 09:51
5 | WTG-3065-0000 | 2904427 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-03-30 12:44 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-08-02 12:27
1 | WTG-0017-0000 | 2414466 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2021-05-07 15:50 | Cancelled | GBXOIL | GBXOILCOOL | GRAND RIDGE | CWRIGHT |  | 2023-06-29 13:21
9 | WTG-0071-0000 | 3063745 | GEARBOX, Oil Change | 2023-01-04 09:02 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-03-15 09:15
2 | WTG-0011-0000 | 2468380 | GEARBOX OIL, Fix oil leak | 2021-07-23 13:22 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | ZMUELLER |  | 2021-09-02 11:20
1 | WTG-0213-0000 | 2468051 | GEARBOX OIL, Fix oil leak | 2021-07-21 13:29 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | CWERNER |  | 2021-11-17 17:16
1 | WTG-0007-0000 | 2467828 | GEARBOX OIL, Fix oil leak | 2021-07-20 14:03 | Closed | GBXOIL | GBXOILLEAK | MARSH HILL | PHEATON |  | 2021-08-26 13:03
1 | WTG-0015-0000 | 2423908 | GEARBOX OIL, Fix oil leak | 2021-05-25 14:45 | Closed | GBXOIL | GBXOILLEAK | MCADOO | TRUDE |  | 2021-06-01 15:52
2 | WTG-0033-0000 | 2425518 | Gbx oil pump replacement | 2021-05-27 14:36 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2021-06-02 11:19
4.1 | WTG-0040A-NDGD-0000 | 2428027 | Desiccant needed | 2021-06-02 14:28 | Closed | GBXOIL | GBXFILTELEM | FORWARD | KLEFFELMAN |  | 2021-11-11 12:28
4.2 | WTG-0008-0000 | 2438197 | Replace Leaking GBX Lube Pump | 2021-06-15 07:31 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JJENSEMA |  | 2021-12-02 12:40
1 | WTG-0093-0000 | 2438725 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2021-06-17 07:51 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | JSTEEN |  | 2023-11-07 07:43
1 | WTG-0050-0000 | 2443518 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2021-06-30 07:09 | Closed | GBXOIL | GBXOILCOOL | ORANGEVILLE | NSPINK |  | 2021-06-30 14:31
1 | WTG-0040-0000 | 2464032 | GEARBOX OIL, Oil Sample | 2021-07-08 08:00 | Closed | GBXOIL | GBXOILSAMP | ORANGEVILLE | NSPINK |  | 2021-07-13 08:20
1 | WTG-0043-0000 | 2464089 | GEARBOX OIL, Fix oil leak | 2021-07-08 10:50 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | PHEATON |  | 2021-07-13 08:16
1 | WTG-0058-NDG0-0000 | 2470540 | GEARBOX OIL, Add/Top-Off | 2021-07-29 12:48 | Closed | GBXOIL | GBXOILADD | ORANGEVILLE | JROULIER |  | 2021-10-05 13:58
1 | WTG-0008-NDG0-0000 | 2470541 | GEARBOX OIL, Oil Sample | 2021-07-29 12:51 | Closed | GBXOIL | GBXOILSAMP | ORANGEVILLE | JROULIER |  | 2021-10-14 14:44
1 | WTG-0058-NDG0-0000 | 2470544 | GEARBOX OIL, Oil Sample | 2021-07-29 12:53 | Closed | GBXOIL | GBXOILSAMP | ORANGEVILLE | JROULIER |  | 2021-10-25 09:24
1 | WTG-0074-0000 | 2470642 | GEARBOX OIL, Secondary filter system installation | 2021-07-29 16:32 | Cancelled | GBXOIL | GBXFILTINS | JUDITH GAP | CROBERTS |  | 2022-01-12 14:12
1 | WTG-0043-0000 | 2476799 | GEARBOX OIL, Fix oil leak | 2021-08-10 13:02 | Closed | GBXOIL | GBXOILLEAK | MCADOO | AHILL2 |  | 2021-08-24 09:06
4 | WTG-0083-0000 | 2515621 | GEARBOX OIL, Add/Top-Off about 5 Gallons | 2021-08-16 11:43 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-08-19 06:59
4.1 | WTG-0055A-0000 | 2573679 | 5 gallons oil add | 2021-09-02 15:02 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2022-03-18 06:54
4 | WTG-0090-0000 | 2573680 | 5 gallons oil add | 2021-09-02 15:03 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2022-02-21 08:00
5 | WTG-0042-0000 | 2575726 | CMS Generator Bearing Check | 2021-09-07 11:52 | Closed | CMS | CMSGENB | UPSTREAM | CBILLIG |  | 2022-08-18 15:28
5 | WTG-0061-0000 | 2575728 | CMS Generator Bearing Check | 2021-09-07 11:53 | Cancelled | CMS | CMSGENB | UPSTREAM | CBILLIG |  | 2022-02-08 16:04
1 | WTG-0063-NDGP-0000 | 2576386 | GEARBOX OIL, Fix oil leak | 2021-09-07 17:08 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | TWIEDEMEIER |  | 2022-07-13 09:00
1 | WTG-0084-NDGP-0000 | 2578935 | Secondary Filtration Installation | 2021-09-17 11:32 | Cancelled | GBXOIL | GBXFILTINS | GREXP | CWRIGHT |  | 2023-06-29 13:23
5 | WTG-0041-0000 | 2581737 | CMS Main Bearing Check | 2021-09-27 10:18 | Closed | CMS | CMSMB | UPSTREAM | CBILLIG |  | 2021-10-18 09:36
1 | WTG-0020-NDGP-0000 | 2617412 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2021-10-18 14:32 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | CCUSACK |  | 2022-09-28 16:46
1 | WTG-0025-0000 | 2624911 | GEARBOX OIL, Fix radiator leak | 2021-10-27 16:21 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2023-05-31 14:53
1 | WTG-0044-0000 | 2624912 | GEARBOX OIL, Fix radiator leak | 2021-10-27 16:21 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2023-03-07 16:20
5 | WTG-0010-NDG0-0000 | 2632876 | GEARBOX OIL, Add 3 gallons | 2021-11-05 07:10 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2022-03-18 06:55
4 | WTG-0039-NDG0-0000 | 2633197 | GEARBOX OIL, Add 5 Gallons | 2021-11-05 10:40 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-05-04 10:30
4 | WTG-0061-0000 | 2644922 | GEARBOX OIL, Add 5 gallons | 2021-11-12 10:31 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-02-15 10:22
2 | GBX-00056 | 2647045 | CMS Gearbox Borescope | 2021-11-18 12:54 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2022-09-12 12:06
1 | WTG-0153-0000 | 2647180 | GEARBOX OIL, Fix oil leak | 2021-11-18 08:40 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2021-12-01 13:47
9 | WTG-0425-0000 | 2650315 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
1 | WTG-0108-0000 | 2324283 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2020-12-11 11:02 | Closed | GBXOIL | GBXOILCOOL | BETHEL | AGALARZA |  | 2023-12-19 16:23
2 | WTG-0056-NDG0-0000 | 2429460 | Add Amsoil | 2021-06-04 11:01 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2021-10-25 10:01
4 | WTG-0029A-0000 | 2353560 | Lube pump leaking | 2021-02-06 13:55 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2021-05-25 09:46
2 | WTG-0026-NDG0-0000 | 2375093 | Add Amsoil | 2021-02-22 17:05 | Closed | GBXOIL | GBXOILADD | VANTAGE | VANTAGE |  | 2021-03-02 10:39
1 | WTG-0052-0000 | 2376579 | GEARBOX OIL, Fix oil leak - ZF Manifold | 2021-02-25 16:02 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | NHEITHOFF |  | 2021-03-12 09:18
4 | WTG-0036-0000 | 2383774 | GEARBOX OIL, Replace yellow oil hose | 2021-03-17 10:58 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2021-06-02 11:00
1 | WTG-0228-0000 | 2395028 | GEARBOX OIL, Fix oil leak | 2021-03-31 16:31 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | DGORDON |  | 2021-05-13 15:32
2 | WTG-0041-NDG0-0000 | 2401892 | Add Amsoil | 2021-04-19 09:55 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2021-04-21 12:04
1 | WTG-0003-NDG0-0000 | 2402503 | GEARBOX OIL, Fix oil leak | 2021-04-22 15:33 | Cancelled | GBXOIL | GBXOILLEAK | GRAND RIDGE | GRAND RIDGE |  | 2023-06-29 13:21
9 | WTG-0020-NDG0-0000 | 2402267 | GEARBOX, Oil Change | 2021-04-21 10:41 | Closed | GBXOIL | GBXOILCHG | BLOOMING GROVE | DGEORGE |  | 2021-04-28 10:43
9 | WTG-0025-NDG0-0000 | 2402269 | GEARBOX, Oil Change | 2021-04-21 11:22 | Closed | GBXOIL | GBXOILCHG | BLOOMING GROVE | DGEORGE |  | 2021-04-30 10:24
2 | WTG-0043-NDG0-0000 | 2405650 | Add Amsoil | 2021-04-28 16:47 | Closed | GBXOIL | GBXOILADD | VANTAGE | CLANDERS |  | 2022-01-20 10:28
1 | WTG-0018-0000 | 2410071 | Gearbox Hose Needs Replacement | 2021-05-05 18:01 | Cancelled | GBXOIL | GBXOILLEAK | GRAND RIDGE | FANAYA |  | 2023-06-29 13:21
2 | WTG-0327-0000 | 2410770 | MAIN BEARING, Main bearing borescope inspection | 2021-05-06 17:56 | Closed | CMS | CMSMBBORE | BISHOP HILL III | ALATERZA |  | 2022-03-08 07:22
1 | WTG-0057-0000 | 2426115 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2021-05-29 11:36 | Closed | GBXOIL | GBXOILCOOL | ORANGEVILLE | CGREIS |  | 2021-06-01 14:01
1 | WTG-0051-NDGP-0000 | 2427147 | GEARBOX OIL, Fix oil leak | 2021-06-01 16:44 | Closed | GBXOIL | GBXOILLEAK | CAMP SPRINGS I | JPOTTER |  | 2021-10-29 07:05
4 | WTG-0041A-0000 | 2433835 | GEARBOX OIL, Add/Top-Off | 2021-06-09 12:14 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-06-10 08:01
4 | WTG-0001-0000 | 2441086 | GEARBOX OIL, Replace oil pump and coupler and add oil | 2021-06-23 11:02 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2021-07-02 07:08
5 | WTG-0101-0000 | 2464125 | CMS KEYPHASOR SENSOR ISSUE | 2021-07-08 12:00 | Cancelled | CMS | CMSINSP | BETHEL | CMORALES |  | 2023-03-15 10:44
4 | WTG-0059A-0000 | 2465423 | Replace gearbox oil filter pump | 2021-07-13 14:12 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2021-07-14 14:02
1 | WTG-0020-0000 | 2468594 | GEARBOX OIL, Secondary filter system installation | 2021-07-23 16:54 | Cancelled | GBXOIL | GBXFILTINS | JUDITH GAP | CROBERTS |  | 2022-01-12 15:38
2 | WTG-0077-NDGP-0000 | 2475070 | GEARBOX OIL, Fix oil leak | 2021-08-05 12:36 | Closed | GBXOIL | GBXOILLEAK | GREXP | JCARRETTO |  | 2024-09-10 12:41
2 | WTG-0210-0000 | 2571229 | GEARBOX OIL, Replace oil cooler radiator | 2021-08-31 11:55 | Closed | GBXOIL | GBXOILCOOL | PRAIRIE BREEZE2 | DGORDON |  | 2023-05-15 13:00
4.2 | WTG-0105-0000 | 2607601 | GEARBOX OIL, Replace oil cooler | 2021-10-04 08:22 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCAPEN |  | 2021-10-19 12:35
4 | WTG-0016-0000 | 2616195 | GEARBOX OIL, Add about 7 gallons | 2021-10-13 07:36 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-04-10 17:23
9 | SITE-AIPL | 2623606 | WO for OOS Oil Changes | 2021-10-25 21:59 | Ready to Schedule | GBXOIL | GBXOILCHG | ALLIANT IPL | MCOURTNEY
9 | SITE-AIPL | 2623607 | WO for OOS Oil Changes -UPWF | 2021-10-25 22:14 | Ready to Schedule | GBXOIL | GBXOILCHG | ALLIANT IPL | MCOURTNEY
9 | SITE-AIPL | 2623608 | WO for OOS Oil Changes -WWF | 2021-10-25 22:23 | Ready to Schedule | GBXOIL | GBXOILCHG | ALLIANT IPL | MCOURTNEY
2 | WTG-0051-0000 | 2631668 | CMS Main Bearing Borescope | 2021-11-02 15:58 | Closed | CMS | CMSMBBORE | MIAMI 1 | BBRASWELL |  | 2021-11-04 10:31
5 | WTG-0016-0000 | 2635789 | CMS HSS Check | 2021-11-08 12:56 | Closed | CMS | CMSHSS | BLOOMING GROVE | CBILLIG |  | 2021-11-15 08:55
2 | WTG-0044-NDGP-0000 | 2645556 | WTG-044 Oil clean up | 2021-11-16 10:18 | Closed | GBXOIL | GBXOILLEAK | ENGLISH FARMS | SBARTHOLOMEW |  | 2021-11-23 10:39
2 | WTG-00D5-0000 | 2645569 | CMS Main Bearing Borescope | 2021-11-16 10:43 | Cancelled | CMS | CMSMBBORE | COYOTE RIDGE | CBILLIG |  | 2022-03-22 13:06
9 | WTG-0431-0000 | 2650312 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
9 | WTG-0415-0000 | 2650313 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
9 | WTG-0409-0000 | 2650314 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
9 | WTG-0426-0000 | 2650316 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
9 | WTG-0427-0000 | 2650317 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
9 | WTG-0028-0000 | 2650282 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0025-0000 | 2650279 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0026-0000 | 2650280 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0027-0000 | 2650281 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0035-0000 | 2650283 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0037-0000 | 2650284 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0063-0000 | 2650288 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0048-0000 | 2650285 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0054-0000 | 2650286 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0055-0000 | 2650287 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0082-0000 | 2650289 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0086-0000 | 2650290 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0087-0000 | 2650291 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0088-0000 | 2650292 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
9 | WTG-0130-0000 | 2650293 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2022-09-15 13:52
9 | WTG-0037-0000 | 2650294 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | ENGLISH FARMS | CMORALES |  | 2022-01-10 11:35
9 | WTG-0044-0000 | 2650295 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | ENGLISH FARMS | CMORALES |  | 2022-01-10 11:30
9 | WTG-0084-0000 | 2650296 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | ENGLISH FARMS | CMORALES |  | 2022-01-10 11:35
9 | WTG-0071-0000 | 2650297 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | ENGLISH FARMS | CMORALES |  | 2022-01-10 11:41
9 | WTG-0019-0000 | 2650298 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | ENGLISH FARMS | CMORALES |  | 2022-01-10 11:49
9 | WTG-0083-0000 | 2650299 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | ENGLISH FARMS | CMORALES |  | 2022-01-10 11:36
9 | WTG-0063-0000 | 2650300 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | ENGLISH FARMS | CMORALES |  | 2022-01-10 11:55
1 | WTG-00G2-NDG0-0000 | 2655570 | CMS Gearbox Borescope | 2021-12-03 15:06 | Closed | CMS | CMSGBXBORE | TATANKA RIDGE | CBILLIG |  | 2022-04-11 12:48
2 | WTG-0037-0000 | 2661070 | Main Bearing borescope and purge | 2021-12-08 16:35 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | CBILLIG |  | 2021-12-28 13:41
5 | GEN-00038 | 2717453 | CMS Generator Bearing Check | 2022-01-11 09:45 | Closed | CMS | CMSGENB | UPSTREAM | CBILLIG |  | 2022-02-08 14:47
1 | WTG-0020-0000 | 2802969 | GEARBOX OIL Cooler, Fix oil leak | 2022-02-15 16:15 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CPOLIFKA |  | 2022-03-17 17:01
4 | WTG-0027-0000 | 2738823 | Gearbox Purple Oil Hose Replacement | 2022-01-27 15:57 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2022-03-18 06:58
5 | WTG-0044-NDGP-0000 | 2740288 | Replace spider insert | 2022-01-31 12:37 | Closed | GBXOIL | GBXOILCOOL | FORWARD | ALANGKAU |  | 2022-02-01 13:58
5 | WTG-0044-NDGP-0000 | 2740289 | Secondary filter is leaking | 2022-01-31 13:26 | Closed | GBXOIL | GBXFILTINS | FORWARD | ALANGKAU |  | 2022-02-01 13:59
4.1 | WTG-0095-0000 | 2789110 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0074A-0000 | 2654549 | Oil leak at secondary filter | 2021-12-02 13:17 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JJENSEMA |  | 2022-06-10 08:51
2 | WTG-0045-0000 | 2656781 | CMS Gearbox Borescope | 2021-12-06 16:49 | Closed | CMS | CMSGBXBORE | SUNDANCE | CBILLIG |  | 2022-02-16 13:34
2 | WTG-0328-0000 | 2679219 | Particle Counter Install Verification | 2021-12-16 12:51 | Closed | GBXOIL | GBXPARTTS | BISHOP HILL III | CBILLIG |  | 2022-01-25 15:46
2 | WTG-0090-0000 | 2680861 | CMS Main Bearing Borescope and Purge | 2021-12-21 08:31 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | HMORENO |  | 2021-12-22 09:39
4 | WTG-0046-0000 | 2803682 | GEARBOX OIL, Secondary filter system element change | 2022-02-18 10:52 | Closed | GBXOIL | GBXFILTELEM | FORWARD | ALANGKAU |  | 2022-09-16 09:42
4 | WTG-0205-0000 | 2727896 | GEARBOX OIL, Add 5 Gallons | 2022-01-20 13:53 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2022-01-25 09:28
4 | WTG-0205-0000 | 2727897 | Secondary filter leak | 2022-01-20 14:20 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2022-01-25 09:28
1 | GBX-000003 | 2728842 | Gearbox oil level low | 2022-01-21 14:16 | Closed | GBXOIL | EM225 | WILLOW CREEK | JBENNETT |  | 2022-01-25 14:59
5 | WTG-0308-0000 | 2737576 | GEARBOX OIL, Fix oil leak | 2022-01-26 07:47 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | RKUDERA |  | 2022-10-28 16:22
1 | WTG-0314-0000 | 2737577 | GEARBOX OIL, Fix oil leak | 2022-01-26 07:48 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | RKUDERA |  | 2022-02-10 11:58
2 | WTG-0017-0000 | 2739404 | Gearbox oil pump leak and replace coupler | 2022-01-28 15:24 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2022-02-03 10:35
5 | WTG-0017-0000 | 2739403 | Secondary Filter Pump Leaking at Shaft Seal | 2022-01-28 15:23 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2022-02-03 10:35
4.1 | WTG-0082-0000 | 2789097 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0083-0000 | 2789098 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0084-0000 | 2789099 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0085-0000 | 2789100 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0086-0000 | 2789101 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0087-0000 | 2789102 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0088-0000 | 2789103 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0089-0000 | 2789104 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0090-0000 | 2789105 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0091-0000 | 2789106 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0092-0000 | 2789107 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0093-0000 | 2789108 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0094-0000 | 2789109 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0096-0000 | 2789111 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0097-0000 | 2789112 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0098-0000 | 2789113 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0099-0000 | 2789114 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0100-0000 | 2789115 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0101-0000 | 2789116 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0105-0000 | 2789120 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0102-0000 | 2789117 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0103-0000 | 2789118 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0104-0000 | 2789119 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0106-0000 | 2789121 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0107-0000 | 2789122 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0108-0000 | 2789123 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0109-0000 | 2789124 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0110-0000 | 2789125 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0111-0000 | 2789126 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0022-0000 | 2789037 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0019-0000 | 2789034 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0020-0000 | 2789035 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0021-0000 | 2789036 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0023-0000 | 2789038 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0024-0000 | 2789039 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0025-0000 | 2789040 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0026-0000 | 2789041 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0027-0000 | 2789042 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0003-0000 | 2789018 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | SYS-WTG-BETH | 2789015 | 2022 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL | GBXOILSAMP | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0001-0000 | 2789016 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0002-0000 | 2789017 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0004-0000 | 2789019 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0005-0000 | 2789020 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0006-0000 | 2789021 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0007-0000 | 2789022 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0011-0000 | 2789026 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0008-0000 | 2789023 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0009-0000 | 2789024 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0010-0000 | 2789025 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0012-0000 | 2789027 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0013-0000 | 2789028 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0014-0000 | 2789029 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0015-0000 | 2789030 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0016-0000 | 2789031 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0017-0000 | 2789032 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4 | WTG-0083-0000 | 2789196 | Secondary filter pump leak at shaft seal | 2022-02-02 16:20 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2022-04-10 17:29
5 | WTG-0083-F000-0000 | 2789197 | Replace red elastomer insert on oil pump coupler | 2022-02-02 16:24 | Closed | GBXOIL | GBXOILCOOL | FORWARD | ALANGKAU |  | 2022-03-02 09:33
1 | WTG-0203-0000 | 2793681 | GEARBOX OIL, Clean up oil./yaw twist. | 2022-02-03 13:44 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | RKUDERA |  | 2022-02-10 11:57
5 | WTG-0066-NDG0-0000 | 2793653 | GEARBOX OIL, Add/Top-Off 5 gallons | 2022-02-03 12:34 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2022-03-18 06:58
4.1 | WTG-0050-0000 | 2814145 | GEARBOX OIL, Replace oil cooler bypass hose | 2022-03-09 13:21 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2022-03-15 07:01
1 | WTG-0023-NALC-0000 | 2826361 | EM: SSD Opened Safety Chain | 2022-03-16 13:57 | Closed | CMS | EM1505 | MAVERICK | BCROPP |  | 2022-04-18 16:29
2 | WTG-0050-NDG0-0000 | 2881836 | Add Amsoil | 2022-03-21 15:40 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2022-03-21 16:28
5 | WTG-0052-0000 | 2891117 | GEARBOX OIL, Fix top of gbx manifold leak | 2022-03-24 16:16 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | AHOFFMANN |  | 2022-08-31 16:45
5 | WTG-0013-0000 | 2912309 | Replace primary GBX oil filter | 2022-04-11 12:15 | Closed | GBXOIL | GBXFILTELEM | FORWARD | JLAWRENCE |  | 2022-06-10 09:02
1 | WTG-0002-NDG0-0000 | 2912322 | GEARBOX OIL, Fix oil leak | 2022-04-11 15:42 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | MMAGER |  | 2022-07-22 16:56
5 | WTG-0032-0000 | 2919868 | Replace primary GBX oil filter | 2022-04-12 14:48 | Closed | GBXOIL | GBXFILTELEM | FORWARD | ALANGKAU |  | 2022-06-10 09:03
1 | WTG-0039-0000 | 2920100 | GEARBOX OIL, Fix oil leak | 2022-04-13 16:19 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | PMAGER |  | 2022-05-12 10:05
2 | WTG-0026-0000 | 2920947 | CMS Main Bearing Check | 2022-04-18 10:47 | Closed | CMS | CMSMB | MAVERICK | CBILLIG |  | 2023-03-27 11:54
6 | GBX-00007 | 2922061 | GEARBOX OIL, Particle counter troubleshooting | 2022-04-21 16:53 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | CBILLIG |  | 2022-05-18 13:22
5 | WTG-0034-0000 | 2921991 | GEARBOX OIL, Replace primary GBX oil filter | 2022-04-21 10:24 | Closed | GBXOIL | GBXFILTELEM | FORWARD | JLAWRENCE |  | 2022-08-29 10:28
2 | WTG-0034-0000 | 2921992 | Fix oil leak at HSS BRG RS temp probe (See comments) | 2022-04-21 13:17 | In Progress | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE
5 | BRG-000080 | 2922956 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-04-25 10:23 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-05-03 17:07
5 | GBX-00103 | 2922958 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-04-25 10:37 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-06-07 13:38
2 | GBX-00045 | 2923526 | GEARBOX OIL, Particle counter troubleshooting | 2022-04-26 15:08 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | CBILLIG |  | 2022-05-16 09:53
5 | WTG-0035-0000 | 2924037 | GEARBOX OIL, Replace Primary Filter | 2022-04-27 15:02 | Closed | GBXOIL | GBXFILTELEM | FORWARD | ALANGKAU |  | 2022-07-07 08:47
2 | GBX-00001 | 2928225 | CMS Gearbox Borescope | 2022-05-05 15:40 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2022-06-28 12:20
2 | GBX-00054 | 2928232 | CMS Gearbox Borescope | 2022-05-05 15:42 | Cancelled | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2022-08-19 10:24
5 | WTG-0055-0000 | 2929289 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-05-09 09:32 | Closed | CMS | CMSTRBLSHOOT | MAVERICK | CBILLIG |  | 2023-10-24 16:45
2 | WTG-0025-NDB0-0000 | 3220555 | CMS Main Bearing Borescope | 2023-11-07 09:13 | Closed | CMS | CMSMBBORE | THUNDERHEAD | AMITCHELL |  | 2023-11-17 13:34
4 | WTG-0003A-0000 | 2936826 | GEARBOX OIL, Replace oil cooler hose (orange) | 2022-05-20 10:26 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-12-19 08:16
5 | WTG-00D5-0000 | 2937209 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-05-23 10:54 | Cancelled | CMS | CMSTRBLSHOOT | COYOTE RIDGE | CBILLIG |  | 2022-07-07 10:44
1 | WTG-0066-0000 | 2938643 | GEARBOX OIL, Secondary filter system not working | 2022-05-26 15:17 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CPOLIFKA |  | 2023-04-24 11:23
1 | WTG-0015-NDG0-0000 | 2945469 | CMS Gearbox Borescope | 2022-06-14 16:04 | Cancelled | CMS | CMSGBXBORE | BLOOMING GROVE | CBILLIG |  | 2022-10-13 13:04
1 | WTG-0083-NDG0-0000 | 2946949 | EM: Gearbox oil overtemperature | 2022-06-17 13:18 | Closed | GBXOIL |  | GRATIOT | DONEILL |  | 2022-06-17 16:27
1 | GBX-00036 | 2946994 | GEARBOX OIL, Particle counter installation | 2022-06-17 16:06 | Closed | GBXOIL | GBXPARTINS | SANTA RITA EAST | CBILLIG |  | 2022-06-22 08:16
5 | GEN-01106 | 2947752 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-20 14:57 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG
2 | WTG-0002-0000 | 2947664 | CMS Main Bearing Borescope | 2022-06-17 16:37 | Closed | CMS | CMSMBBORE | CAMP SPRINGS I | PPRATER |  | 2022-11-21 09:32
2 | WTG-0002-0000 | 2947665 | CMS Main Bearing Borescope | 2022-06-17 16:37 | Closed | CMS | CMSMBBORE | CAMP SPRINGS I | PPRATER |  | 2023-05-25 07:20
1 | GBX-00120 | 2947723 | CMS Gearbox Borescope | 2022-06-20 13:29 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | CBILLIG |  | 2022-06-26 09:34
5 | WTG-1098-NDG0-0000 | 2947751 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-20 14:53 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-27 11:36
5 | WTG-3061-0000 | 2948412 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-22 10:19 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-13 12:19
2 | WTG-0059A-0000 | 2950068 | GEARBOX OIL, Replace oil hoses ( see comments ) | 2022-06-27 13:12 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-01-09 16:16
4 | WTG-0060A-0000 | 2950739 | GEARBOX OIL, Add/Top-Off 3-5 gal | 2022-06-28 12:44 | Closed | GBXOIL | GBXOILADD | FORWARD | DMONROE |  | 2022-09-14 09:36
2 | WTG-0086-NDB0-0000 | 2950746 | CMS Main Bearing Borescope | 2022-06-28 14:54 | Cancelled | CMS | CMSMBBORE | DEUEL HARVEST | CBILLIG |  | 2022-09-21 17:10
4 | WTG-0041A-0000 | 2950641 | Secondary Oil Filter Leak | 2022-06-28 11:41 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2022-12-09 10:31
4 | WTG-0081-0000 | 2950642 | GEARBOX OIL, Add 5 gallons | 2022-06-28 11:48 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-01-30 11:02
5 | WTG-0041A-0000 | 2950643 | Flip GBX Thermal Bypass Valve (TBV) | 2022-06-28 12:34 | Closed | GBXOIL | GBXOILCOOL | FORWARD | ALANGKAU |  | 2022-07-05 08:51
4 | WTG-0023A-0000 | 2955656 | GEARBOX OIL, Fix oil leak on Jensen | 2022-07-07 10:21 | Closed | GBXOIL | GBXOILLEAK | FORWARD | DMONROE |  | 2022-10-10 15:10
5 | WTG-0212-0000 | 2958778 | Replace, Filter pot drain valve | 2022-07-13 12:21 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-08-07 09:22
1 | WTG-0003-0000 | 2965308 | GEARBOX OIL, Fix oil leak | 2022-07-22 00:45 | Closed | GBXOIL | GBXOILLEAK | MAVERICK | BPETERMAN |  | 2022-12-06 12:12
2 | WTG-0305-0000 | 3121867 | CMS Gearbox Borescope | 2023-05-04 10:51 | Closed | CMS | CMSGBXBORE | PRAIRIE BREEZE3 | JSTAHLECKER |  | 2023-05-15 12:59
5 | WTG-2062-0000 | 2971145 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-02 13:56 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-10 10:47
5 | WTG-2084-0000 | 2971146 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-02 13:56 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-10 11:07
5 | WTG-0015-0000 | 2988830 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-13 10:42
5 | WTG-0036-0000 | 2988836 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 10:50
5 | WTG-0059-0000 | 2988837 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 10:51
5 | WTG-0073-0000 | 2988838 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-04-05 14:49
5 | WTG-0077-0000 | 2988839 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 10:58
5 | GBX-00028 | 2992339 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-18 14:23 | Closed | CMS | CMSTRBLSHOOT | UPSTREAM | CBILLIG |  | 2022-08-31 16:33
4 | WTG-0042-0000 | 2992478 | GEARBOX OIL, Oil Sample | 2022-08-18 16:54 | Closed | GBXOIL | GBXOILSAMP | UPSTREAM | JSTAHLECKER |  | 2023-06-05 15:38
1 | WTG-0048-0000 | 2992479 | GEARBOX OIL, Oil Sample | 2022-08-18 16:56 | Closed | GBXOIL | GBXOILSAMP | UPSTREAM | JSTAHLECKER |  | 2022-11-15 16:37
1 | WTG-0039-0000 | 3006673 | Oil Cleanup | 2022-08-29 08:39 | Closed | GBXOIL | GBXOILLEAK | DEUEL HARVEST | CKRAUS |  | 2022-09-22 08:38
2 | GBX-00049 | 3012690 | CMS HSS Check | 2022-09-07 10:37 | Closed | CMS | CMSHSS | UPSTREAM | CBILLIG |  | 2022-10-11 14:07
5 | WTG-0B01-NDGP-0000 | 3018833 | GEARBOX OIL, Secondary filter system element change | 2022-09-15 09:15 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | KRENICK |  | 2024-07-11 08:40
1 | WTG-0045-0000 | 3019598 | GEARBOX OIL, Fix oil leak | 2022-09-16 10:51 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | NSPINK |  | 2022-09-16 13:44
5 | WTG-0087-NDG0-0000 | 3024734 | GEARBOX OIL, Add/Top-Off 5GAls | 2022-09-22 06:58 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2022-09-26 08:37
2 | WTG-0005-0000 | 3027290 | GEARBOX OIL, Add/Top-Off | 2022-09-28 14:50 | Closed | GBXOIL | GBXOILADD | GORDON BUTTE | TWIEDEMEIER |  | 2022-11-23 10:26
5 | WTG-3038-0000 | 3027353 | CMS HSS Check | 2022-09-28 17:17 | Closed | CMS | CMSHSS | TRAVERSE | JFRIESEN |  | 2022-10-25 09:30
2 | WTG-0111-0000 | 3028302 | GEARBOX OIL, Oil Sample | 2022-09-30 14:08 | Closed | GBXOIL | GBXOILSAMP | MIAMI 1 | CMORRISON |  | 2024-09-24 07:19
1 | WTG-0028-0000 | 3028307 | GEARBOX OIL, Fix oil leak | 2022-09-30 14:38 | Closed | GBXOIL | GBXOILLEAK | MCADOO | MGIVENS |  | 2022-10-04 13:42
2 | GBX-00078 | 3028329 | CMS Gearbox Borescope | 2022-09-30 15:41 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2022-10-18 16:08
1 | WTG-0107-0000 | 3030290 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2022-10-05 10:11 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | JEPPISON |  | 2022-10-07 15:05
5 | WTG-0007-0000 | 3033100 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-10-11 14:44 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-11-03 08:28
4.1 | WTG-0018-0000 | 2789033 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4 | WTG-0026-0000 | 2814806 | GEARBOX OIL, replace multiple gearbox hoses (see comments) | 2022-03-11 10:33 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-01-30 09:27
4 | WTG-0043-0000 | 2815625 | GEARBOX OIL, Replace blue and purple hoses | 2022-03-15 12:34 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-04-10 17:41
4 | WTG-0009-NDGP-0000 | 2826311 | GEARBOX OIL, Secondary filter system installation | 2022-03-16 08:42 | Closed | GBXOIL | GBXFILTINS | WOLVERINE CREEK | ACASON |  | 2024-07-09 17:30
4.1 | WTG-0083-0000 | 2860128 | GBX Hose Replacement Purple & Yellow | 2022-03-18 10:29 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-09-14 09:35
4 | WTG-0044-0000 | 2879265 | GEARBOX OIL, Replace bypass hose (purple hose) | 2022-03-21 10:54 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-10-07 14:51
5 | WTG-0077-0000 | 2917863 | Replace Gearbox Hose | 2022-04-12 12:26 | Closed | GBXOIL | GBXOILLEAK | BETHEL | JGARLAND |  | 2022-08-29 16:48
2 | WTG-0022-NDG0-0000 | 2920112 | GEARBOX OIL, Add/Top-Off | 2022-04-13 16:53 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DLOWREY |  | 2022-04-15 15:36
5 | WTG-0031-0000 | 2920591 | GEARBOX OIL, Replace primary GBX oil filter | 2022-04-15 11:57 | Closed | GBXOIL | GBXFILTELEM | FORWARD | JLAWRENCE |  | 2022-10-07 14:58
2 | WTG-0017-0000 | 2921372 | GEARBOX OIL, Fix oil leak | 2022-04-19 15:17 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | AADAMS |  | 2025-01-30 07:38
6 | GBX-00029 | 2922062 | GEARBOX OIL, Particle counter troubleshooting | 2022-04-21 17:00 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | CBILLIG |  | 2022-06-24 08:27
3.1 | WTG-0005-NDG0-0000 | 3262516 | CMS sensor | 2024-01-30 14:31 | Closed | CMS | CMSINSP | ORANGEVILLE | BHUNTER |  | 2024-05-24 08:27
1 | WTG-0006-NDGP-0000 | 2928154 | GEARBOX OIL, Fix oil leak | 2022-05-05 15:36 | Closed | GBXOIL | GBXOILLEAK | VANTAGE | CCUSACK |  | 2022-05-10 13:08
4 | WTG-0008-0000 | 2928226 | GEARBOX OIL, Secondary filter leak | 2022-05-05 12:40 | Closed | GBXOIL | GBXFILTELEM | FORWARD | DMONROE |  | 2022-05-10 09:42
5 | WTG-0008-0000 | 2928227 | GEARBOX OIL, Replace Orange Hose | 2022-05-05 12:47 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-08-29 10:29
5 | WTG-0008-0000 | 2928228 | GBX Replace desiccant hose | 2022-05-05 12:51 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-08-29 10:29
5 | WTG-0008-0000 | 2928230 | Replace GBX Primary filter | 2022-05-05 13:13 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-08-29 10:31
4 | WTG-0009-0000 | 2928141 | GEARBOX OIL, Replace primary GBX oil filter | 2022-05-05 12:52 | Closed | GBXOIL | GBXFILTELEM | FORWARD | JLAWRENCE |  | 2022-12-09 09:42
2 | WTG-0007-NDG0-0000 | 2929059 | GEARBOX OIL, Add/Top-Off | 2022-05-07 16:20 | Closed | GBXOIL | GBXOILADD | VANTAGE | CCUSACK |  | 2022-08-18 15:33
2 | WTG-0037-NDG0-0000 | 2929058 | GEARBOX OIL, Add/Top-Off | 2022-05-07 16:16 | Closed | GBXOIL | GBXOILADD | VANTAGE | CCUSACK |  | 2022-08-18 15:34
2 | WTG-0023-0000 | 2929323 | CMS Generator Bearing Check | 2022-05-09 10:41 | Closed | CMS | CMSGENB | MAVERICK | CBILLIG |  | 2022-09-06 11:51
5 | WTG-3035-NDG0-0000 | 2930909 | CMS HSS Check | 2022-05-12 14:39 | Cancelled | CMS | CMSHSS | TRAVERSE | CBILLIG |  | 2022-06-22 14:59
2 | GBX-00045 | 2931531 | GEARBOX OIL, Particle counter removal | 2022-05-16 10:24 | Closed | GBXOIL | GBXPARTREM | SANTA RITA EAST | CBILLIG |  | 2022-05-18 15:09
2 | GBX-00006 | 2935724 | CMS Gearbox Borescope | 2022-05-18 16:50 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2022-06-28 12:13
5 | WTG-0004-0000 | 2943378 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-08 14:58 | Closed | CMS | CMSTRBLSHOOT | GORDON BUTTE | CBILLIG |  | 2023-01-24 09:53
5 | WTG-0A04-NDG0-0000 | 2944789 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-13 10:07 | Closed | CMS | CMSTRBLSHOOT | JAYHAWK | CBILLIG |  | 2022-08-08 17:20
5 | WTG-1064-NDG0-0000 | 2947750 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-20 14:51 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-01-27 14:02
5 | WTG-0029A-NDGP-0000 | 2947739 | GEARBOX OIL, Replace oil cooler yellow return hose | 2022-06-20 09:28 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2022-10-31 14:21
1 | WTG-0059-0000 | 2948458 | GEARBOX OIL, Fix oil leak | 2022-06-22 15:31 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH |  | 2022-06-29 07:59
4 | WTG-0060A-0000 | 2950738 | GEARBOX OIL Hose , Replace orange hose | 2022-06-28 12:11 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-09-14 09:35
1 | BRG-000048 | 2965426 | CMS Main Bearing Borescope | 2022-07-22 12:03 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | CBILLIG |  | 2022-08-11 08:29
4 | WTG-0003A-0000 | 2967911 | Secondary filtration system leak | 2022-07-26 13:45 | Closed | GBXOIL | GBXOILCOOL | FORWARD | ALANGKAU |  | 2022-12-19 08:20
1 | GBX-000010 | 2970495 | Gearbox Oil Work/Issue | 2022-08-01 15:21 | Closed | GBXOIL | EM225 | GOLDTHWAITE | JMCDOUGAL |  | 2022-08-05 14:49
5 | WTG-1042-NDB0-0000 | 2972112 | CMS Main Bearing Check | 2022-08-04 10:40 | Cancelled | CMS | CMSMB | TRAVERSE | CBILLIG |  | 2023-01-27 11:09
1 | WTG-0053-F000-0000 | 2988720 | GEARBOX OIL, Fix oil leak | 2022-08-11 16:09 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | AADAMS |  | 2022-09-28 14:15
5 | WTG-00C7-0000 | 2989827 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-15 16:22 | Cancelled | CMS | CMSTRBLSHOOT | COYOTE RIDGE | CBILLIG |  | 2022-08-16 13:37
1 | WTG-3063-0000 | 3064210 | Gearbox Oil Work/Issue | 2023-01-04 15:53 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | CMIXON |  | 2023-02-21 11:10
1 | WTG-0308-NDG0-0000 | 3012924 | GEARBOX OIL, Particle counter installation | 2022-09-07 16:31 | Closed | GBXOIL | GBXPARTINS | BISHOP HILL III | CBILLIG |  | 2022-10-31 09:02
1 | WTG-0089-0000 | 3024600 | GEARBOX , particle counter troubleshoot | 2022-09-21 15:51 | Closed | GBXOIL | GBXPARTTS | MAVERICK | VPHIASIRIPANYO |  | 2022-11-14 09:33
5 | WTG-0071-0000 | 3033101 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-10-11 14:46 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-12-12 15:43
4 | WTG-0056A-0000 | 3033104 | Change GBX Desiccant | 2022-10-11 12:57 | Closed | GBXOIL |  | FORWARD | DMONROE |  | 2023-01-30 11:36
5 | WTG-0016-NDGP-0000 | 3035290 | Top off gear oil (2gals) | 2022-10-14 14:46 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2023-03-27 10:40
9 | WTG-0002-0000 | 3039617 | GEARBOX, Oil Change | 2022-10-31 09:21 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | KWHATLEY |  | 2023-01-03 10:55
9 | WTG-0003-0000 | 3039618 | GEARBOX, Oil Change | 2022-10-31 09:22 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | KWHATLEY |  | 2023-01-27 16:25
9 | WTG-0004-0000 | 3039619 | GEARBOX, Oil Change | 2022-10-31 09:22 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | KWHATLEY |  | 2022-11-21 13:05
9 | WTG-0005-0000 | 3039620 | GEARBOX, Oil Change | 2022-10-31 09:22 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | KWHATLEY |  | 2022-11-30 08:45
1 | WTG-3022-0000 | 3041048 | Gearbox Inspection | 2022-11-02 09:46 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | TPARKER |  | 2023-02-20 12:30
5 | GBX-00020 | 3041728 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-11-03 15:32 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-11-11 09:22
1 | WTG-0232-0000 | 3041738 | GEARBOX OIL, Fix oil leak | 2022-11-03 11:40 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | THOLZ |  | 2023-01-06 10:40
9 | WTG-0084-0000 | 3042476 | GEARBOX, Oil Change | 2022-11-07 11:17 | Closed | GBXOIL | GBXOILCHG | BETHEL | MTERRONES |  | 2023-03-20 12:26
9 | WTG-0119-0000 | 3044568 | GEARBOX, Oil Change | 2022-11-11 10:08 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2022-11-21 13:03
5 | WTG-0219-0000 | 3045196 | GEARBOX OIL, Fix oil leak | 2022-11-14 09:18 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NMCFARLAND |  | 2023-10-23 22:54
9 | WTG-0015-0000 | 3046045 | GEARBOX, Oil Change | 2022-11-16 09:08 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-02-10 06:36
5 | WTG-0021-NDD0-0000 | 3072462 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-26 13:46 | Closed | CMS | CMSTRBLSHOOT | BETHEL | CBILLIG |  | 2023-07-10 14:10
4 | WTG-0058-NDGP-0000 | 3048514 | Replace gear oil pump red spider | 2022-11-18 15:01 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-01-30 11:38
9 | WTG-0052-0000 | 3053762 | GEARBOX, Oil Change | 2022-12-05 12:57 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-04-08 08:53
9 | WTG-0069-0000 | 3054530 | GEARBOX, Oil Change | 2022-12-07 13:46 | Closed | GBXOIL | GBXOILCHG | BETHEL | MRAHMAN |  | 2023-04-21 16:11
9 | WTG-0038-0000 | 3055212 | GEARBOX, Oil Change | 2022-12-09 14:01 | Closed | GBXOIL | GBXOILCHG | BETHEL | TMILLER2 |  | 2022-12-30 12:05
5 | WTG-0A17-NDG0-0000 | 3055218 | GEARBOX OIL, Add/Top-Off | 2022-12-09 14:46 | Closed | GBXOIL | GBXOILADD | BEECH RIDGE | JBENDER |  | 2022-12-13 08:05
2 | WTG-0015-NDG0-0000 | 3056712 | GEARBOX OIL, Particle counter troubleshooting | 2022-12-14 09:42 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-08-28 14:01
2 | WTG-0039-NDG0-0000 | 3056716 | GEARBOX OIL, Particle counter troubleshooting | 2022-12-14 09:48 | Cancelled | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-03-13 11:54
2 | WTG-0042-NDG0-0000 | 3056721 | GEARBOX OIL, Particle counter troubleshooting | 2022-12-14 09:50 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-04-27 15:51
2 | WTG-0058-NDG0-0000 | 3056723 | GEARBOX OIL, Particle counter troubleshooting | 2022-12-14 09:51 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2024-10-10 16:32
2 | WTG-0070-NDG0-0000 | 3056729 | GEARBOX OIL, Particle counter troubleshooting | 2022-12-14 09:53 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-11-29 09:18
2 | WTG-0063-NDG0-0000 | 3056725 | GEARBOX OIL, Particle counter troubleshooting | 2022-12-14 09:51 | Completed Awaiting Review | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-01-09 09:54
2 | WTG-0045-0000 | 3057498 | CMS Inspection | 2022-12-15 12:11 | Closed | CMS | CMSINSP | BLOOMING GROVE | MWILSON |  | 2023-03-28 13:31
5 | GEN-00061 | 3058277 | CMS Generator Bearing Check | 2022-12-19 12:14 | Cancelled | CMS | CMSGENB | UPSTREAM | CBILLIG |  | 2022-12-20 13:58
9 | WTG-0072-0000 | 3063261 | GEARBOX, Oil Change | 2023-01-03 10:29 | Closed | GBXOIL | GBXOILCHG | BETHEL | MRAHMAN |  | 2023-04-21 16:06
2 | 0BJA40GH001GS55 0GBS60AM002 | 3064169 | Fuga de aceite en el reductor del agitador 0GBS60AM002 | 2023-01-04 15:15 | Closed | GBXOIL |  | GUADALUPE | RMORALES |  | 2023-02-09 09:16
2 | WTG-0083-0000 | 3064080 | CMS Main Bearing Borescope | 2023-01-04 13:36 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | BVANVALKENBURG |  | 2023-01-16 06:55
2 | WTG-0083-0000 | 3064083 | CMS Main Bearing Borescope | 2023-01-04 13:39 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | BVANVALKENBURG |  | 2023-01-27 06:29
2 | WTG-2031-0000 | 3066632 | GEARBOX OIL, Oil Sample | 2023-01-10 15:41 | Closed | GBXOIL | GBXOILSAMP | TRAVERSE | WDEAS |  | 2023-01-12 12:01
1 | WTG-0061-0000 | 3067428 | GEARBOX OIL, Fix radiator leak | 2023-01-11 16:33 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | ZNASH |  | 2024-10-09 14:06
1 | WTG-2115-0000 | 3067586 | Gearbox Oil Work/Issue | 2023-01-12 09:13 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | BWALLIS |  | 2023-02-23 14:05
1 | WTG-0324-NDB0-0000 | 3067616 | CMS Main Bearing Borescope | 2023-01-12 10:16 | Closed | CMS | CMSMBBORE | BISHOP HILL III | ABARNDT |  | 2023-04-03 15:32
1 | WTG-2030-0000 | 3067584 | Gearbox Oil Work/Issue | 2023-01-12 09:08 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | BWALLIS |  | 2023-02-23 14:05
2 | WTG-0005-NDB0-0000 | 3069034 | CMS Main Bearing Borescope | 2023-01-17 11:48 | Closed | CMS | CMSMBBORE | GORDON BUTTE | ABARNDT |  | 2023-05-11 12:17
4 | WTG-0096-0000 | 3069017 | Replace Secondary Pump Shaft Seal | 2023-01-17 09:00 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2023-06-09 11:53
2 | WTG-0100-NDD0-0000 | 3072434 | CMS Generator Bearing Check | 2023-01-26 12:36 | Closed | CMS | CMSGENB | BETHEL | JCULLITY |  | 2023-03-20 12:38
2 | WTG-0048-NDD0-0000 | 3072435 | CMS Generator Bearing Check | 2023-01-26 12:36 | Cancelled | CMS | CMSGENB | BETHEL | JCULLITY |  | 2023-01-26 17:03
2 | WTG-0065-NDD0-0000 | 3072432 | CMS Generator Bearing Check | 2023-01-26 11:59 | Closed | CMS | CMSGENB | BETHEL | JCULLITY |  | 2023-01-27 12:55
2 | WTG-0054-NDD0-0000 | 3072433 | CMS Generator Bearing Check | 2023-01-26 12:36 | Cancelled | CMS | CMSGENB | BETHEL | JCULLITY |  | 2023-01-26 17:04
5 | WTG-0102-NDD0-0000 | 3072478 | CMS Generator Bearing Check | 2023-01-26 13:55 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-05-19 09:31
1 | WTG-0017-NDD0-0000 | 3072465 | CMS Generator Bearing Check | 2023-01-26 13:49 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-02-16 16:15
5 | WTG-0050-NDD0-0000 | 3072468 | CMS Generator Bearing Check | 2023-01-26 13:52 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-12-14 07:51
2 | WTG-0057-NDD0-0000 | 3072470 | CMS Generator Bearing Check | 2023-01-26 13:53 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-04-12 17:02
3 | WTG-0067-NDD0-0000 | 3072474 | CMS Generator Bearing Check | 2023-01-26 13:54 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-05-02 14:02
5 | WTG-0081-NDD0-0000 | 3072475 | CMS Generator Bearing Check | 2023-01-26 13:54 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-08-31 16:15
5 | WTG-0087-NDD0-0000 | 3072476 | CMS Generator Bearing Check | 2023-01-26 13:54 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-05-09 15:52
5 | WTG-0098-NDD0-0000 | 3072477 | CMS Generator Bearing Check | 2023-01-26 13:55 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-05-19 14:51
1 | WTG-0024-NDG0-0000 | 3094977 | GEARBOX OIL, Fix oil leak | 2023-03-08 17:41 | Closed | GBXOIL | GBXOILLEAK | BLOOMING GROVE | MWILSON |  | 2023-03-28 11:20
1 | WTG-1010-0000 | 3073368 | GBX Install CCJ 27/27 Secondary Filter and Particle Counter | 2023-01-27 18:25 | Closed | GBXOIL | GBXPARTINS | TRAVERSE | JFRIESEN | 30 | 2023-04-13 14:50
9 | WTG-0039-0000 | 3073247 | GEARBOX, Oil Change | 2023-01-27 10:06 | Closed | GBXOIL | GBXOILCHG | MAVERICK | JEROMAN |  | 2023-07-12 09:20
5 | WTG-0096-NTV0-0000 | 3073245 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-27 10:06 | Closed | CMS | CMSTRBLSHOOT | MAVERICK | ABARNDT |  | 2024-03-05 15:37
1 | WTG-1002-0000 | 3073995 | GEAR BOX LEAK | 2023-01-30 15:43 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | ATHOMPSON |  | 2023-04-13 14:44
1 | WTG-1011-0000 | 3073996 | GEAR BOX LEAK | 2023-01-30 15:52 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | ATHOMPSON |  | 2023-04-13 14:52
2 | WTG-0004-0000 | 3074199 | GEARBOX OIL, Particle counter troubleshooting | 2023-01-31 10:30 | Closed | GBXOIL | GBXPARTTS | STANTON | WDEAS |  | 2023-02-28 16:17
5 | WTG-1100-NTV0-0000 | 3074132 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-31 09:30 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-01-30 13:25
5 | WTG-1117-NTV0-0000 | 3074136 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-31 09:38 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-09-18 11:48
5 | WTG-0044-NTV0-0000 | 3078542 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-02-06 10:02 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | ABARNDT |  | 2023-02-09 15:27
5 | WTG-0044-NDG0-0000 | 3078563 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-02-06 11:05 | Cancelled | CMS | CMSTRBLSHOOT | SUNDANCE | TKORNELE |  | 2023-02-06 17:43
1 | WTG-0075-NDBP-0000 | 3079224 | CMS Main Bearing Borescope | 2023-02-08 09:57 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2023-02-22 09:56
5 | WTG-0062-0000 | 3079997 | Secondary filter is stuck inside the filter pot see comments | 2023-02-09 10:08 | Closed | GBXOIL | GBXFILTELEM | FORWARD | ALANGKAU |  | 2023-10-02 11:50
2 | WTG-0108-NDG0-0000 | 3080003 | CMS Gearbox Borescope | 2023-02-09 13:23 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2023-04-24 09:13
5 | WTG-0088-NDGP-0000 | 3080051 | Gearbox Oil Pump replacement | 2023-02-09 15:16 | Closed | GBXOIL | GBXOILCOOL | DEUEL HARVEST | SKUEHN |  | 2023-03-28 14:55
2 | WTG-0079-NDG0-0000 | 3079967 | CMS Gearbox Borescope | 2023-02-09 11:25 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2023-02-13 11:35
3 | WTG-0099-NDD0-0000 | 3079959 | CMS Generator Bearing Check | 2023-02-09 10:46 | Closed | CMS | CMSGENB | SANTA RITA EAST | ABARNDT |  | 2023-02-16 09:15
3 | WTG-0087-NTV0-0000 | 3085874 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-02-21 11:58 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | ABARNDT |  | 2023-07-27 10:52
2 | WTG-0002-NDD0-0000 | 3081401 | CMS Generator Bearing Check | 2023-02-13 09:57 | Closed | CMS | CMSGENB | GORDON BUTTE | ABARNDT |  | 2023-06-27 09:12
5 | WTG-0011-0000 | 3036069 | Add/top off 5 gallons of oil | 2022-10-18 11:48 | Closed | GBXOIL | GBXOILADD | FORWARD | DMONROE |  | 2023-04-03 16:20
5 | WTG-0036-NDGP-0000 | 3036714 | Tvb valve flip/ replace red spider insert | 2022-10-20 14:07 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2022-10-21 13:29
4.1 | WTG-0097-0000 | 3040975 | GEARBOX OIL, Replace oil pump motor | 2022-11-02 07:07 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCAPEN |  | 2022-11-11 17:46
9 | WTG-0013-0000 | 3041014 | GEARBOX, Oil Change | 2022-11-02 09:14 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2022-11-21 13:06
5 | WTG-0068-0000 | 3048632 | Generator Outboard Bearing Inspection | 2022-11-19 07:53 | Closed | CMS | CMSGENB | MAVERICK | VPHIASIRIPANYO |  | 2023-07-12 10:18
3 | NEL-RIV-PUMP 2 | 3050099 | Imbalance on River Pump #2 | 2022-11-23 18:31 | Rejected | CMS |  | NELSON | LZIMMERMAN |  | 2024-05-22 13:46
4 | WTG-0008-0000 | 3052378 | Replace secondary filter pump shaft seal | 2022-12-01 13:26 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2022-12-19 09:48
2 | WTG-0315-0000 | 3052309 | CMS Main Bearing Borescope | 2022-12-01 10:30 | Closed | CMS | CMSMBBORE | BISHOP HILL III | CBILLIG |  | 2023-01-31 15:07
2 | WTG-0319-NDG0-0000 | 3052342 | CMS Gearbox Borescope | 2022-12-01 12:31 | Cancelled | CMS | CMSGBXBORE | BISHOP HILL III | CBILLIG |  | 2023-02-02 10:07
1 | WTG-0323-NDG0-0000 | 3052345 | CMS Gearbox Borescope | 2022-12-01 12:58 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | CBILLIG |  | 2022-12-06 08:19
2 | WTG-0037-0000 | 3055289 | CMS Gearbox Borescope | 2022-12-10 07:21 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | PHEATON |  | 2022-12-13 08:24
9 | WTG-0039-0000 | 3055213 | GEARBOX, Oil Change | 2022-12-09 14:02 | Closed | GBXOIL | GBXOILCHG | BETHEL | TMILLER2 |  | 2022-12-30 12:07
1 | BRG-000028 | 3059666 | CMS Main Bearing Borescope | 2022-12-22 14:28 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | CBILLIG |  | 2023-02-22 09:53
5 | WTG-0069-0000 | 3061951 | CMS Generator Bearing Check | 2022-12-31 13:08 | Closed | CMS | CMSGENB | GREXP | JCARRETTO |  | 2023-01-20 11:36
9 | WTG-0087-0000 | 3062636 | GEARBOX, Oil Change | 2023-01-03 09:18 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-02-06 16:26
9 | WTG-0088-0000 | 3062637 | GEARBOX, Oil Change | 2023-01-03 09:19 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-05-11 11:05
5 | WTG-0209-NTV0-0000 | 3068793 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-16 13:09 | Cancelled | CMS | CMSTRBLSHOOT | BEECH RIDGE II | ABARNDT |  | 2023-01-16 13:14
5 | GBX-00026 | 3069057 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-17 14:41 | Closed | CMS | CMSTRBLSHOOT | DEUEL HARVEST | CBILLIG |  | 2023-12-11 14:36
5 | WTG-0021-0000 | 3069705 | Generator Bearing Check | 2023-01-18 13:58 | Closed | CMS | CMSGENB | JUDITH GAP | CROBERTS |  | 2023-03-22 11:52
1 | WTG-0070-0000 | 3069757 | GEARBOX OIL, Fix oil leak | 2023-01-18 14:39 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | JBRILEY |  | 2023-02-10 16:17
5 | WTG-0213-NDGP-0000 | 3069763 | Check gearbox drain port for leak-see comment | 2023-01-18 14:57 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2023-09-15 14:45
5 | WTG-0086-NTV0-0000 | 3071073 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-23 10:27 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-01-27 09:30
1 | WTG-0043-0000 | 3073334 | GEARBOX OIL, Particle counter installation | 2023-01-27 15:49 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | BVANVALKENBURG |  | 2023-02-09 14:45
1 | WTG-0006-0000 | 3073339 | GEARBOX OIL, Particle counter installation | 2023-01-27 15:50 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | BVANVALKENBURG |  | 2023-02-09 14:45
5 | WTG-0032-NDD0-0000 | 3078019 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-02-03 13:05 | Closed | CMS | CMSTRBLSHOOT | BETHEL | CBILLIG |  | 2023-03-16 09:09
5 | WTG-0031-NDD0-0000 | 3078015 | CMS Generator Bearing Check | 2023-02-03 12:41 | Closed | CMS | CMSGENB | THUNDERHEAD | CBILLIG |  | 2023-08-11 15:01
2 | WTG-0016-0000 | 3085625 | CMS Gearbox Borescope | 2023-02-20 14:36 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | OLAM |  | 2023-02-21 15:43
5 | WTG-00C9-NDB0-0000 | 3094928 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-08 14:52 | Closed | CMS | CMSTRBLSHOOT | COYOTE RIDGE | CBILLIG |  | 2023-10-04 13:33
5 | WTG-0013-NTV0-0000 | 3084374 | CMS Trouble Shoot (Invenergy request, non-GE) /SR# 6170336 | 2023-02-16 09:44 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2023-04-20 09:09
4 | WTG-0061-0000 | 3084956 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2023-02-17 13:59 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-08-18 12:15
4 | WTG-0046-0000 | 3084946 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2023-02-17 12:29 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-07-20 12:02
1 | WTG-0096-NDB0-0000 | 3088488 | CMS Main Bearing Borescope | 2023-03-01 10:19 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2023-06-06 15:38
5 | WTG-0049-0000 | 3089293 | Replace Yellow GBX Hose | 2023-03-01 15:38 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-03-07 11:41
1 | WTG-0018-NDB0-0000 | 3094778 | CMS Main Bearing Borescope | 2023-03-08 10:59 | Closed | CMS | CMSMBBORE | BETHEL | CBILLIG |  | 2023-04-27 15:31
4 | WTG-0033-0000 | 3095411 | Gearbox Secondary Filter Leak | 2023-03-09 14:54 | Closed | GBXOIL | GBXFILTELEM | FORWARD | DMONROE |  | 2023-04-13 10:41
2 | WTG-0002-0000 | 3101685 | CMS Gearbox Borescope | 2023-03-22 07:46 | Closed | CMS | CMSGBXBORE | MARSH HILL | CSTRZELEC |  | 2023-03-23 10:07
5 | WTG-0080-NTV0-0000 | 3101733 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-22 09:28 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-03-24 09:32
4 | WTG-0035-0000 | 3101850 | GEARBOX OIL, Add 5 Gallons | 2023-03-22 14:16 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-04-03 16:23
2 | WTG-0313-0000 | 3102462 | GEARBOX OIL, Fix oil leak | 2023-03-24 11:36 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | THOLZ |  | 2024-09-13 12:33
1 | WTG-0E11-0000 | 3102532 | GEARBOX OIL, Fix oil leak | 2023-03-24 13:54 | Closed | GBXOIL | GBXOILLEAK | BEECH RIDGE | JCROBERSON |  | 2023-06-20 21:32
1 | WTG-1109-0000 | 3102592 | GEARBOX OIL, Fix oil leak | 2023-03-24 16:19 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | QCROUSE |  | 2023-06-05 11:28
1 | WTG-0054-0000 | 3102542 | GEARBOX OIL, Fix oil leak WC# 6118390 | 2023-03-24 14:48 | Closed | GBXOIL | GBXOILLEAK | THUNDERHEAD | NHEITHOFF |  | 2023-05-15 13:02
2 | WTG-00D2-NDB0-0000 | 3103261 | CMS Main Bearing Borescope | 2023-03-27 14:48 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | CBILLIG |  | 2024-09-13 16:44
1 | WTG-00E1-NDB0-0000 | 3103266 | CMS Main Bearing Borescope | 2023-03-27 15:15 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | CBILLIG |  | 2023-04-18 13:46
5 | WTG-0019A-NDGP-0000 | 3103251 | Replace red spider insert | 2023-03-27 14:22 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2024-10-25 16:56
2 | GBX-00024 | 3106112 | GEARBOX OIL, Particle counter removal | 2023-03-31 10:49 | Closed | GBXOIL | GBXPARTREM | BLOOMING GROVE | CBILLIG |  | 2023-08-17 13:29
2 | GBX-00008 | 3106113 | GEARBOX OIL, Particle counter installation | 2023-03-31 10:51 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | CBILLIG |  | 2023-08-09 11:14
2 | WTG-0097-0000 | 3108193 | CMS Gearbox Borescope | 2023-04-04 10:44 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2023-04-27 10:42
1 | WTG-3002-0000 | 3110174 | GEARBOX OIL, Fix oil leak | 2023-04-07 21:53 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | TPARKER |  | 2023-08-08 12:41
4 | WTG-0039-0000 | 3111810 | GEARBOX OIL Hose, Replace Blue Hose | 2023-04-11 12:56 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-10-13 14:38
1 | WTG-3036-0000 | 3112631 | GEARBOX OIL, Fix oil leak | 2023-04-13 13:08 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | ATHOMPSON |  | 2023-10-16 17:31
3 | WTG-2097-0000 | 3113551 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-17 09:21 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-06-13 11:11
3 | WTG-2109-0000 | 3113555 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-17 09:43 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-06-13 11:03
3 | WTG-2084-0000 | 3113559 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-17 09:55 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-06-13 11:05
1 | WTG-0115-0000 | 3117320 | GEARBOX OIL, Fix oil leak | 2023-04-27 09:01 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | DBMINER |  | 2023-05-09 14:44
3 | WTG-1087-0000 | 3117949 | CMS HSS Check | 2023-04-28 09:26 | Closed | CMS | CMSHSS | TRAVERSE | ABARNDT |  | 2023-06-05 10:36
5 | WTG-1091-0000 | 3118231 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-28 12:12 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ATHOMPSON |  | 2023-06-05 10:40
1 | WTG-0003-0000 | 3120356 | GEARBOX OIL, Fix oil leak | 2023-05-01 20:21 | Closed | GBXOIL | GBXOILLEAK | MAVERICK | AALATORRE |  | 2023-07-07 15:49
1 | WTG-0097-0000 | 3123173 | Oil sample | 2023-05-05 16:32 | Closed | GBXOIL | GBXOILSAMP | MAVERICK | JMILES |  | 2023-07-12 11:00
4 | WTG-0057-0000 | 3126379 | Replace Purple hose | 2023-05-15 13:27 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-06-09 12:45
4 | WTG-0057-0000 | 3126381 | Add/Top off with 5 Gal of Oil | 2023-05-15 13:38 | Closed | GBXOIL | GBXOILADD | FORWARD | DMONROE |  | 2023-06-09 12:45
5 | WTG-0029-NDD0-0000 | 3127041 | CMS Generator Bearing Check | 2023-05-16 12:39 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-07-03 11:24
5 | WTG-0101-0000 | 3127042 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-16 12:46 | Closed | CMS | CMSTRBLSHOOT | BETHEL | CBILLIG |  | 2023-09-19 17:25
2 | WTG-0059-NDG0-0000 | 3127840 | GEARBOX OIL, Secondary filter system not working | 2023-05-18 09:49 | Closed | GBXOIL | GBXFILTELEM | VANTAGE | CCUSACK |  | 2023-11-29 10:16
5 | WTG-0034-0000 | 3129747 | GEARBOX OIL, Replace oil cooler fan motor | 2023-05-19 07:40 | Closed | GBXOIL | GBXOILCOOL | UPSTREAM | RKUDERA |  | 2024-10-17 10:38
5 | WTG-0093-0000 | 3130604 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-22 11:48 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-05-24 15:57
2 | WTG-0020-0000 | 3130547 | CMS Main Bearing Borescope | 2023-05-22 10:40 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-03-26 07:53
5 | WTG-0050-0000 | 3130586 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-22 11:22 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-06-07 10:49
1 | GBX-MOV-J51423 | 3138160 | LOW OIL LEVEL WTG005 | 2023-06-06 09:45 | Closed | GBXOIL |  | BUFFALO MOUNT | VFRENCH |  | 2023-07-07 10:50
5 | WTG-0040A-NDGP-0000 | 3143576 | GEARBOX oil pump coupler replacement | 2023-06-16 10:33 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-07-20 12:10
1 | WTG-0040A-NDGP-0000 | 3143577 | Replace filter bypass hose. Najing | 2023-06-16 12:39 | Ready to Schedule | GBXOIL | GBXOILCOOL | FORWARD | DMONROE
2 | WTG-0048-0000 | 3145440 | CMS Gearbox Borescope | 2023-06-22 10:38 | Closed | CMS | CMSGBXBORE | UPSTREAM | ABARNDT |  | 2023-06-30 10:49
1 | WTG-0206-0000 | 3145511 | GEARBOX OIL, Fix oil leak | 2023-06-22 11:15 | Closed | GBXOIL | GBXOILLEAK | SCEXP | CMUSTAIN |  | 2023-06-26 12:28
2 | WTG-0073-0000 | 3147880 | Main Bearing Inspection | 2023-06-26 10:02 | Closed | CMS | CMSMBBORE | MAVERICK | VPHIASIRIPANYO |  | 2023-07-12 10:37
3 | WTG-1065-0000 | 3148632 | CMS Keyphasor Troubleshoot | 2023-06-27 14:55 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
2 | WTG-0087-0000 | 3148601 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-06-27 13:45 | Closed | CMS | CMSTRBLSHOOT | MAVERICK | ABARNDT |  | 2023-11-09 11:37
3 | WTG-0008-0000 | 3153600 | CMS Generator Bearing Check | 2023-07-06 11:30 | Closed | CMS | CMSGENB | MAVERICK | ABARNDT |  | 2023-07-08 11:54
1 | WTG-0020-0000 | 3149438 | CMS HSS Check | 2023-06-28 15:21 | Closed | CMS | CMSHSS | BETHEL | ABARNDT |  | 2023-07-24 13:01
1 | WTG-0100-0000 | 3155001 | GEARBOX OIL, Secondary filter leak | 2023-07-11 09:03 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | TWIEDEMEIER |  | 2024-07-31 15:34
4.1 | WTG-0090-0000 | 3156541 | OHAIN OIL BUCKET LLC NEEDED | 2023-07-14 10:01 | Closed | GBXOIL | GBXOILLEAK | FORWARD | DMONROE |  | 2024-03-19 15:34
5 | WTG-0009-NDGP-0000 | 3158151 | Replace red spider insert on gear oil pump | 2023-07-19 07:05 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-08-02 10:45
2 | WTG-0053-NDG0-0000 | 3158206 | GEARBOX OIL, Add/Top-Off | 2023-07-19 09:17 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2023-11-14 11:20
2 | WTG-0087-0000 | 3159685 | GEARBOX OIL, Particle counter troubleshooting | 2023-07-21 08:53 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JWWILSON |  | 2024-02-07 11:27
2 | GBX-00092 | 3159686 | GEARBOX OIL, Particle counter troubleshooting | 2023-07-21 08:53 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JWWILSON |  | 2023-07-21 12:50
2 | GBX-00078 | 3159684 | GEARBOX OIL, Particle counter troubleshooting | 2023-07-21 08:52 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JWWILSON |  | 2023-07-25 11:43
4 | WTG-3030-0000 | 3161689 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-07-25 14:02 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-04-02 16:06
4 | WTG-3031-0000 | 3161691 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-07-25 14:06 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-04-02 16:07
3 | WTG-0019-0000 | 3168306 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-08-02 13:28 | Closed | CMS | CMSTRBLSHOOT | BLOOMING GROVE | ABARNDT |  | 2023-08-15 06:29
2 | WTG-0068-0000 | 3175006 | CMS Main Bearing Borescope | 2023-08-16 14:09 | Closed | CMS | CMSMBBORE | MAVERICK | AALATORRE |  | 2023-08-28 15:15
3 | 0BJA40GH001GS54 0GBS60AM001 | 3175790 | Fuga de aceite en el reductor de agitador de tanque de lavado de filtros # 1 | 2023-08-17 14:23 | Closed | GBXOIL |  | GUADALUPE | RMORALES |  | 2024-08-02 16:28
4 | WTG-0090-0000 | 3175816 | Replace lube pump and seals on flange between lube pump and filter pot | 2023-08-17 15:38 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2023-12-15 10:47
2 | WTG-0060-0000 | 3176757 | CMS Gearbox Borescope / SR# 6429276 | 2023-08-21 09:56 | Closed | CMS | CMSGBXBORE | PLYMOUTH | ABARNDT |  | 2023-09-21 12:39
3 | WTG-0026-0000 | 3176864 | CMS Generator Bearing Check | 2023-08-21 13:50 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-10-23 11:05
5 | WTG-0052-NDB0-0000 | 3177458 | CMS Main Bearing Replace/Install | 2023-08-22 14:27 | Closed | CMS | CMSMB | SUNDANCE | TKORNELE |  | 2024-10-07 19:23
5 | WTG-00I2-0000 | 3182520 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-08-31 10:17 | Closed | CMS | CMSTRBLSHOOT | TATANKA RIDGE | ABARNDT |  | 2024-08-29 16:23
5 | WTG-0008-0000 | 3182538 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-08-31 11:22 | Closed | CMS | CMSTRBLSHOOT | BETHEL | ABARNDT |  | 2023-10-30 09:10
1 | WTG-0153-0000 | 3187682 | GEARBOX OIL, Fix oil leak | 2023-09-08 09:01 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | FRAMIREZ |  | 2023-12-04 15:14
4.1 | WTG-0048-0000 | 3187648 | Oil Cooler Shroud Replacement_Blue Vent Tube | 2023-09-08 07:15 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2024-06-10 09:46
3 | WTG-0042-0000 | 3187713 | CMS Generator Bearing Check | 2023-09-08 09:40 | Closed | CMS | CMSGENB | UPSTREAM | ABARNDT |  | 2024-06-05 13:31
5 | WTG-0H05-0000 | 3188444 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-11 10:36 | Closed | CMS | CMSTRBLSHOOT | JAYHAWK | ABARNDT |  | 2023-10-18 11:08
1 | WTG-0214-NDB0-0000 | 3083678 | CMS Main Bearing Borescope | 2023-02-14 09:35 | Closed | CMS | CMSMBBORE | BEECH RIDGE II | ABARNDT |  | 2023-02-22 09:06
1 | WTG-1136-0000 | 3084163 | Gearbox leak | 2023-02-15 13:04 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | ATHOMPSON |  | 2023-06-05 12:10
2 | GEN-000004 | 3086228 | Field Service Labor - Generator Bearing Replacement | 2023-02-22 09:26 | Closed | CMS | FSO-MC-LABOR-2 | STANTON | JBYNUM |  | 2023-02-22 09:35
2 | GEN-000046 | 3086234 | Field Service Labor - Generator Bearing Replacement | 2023-02-22 09:29 | Closed | CMS | FSO-MC-LABOR-2 | STANTON | JBYNUM |  | 2023-02-22 09:36
5 | WTG-0026-0000 | 3090604 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2023-03-02 12:28 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-04-13 10:37
2 | WTG-0241-0000 | 3093210 | GEARBOX OIL, Fix oil leak | 2023-03-04 17:17 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | THOLZ |  | 2023-10-23 22:46
2 | WTG-0088-NDG0-0000 | 3094683 | GEARBOX OIL, Particle counter installation | 2023-03-08 10:26 | Closed | GBXOIL | GBXPARTINS | MAVERICK | CBILLIG |  | 2023-07-12 10:50
3 | WTG-0202-NTV0-0000 | 3097502 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-14 09:25 | Closed | CMS | CMSTRBLSHOOT | BEECH RIDGE II | ABARNDT |  | 2023-03-21 09:10
4 | WTG-0021-0000 | 3099722 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-03-16 13:39 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-09-13 15:06
2 | WTG-1018-0000 | 3103441 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-28 09:26 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-06-13 09:17
1 | WTG-0041-0000 | 3108178 | CMS Gearbox Borescope | 2023-04-04 09:57 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2023-04-14 09:52
5 | WTG-0315-0000 | 3114191 | Oily pitch slip ring | 2023-04-18 14:51 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | THOLZ |  | 2024-01-25 10:23
4.2 | WTG-0004-NDG0-0000 | 3116734 | Empty Ohain Oil Bucket | 2023-04-26 07:06 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN
1 | WTG-0014-0000 | 3132094 | Poseidon inspection | 2023-05-24 12:15 | Closed | GBXOIL | GBXPARTTS | MAVERICK | MWEBER |  | 2023-07-08 11:23
4 | WTG-0210A-NDGP-0000 | 3133215 | Replace red spider gear | 2023-05-26 14:30 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-07-20 12:15
2 | WTG-0025-NDB0-0000 | 3133989 | CMS Main Bearing Borescope | 2023-05-30 11:10 | Closed | CMS | CMSMBBORE | BETHEL | CBILLIG |  | 2023-05-31 14:44
2 | WTG-0057-NDG0-0000 | 3142104 | GEARBOX OIL, look for oil leak | 2023-06-12 11:22 | Closed | GBXOIL | GBXOILLEAK | SUNDANCE | WDEAS |  | 2024-02-23 10:50
2 | WTG-1056-0000 | 3148703 | CMS Gearbox Borescope | 2023-06-27 16:37 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2023-08-08 09:37
1 | WTG-0022-0000 | 3152452 | CMS Main Bearing Borescope | 2023-07-05 10:54 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2023-08-15 10:42
2 | WTG-0095-NDGP-0000 | 3155770 | GEARBOX OIL pump, replace red spider coupling | 2023-07-12 09:40 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-07-17 14:29
2 | GBX-00071 | 3159682 | GEARBOX OIL, Particle counter troubleshooting | 2023-07-21 08:51 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JWWILSON |  | 2023-07-25 11:44
2 | GBX-00082 | 3159683 | GEARBOX OIL, Particle counter troubleshooting | 2023-07-21 08:51 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | JWWILSON |  | 2023-07-25 11:43
3 | WTG-0048-0000 | 3164225 | CMS Generator Bearing Check | 2023-07-31 13:53 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-11-22 09:53
2 | WTG-0004-0000 | 3177444 | CMS Main Bearing Borescope | 2023-08-22 09:21 | Closed | CMS | CMSMBBORE | THUNDERHEAD | AKERKMAN |  | 2023-08-25 11:17
2 | WTG-0006-0000 | 3183251 | GEARBOX OIL, Add/Top-Off | 2023-09-01 11:57 | Closed | GBXOIL | GBXOILADD | GORDON BUTTE | TWIEDEMEIER |  | 2023-12-01 14:41
5 | WTG-2037-0000 | 3193999 | CMS Gearbox Borescope | 2023-09-20 08:24 | Closed | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT |  | 2023-09-27 17:30
3 | WTG-0067-0000 | 3196350 | CMS Generator Bearing Check | 2023-09-25 10:21 | Closed | CMS | CMSGENB | SUNDANCE | ABARNDT |  | 2023-10-09 09:12
5 | WTG-1014-0000 | 3197119 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-26 11:18 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-01-08 11:20
3 | WTG-1009-0000 | 3197129 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-26 11:41 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-01-30 13:24
3 | WTG-1053-0000 | 3197123 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-26 11:25 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-11-06 12:42
3 | WTG-1035-0000 | 3197130 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-26 11:44 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-09-20 11:53
2 | WTG-0108-0000 | 3197848 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-27 15:39 | Closed | CMS | CMSTRBLSHOOT | BETHEL | ABARNDT |  | 2025-04-28 15:31
5 | WTG-0050-0000 | 3198514 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-29 10:27 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2024-01-22 07:49
9 | GBX-000096 | 3199905 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
1 | GBX-HAN-EH802C-004/LM0003 | 3186827 | WTG-011 LOW OIL LEVEL | 2023-09-06 10:11 | Closed | GBXOIL |  | BUFFALO MOUNT | VFRENCH |  | 2023-12-29 18:52
4 | WTG-0043-0000 | 3194110 | GEARBOX OIL, Particle counter troubleshooting | 2023-09-20 12:17 | Closed | GBXOIL | GBXPARTTS | BLOOMING GROVE | ABARNDT |  | 2024-03-21 11:45
2 | WTG-0074-0000 | 3194028 | CMS Main Bearing Borescope | 2023-09-20 09:35 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | ABARNDT |  | 2023-10-19 09:11
4 | WTG-0019-0000 | 3194130 | GEARBOX OIL, Particle counter troubleshooting | 2023-09-20 12:34 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | ABARNDT |  | 2024-01-29 13:47
4 | WTG-0059-0000 | 3194127 | GEARBOX OIL, Particle counter troubleshooting | 2023-09-20 12:27 | Closed | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT |  | 2024-10-22 09:29
3 | WTG-1078-0000 | 3197131 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-09-26 11:47 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-11-11 10:43
9 | GBX-000078 | 3199898 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000079 | 3199899 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000087 | 3199900 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000091 | 3199901 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000092 | 3199902 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000093 | 3199903 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000095 | 3199904 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000099 | 3199906 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000100 | 3199907 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000104 | 3199911 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000101 | 3199908 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000102 | 3199909 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000103 | 3199910 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000105 | 3199912 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000106 | 3199913 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000107 | 3199914 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000108 | 3199915 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000109 | 3199916 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000110 | 3199917 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000115 | 3199921 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000111 | 3199918 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000112 | 3199919 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000114 | 3199920 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000116 | 3199922 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000118 | 3199923 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000120 | 3199924 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000121 | 3199925 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000124 | 3199926 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000125 | 3199927 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000134 | 3199931 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000126 | 3199928 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000128 | 3199929 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000129 | 3199930 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000135 | 3199932 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000137 | 3199933 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000140 | 3199934 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000142 | 3199935 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000143 | 3199936 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000145 | 3199937 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | WTG-0098-NDG0-0000 | 3199941 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000146 | 3199938 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000147 | 3199939 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | WTG-0080-NDG0-0000 | 3199940 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000040 | 3199872 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000044 | 3199876 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000041 | 3199873 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000042 | 3199874 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000043 | 3199875 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000046 | 3199877 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000047 | 3199878 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000049 | 3199879 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000050 | 3199880 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000052 | 3199881 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000053 | 3199882 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000005 | 3199852 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000002 | 3199849 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000003 | 3199850 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000004 | 3199851 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000009 | 3199853 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000010 | 3199854 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000012 | 3199855 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000013 | 3199856 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000014 | 3199857 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000016 | 3199858 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000017 | 3199859 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
3 | WTG-0237-0000 | 3200110 | GEARBOX OIL, Fix oil leak, Radiator | 2023-10-02 16:05 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | RKUDERA |  | 2023-12-28 10:36
1 | WTG-1128-0000 | 3202911 | GEARBOX OIL, Fix oil leak | 2023-10-06 09:22 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | ATHOMPSON |  | 2024-09-16 07:18
1 | WTG-0040-0000 | 3225131 | GEARBOX OIL, Replace oil cooler | 2023-11-13 09:48 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | TWIEDEMEIER |  | 2023-11-14 13:53
9 | WTG-0082-0000 | 1282717 | Radiator Cooler Oil Leak Found - Nanjing | 2016-06-17 08:21 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | KIRBY |  | 2017-11-20 14:37
2 | WTG-0038-0000 | 3200607 | CMS Gearbox Borescope | 2023-10-03 12:59 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | CMORRISON |  | 2024-09-11 14:27
5 | WTG-0001-0000 | 3200902 | Main bearing check | 2023-10-03 13:17 | Closed | CMS | CMSMB | MAVERICK | MWEBER |  | 2024-02-12 08:01
1 | WTG-0108-0000 | 3201449 | GEARBOX OIL, Fix leaking hose under pump | 2023-10-03 16:09 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | BPOPE |  | 2024-02-07 11:18
5 | WTG-0226-0000 | 3202796 | Gbx hose needs replaced | 2023-10-05 13:33 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | THOLZ |  | 2024-08-15 12:29
1 | WTG-1122-0000 | 3202909 | GEARBOX OIL, Fix oil leak | 2023-10-06 09:19 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | ATHOMPSON |  | 2024-03-27 08:56
1 | WTG-0017-0000 | 3207086 | GEARBOX OIL, Oil Sample | 2023-10-13 15:46 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | DKEETON |  | 2023-10-15 18:55
3 | WTG-00L6-0000 | 3208045 | CMS Generator Bearing Check | 2023-10-17 09:20 | Closed | CMS | CMSGENB | TATANKA RIDGE | ABARNDT |  | 2024-09-16 14:12
4 | WTG-0037-0000 | 3208813 | Secondary Oil Leak | 2023-10-19 07:55 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2024-05-08 14:47
5 | WTG-0014-NDD0-0000 | 3211993 | CMS Generator Bearing Check | 2023-10-25 07:39 | Closed | CMS | CMSGENB | GRAND RIDGE | JSENICA |  | 2024-04-18 12:07
2 | WTG-0025-0000 | 3221464 | CMS Gearbox Borescope | 2023-11-08 07:51 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | BSMITH |  | 2024-02-19 09:51
3 | WTG-2030-0000 | 3223562 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-09 13:19 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-12-05 08:30
3 | WTG-2049-0000 | 3223563 | Tracking Pulse Point Notifications | 2023-11-09 13:22 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-03-26 12:54
4 | WTG-0070-0000 | 3224184 | Secondary filter pump leaking at shaft seal | 2023-11-10 11:57 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2024-03-19 15:34
4 | WTG-0070-0000 | 3224185 | GEARBOX OIL, Add/Top-Off about 3 gallons | 2023-11-10 11:58 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-03-19 15:34
4.2 | WTG-0037-NDG0-0000 | 1114209 | Pre-Gearbox Oil Change Detergent Add | 2015-03-30 12:27 | Closed | GBXOIL |  | WILLOW CREEK | FSANTIAGO |  | 2015-04-13 08:33
1 | WTG-0135-0000 | 1658037 | GEARBOX OIL, Fix oil leak | 2017-01-10 10:28 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | RHAGHNAZARIAN |  | 2017-01-12 10:53
1 | WTG-0014-0000 | 1344038 | Install secondary filtration system on gearbox oil | 2016-07-12 09:34 | Closed | GBXOIL | GBXFILTINS | WOLVERINE CREEK | DSTEO | 1 | 2016-07-25 14:13
2 | WTG-0002C-NDGP-0000 | 1582819 | Bad Bearings in Oil Pump Motor - Needs Replaced | 2016-10-07 10:04 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KDRAKE |  | 2016-10-11 10:41
4.2 | WTG-0037-NDG0-0000 | 1668740 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:16 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-05-04 10:58
4.2 | WTG-0034-NDG0-0000 | 1668741 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:17 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-04-29 12:18
4.2 | WTG-0033-NDG0-0000 | 1668743 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:18 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-04-21 21:49
4.2 | WTG-0031-NDG0-0000 | 1668745 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:18 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-04-20 10:49
4 | WTG-0070-NDGP-0000 | 1601473 | WTG 0070 gearbox radiator has small leak | 2016-11-10 15:13 | Closed | GBXOIL | GBXOILCOOL | TURKEY TRACK | JBRILEY |  | 2017-03-22 06:57
1 | WTG-0043-NDGP-0000 | 1259537 | Winergy Gearbox Oil Pump and Motor Inversion Kit | 2016-04-04 14:04 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MMCCABE |  | 2016-04-06 14:51
1 | WTG-0042-0000 | 1650645 | GEARBOX OIL, Fix oil leak | 2017-01-02 16:28 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CWERNER |  | 2017-01-09 16:13
1 | WTG-0107-NDGP-0000 | 1656903 | Radiator leaking | 2017-01-09 15:45 | Closed | GBXOIL | GBXOILCOOL | GREXP | GRAND RIDGE |  | 2017-07-03 10:30
1 | WTG-0111-0000 | 1656915 | GEARBOX OIL, Fix oil leak | 2017-01-09 18:13 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE2 |  | 2019-02-08 18:13
4.2 | WTG-0060-NDGP-0000 | 1662521 | Oil Cooler Leak | 2017-01-25 08:15 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2017-02-17 06:58
4 | WTG-0203B-NDGP-0000 | 1268866 | GEARBOX OIL, Replace oil cooler pump | 2016-05-03 10:52 | Closed | GBXOIL | GBXOILCOOL | FORWARD | IFRANCISCO |  | 2016-05-05 09:36
4 | WTG-0048-NDG0-0000 | 1586224 | GEARBOX OIL, Add/Top-Off | 2016-10-12 07:43 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2016-10-20 11:02
5 | WTG-0012-0000 | 1270508 | GEARBOX OIL, Oil Sample | 2016-05-10 10:37 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-28 08:35
5 | WTG-0013-0000 | 1270509 | GEARBOX OIL, Oil Sample | 2016-05-10 10:40 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-03 14:44
5 | WTG-0021-0000 | 1270510 | GEARBOX OIL, Oil Sample | 2016-05-10 10:42 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-03 14:46
5 | WTG-0022-0000 | 1270511 | GEARBOX OIL, Oil Sample | 2016-05-10 10:42 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-03 14:47
5 | WTG-0023-0000 | 1270512 | GEARBOX OIL, Oil Sample | 2016-05-10 10:43 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-03 14:49
5 | WTG-0042-0000 | 1270513 | GEARBOX OIL, Oil Sample | 2016-05-10 10:44 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-03 14:54
5 | WTG-0019-0000 | 1270514 | GEARBOX OIL, Oil Sample | 2016-05-10 10:44 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-28 08:35
5 | WTG-0059-0000 | 1270515 | GEARBOX OIL, Oil Sample | 2016-05-10 10:45 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-28 08:35
2 | WTG-0012-NDGP-0000 | 1272969 | GEARBOX OIL, Fix oil leak on oil pump | 2016-05-18 10:00 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ACASPER |  | 2016-05-23 09:21
1 | WTG-0025-NDGP-0000 | 1274731 | GEARBOX OIL, Oil Sample | 2016-05-25 10:18 | Closed | GBXOIL | GBXOILSAMP | MCADOO | MSNOW |  | 2016-05-31 10:51
4 | WTG-0057-NDGP-0000 | 1274703 | GEARBOX OIL, Replace oil cooler fan/motor/pump(pump was relpace 4/13/16) | 2016-05-25 06:46 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-10-25 09:05
1 | WTG-0082-0000 | 1658185 | GEARBOX OIL, Fix oil leak | 2017-01-12 17:43 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-13 12:57
1 | WTG-0105-0000 | 1401572 | Gearbox Oil Work/Issue | 2016-08-12 18:33 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | TSHARP |  | 2016-10-06 10:44
1 | WTG-0022-NDGP-0000 | 1401594 | GEARBOX OIL, Fix oil leak | 2016-08-13 10:34 | Closed | GBXOIL | GBXOILLEAK | GUNSIGHT | JELLIS |  | 2016-08-17 14:26
4.2 | WTG-0018-0000 | 1401349 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:27 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:55
4.2 | WTG-0045-0000 | 1401390 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:34 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:45
4.2 | WTG-0059-0000 | 1401420 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:37 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-27 18:46
4.2 | WTG-0003-0000 | 1401321 | gearbox oil sample and Post oil change Oil sample | 2016-08-12 14:22 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-17 15:40
4.2 | WTG-0004-0000 | 1401322 | gearbox oil sample and Post oil change Oil sample | 2016-08-12 14:22 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-17 15:43
4.2 | WTG-0005-0000 | 1401323 | gearbox oil sample and Post oil change Oil sample | 2016-08-12 14:23 | Cancelled | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-08-17 15:53
4.2 | WTG-0044-0000 | 1401387 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:34 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-12 12:44
4.2 | WTG-0047-0000 | 1401398 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:35 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:31
4.2 | WTG-0048-0000 | 1401399 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:35 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:29
4.2 | WTG-0049-0000 | 1401400 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:35 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:29
4.2 | WTG-0053-0000 | 1401409 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:36 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:39
4.2 | WTG-0054-0000 | 1401410 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:36 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:38
4.2 | WTG-0055-0000 | 1401413 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:36 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-27 18:49
4.2 | WTG-0056-0000 | 1401414 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:36 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:37
4.2 | WTG-0057-0000 | 1401417 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:37 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-27 18:49
4.2 | WTG-0058-0000 | 1401418 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:37 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-21 20:36
4.2 | WTG-0050-0000 | 1401404 | gearbox oil change and Post oil change Oil sample | 2016-08-12 14:35 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | CMORRIS |  | 2016-09-29 16:27
2 | WTG-0119-NDG0-0000 | 1599483 | GEARBOX OIL, Particle counter installation | 2016-11-03 10:18 | Closed | GBXOIL | GBXPARTINS | GREXP | SCLARK |  | 2016-12-22 08:53
4.2 | WTG-0057-NDGP-0000 | 1661281 | Oil Cooler Leak | 2017-01-23 10:03 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2017-02-08 07:06
9 | WTG-0089-0000 | 1188564 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:17 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
9 | WTG-0017-0000 | 1188565 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:19 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:46
9 | WTG-0036-0000 | 1188567 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:22 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:46
9 | WTG-0037-0000 | 1188568 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:24 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:46
9 | WTG-0076-0000 | 1188573 | GEARBOX OIL, Secondary filter system installation | 2015-10-03 09:32 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | CWADE |  | 2015-10-10 17:47
1 | WTG-0032-NDGP-0000 | 1205868 | GEARBOX OIL, Fix oil leak/ Replace Filter Housing | 2015-11-16 19:06 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | JGILLILAN |  | 2015-11-23 17:09
2 | WTG-0032-NDG0-0000 | 1205870 | GEARBOX OIL, Add/Top-Off- Needs 10 to 15 Gallons | 2015-11-16 19:20 | Closed | GBXOIL | GBXOILADD | PRAIRIE BREEZE | JGILLILAN |  | 2015-12-15 16:18
4.2 | WTG-0029-NDG0-0000 | 1114203 | Pre-Gearbox Oil Change Detergent Add | 2015-03-30 12:27 | Closed | GBXOIL |  | WILLOW CREEK | FSANTIAGO |  | 2015-04-13 08:33
4.2 | WTG-0030-NDG0-0000 | 1114204 | Pre-Gearbox Oil Change Detergent Add | 2015-03-30 12:27 | Closed | GBXOIL |  | WILLOW CREEK | FSANTIAGO |  | 2015-04-13 08:33
4.2 | WTG-0031-NDG0-0000 | 1114205 | Pre-Gearbox Oil Change Detergent Add | 2015-03-30 12:27 | Closed | GBXOIL |  | WILLOW CREEK | FSANTIAGO |  | 2015-04-13 08:33
4.2 | WTG-0032-NDG0-0000 | 1114206 | Pre-Gearbox Oil Change Detergent Add | 2015-03-30 12:27 | Closed | GBXOIL |  | WILLOW CREEK | FSANTIAGO |  | 2015-04-13 08:33
4.2 | WTG-0033-NDG0-0000 | 1114207 | Pre-Gearbox Oil Change Detergent Add | 2015-03-30 12:27 | Closed | GBXOIL |  | WILLOW CREEK | FSANTIAGO |  | 2015-04-13 08:33
4.2 | WTG-0036-NDG0-0000 | 1114208 | Pre-Gearbox Oil Change Detergent Add | 2015-03-30 12:27 | Closed | GBXOIL |  | WILLOW CREEK | FSANTIAGO |  | 2015-04-13 08:33
1 | WTG-0044-0000 | 1402300 | gearbox oil change and post oil change oil sample | 2016-08-16 19:06 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | BTAFT |  | 2016-08-17 14:04
1 | WTG-0036-NDGP-0000 | 1160556 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2015-07-10 08:37 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JBARRETT |  | 2015-07-14 08:25
9 | WTG-0043-0000 | 1187149 | Radiator Cooler Oil Leak Found - Nanjing | 2015-10-02 08:28 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2021-08-25 07:53
4.2 | WTG-0061-NDGP-0000 | 1282037 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-06-14 07:30 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GBOTT |  | 2016-09-28 07:12
1 | WTG-0115-0000 | 1571086 | GEARBOX OIL, Fix oil leak | 2016-09-29 10:43 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2016-11-03 15:55
1 | WTG-0086-0000 | 1580859 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-10-04 20:55 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | JHAVENS |  | 2016-10-05 10:14
2 | WTG-0106-0000 | 1599716 | GEARBOX OIL, Fix oil leak | 2016-11-03 13:59 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2017-06-29 15:55
4 | WTG-0107-NDG0-0000 | 1589485 | Add 5 gallons of oil | 2016-10-19 11:22 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2016-10-20 11:25
1 | WTG-0039-NDGP-0000 | 1608002 | Install secondary filtration system on gearbox oil | 2016-11-23 12:24 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2016-11-23 12:57
1 | WTG-0046-NDGP-0000 | 1614735 | Gearbox Oil Work/Issue leaking cooler | 2016-12-01 07:18 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | GRAND RIDGE |  | 2018-04-23 08:49
2 | WTG-0094-NDG0-0000 | 1632511 | GEARBOX OIL, Add/Top-Off | 2016-12-07 15:58 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2016-12-08 07:27
1 | WTG-0048-0000 | 1644083 | Gearbox oil pump coupler needs replaced | 2016-12-16 12:55 | Closed | GBXOIL | GBXOILCOOL | CAL RIDGE | DLANGDON |  | 2017-02-13 18:12
5 | WTG-0010-0000 | 1657077 | Pitch drive oil leak-Axis1,2 | 2017-01-10 17:58 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE2 |  | 2017-04-03 16:23
4.2 | WTG-0029-NDG0-0000 | 1668747 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:18 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-04-17 14:28
4.2 | WTG-0026-NDG0-0000 | 1668752 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:19 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-04-06 11:00
4.2 | WTG-0025-NDG0-0000 | 1668754 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:20 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-04-12 09:34
4.2 | WTG-0024-NDG0-0000 | 1668756 | GEARBOX OIL, Add/Top-Off | 2017-02-02 15:20 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | AMARTORANA |  | 2017-04-11 07:49
2 | WTG-0023-NDGP-0000 | 1259978 | Oil Pump Inversion | 2016-04-06 09:50 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | DSTEO |  | 2016-08-04 06:06
9 | WTG-043E-0000 | 1602036 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-11-14 08:52 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS | 30 | 2016-12-28 13:44
9 | WTG-0071-0000 | 1602032 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-11-14 08:46 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS | 30 | 2017-01-03 13:29
1 | WTG-0057-NDGP-0000 | 1267380 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 09:34 | Closed | GBXOIL | GBXFILTELEM | GRAND RIDGE | MSNOW |  | 2017-12-08 11:29
1 | WTG-0003-NDGP-0000 | 1267392 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 08:36 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | MSNOW |  | 2016-06-02 13:41
1 | WTG-0009-NDGP-0000 | 1267394 | GEARBOX OIL, Secondary filter system element change | 2016-05-02 08:38 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | MSNOW |  | 2016-06-07 15:32
1 | WTG-043E-0000 | 1269038 | Gearbox Suctoin hose cracked and needs replaced | 2016-05-03 22:13 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2016-05-06 19:41
5 | WTG-0065-0000 | 1270522 | GEARBOX OIL, Oil Sample | 2016-05-10 10:52 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-28 08:35
5 | WTG-0068-0000 | 1270523 | GEARBOX OIL, Oil Sample | 2016-05-10 10:53 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | NFALASZ |  | 2016-06-28 08:35
4.2 | WTG-0003-NDG0-0000 | 1669002 | GEARBOX OIL, Add/Top-Off | 2017-02-03 09:00 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-02-20 07:26
4.2 | WTG-0009-NDG0-0000 | 1669003 | GEARBOX OIL, Add/Top-Off | 2017-02-03 09:01 | Closed | GBXOIL | GBXOILADD | WOLVERINE CREEK | DSTEO |  | 2017-03-15 13:31
4 | WTG-0095-NDGP-0000 | 1274983 | Replace Leaking Oil Pump | 2016-05-26 06:47 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-05-26 11:36
4.2 | WTG-0098-NDGP-0000 | 1274844 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-05-25 14:47 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-05-25 15:21
1 | WTG-0045-0000 | 1231661 | GEARBOX OIL, Oil Sample | 2016-01-19 08:20 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | KCOOPER |  | 2016-01-22 10:37
1 | WTG-0029-NDGP-0000 | 1586812 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-10-14 10:40 | Closed | GBXOIL | GBXOILCOOL | TURKEY TRACK | SGRIFFIN |  | 2016-10-21 09:32
1 | WTG-0092-NDG0-0000 | 1001473 | Pre-Gearbox Oil Change Detergent Add | 2014-05-08 15:50 | Closed | GBXOIL | GBXOILSAMP | GREXP | R5 |  | 2015-03-24 06:49
2 | WTG-0098-0000 | 1280830 | GEARBOX OIL, Add/Top-Off | 2016-06-07 16:49 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | ATRYON |  | 2016-06-08 07:40
1 | WTG-0020-NDGP-0000 | 1256159 | Oil Pump Inversion | 2016-03-31 12:14 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | ZMUELLER |  | 2016-04-04 08:11
1 | WTG-0009-0000 | 1402297 | gearbox oil change and post oil change oil sample | 2016-08-16 18:58 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | BTAFT |  | 2016-08-17 14:13
1 | WTG-0010-0000 | 1402298 | gearbox oil change and post oil change oil sample | 2016-08-16 19:01 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | BTAFT |  | 2016-08-17 14:20
1 | WTG-0006-0000 | 1402299 | gearbox oil change and post oil change oil sample | 2016-08-16 19:03 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | BTAFT |  | 2016-08-17 14:05
4 | WTG-0120-N000-0000 | 1273615 | GEARBOX OIL, Replace oil cooler pump part #4841 with part #3936 | 2016-05-23 13:04 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GBOTT |  | 2016-07-19 07:48
2 | WTG-0103-NDGP-0000 | 1107223 | Change Jensen System Filter | 2015-03-11 14:30 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE | CBORER |  | 2015-08-07 14:32
2 | WTG-0104-NDGP-0000 | 1107224 | Change Jensen System Filter | 2015-03-11 14:30 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE | CBORER |  | 2015-08-07 14:32
2 | WTG-0047-NDG0-0000 | 1123877 | GEARBOX OIL, Add 3-5 Gallons of Oil | 2015-04-14 07:02 | Closed | GBXOIL | GBXOILLEAK | FORWARD | NZIRBEL |  | 2015-05-13 15:18
9 | WTG-0063-0000 | 1670720 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2017-02-09 08:07 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA | 30 | 2017-04-07 16:03
1 | RSW1 | 1269959 | Abnormal Gearbox Oil Test Results | 2016-05-06 13:18 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | AMAXWELL |  | 2016-07-15 07:56
2 | WTG-0102-NDGP-0000 | 1241705 | GEARBOX OIL, Particle counter installation | 2016-02-10 15:30 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2016-02-16 13:06
2 | WTG-0103-NDGP-0000 | 1241706 | GEARBOX OIL, Particle counter installation | 2016-02-10 15:30 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2016-02-16 19:16
2 | WTG-0020-NDGP-0000 | 1241707 | GEARBOX OIL, Particle counter installation | 2016-02-10 15:31 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2016-03-08 15:34
4 | WTG-0032-NDGP-0000 | 1272523 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 13:51 | Closed | GBXOIL | GBXFILTELEM | WOLVERINE CREEK | RJOHNSON |  | 2018-08-06 08:55
1 | WTG-0029-NDGP-0000 | 1272524 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 13:51 | Closed | GBXOIL | GBXFILTELEM | SPRING CANYON | RJOHNSON |  | 2023-07-31 11:28
3 | WTG-0042-NDGP-0000 | 1272539 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | FORWARD | RJOHNSON |  | 2018-03-16 16:16
3 | WTG-0013-NDGP-0000 | 1272540 | GEARBOX OIL, Secondary filter system element change | 2016-05-16 14:51 | Closed | GBXOIL | GBXFILTELEM | FORWARD | RJOHNSON |  | 2018-03-02 16:08
1 | WTG-0174-NDGP-0000 | 1245778 | GEARBOX OIL, Oil Sample | 2016-02-26 11:07 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS II | JSULLIVAN |  | 2016-02-29 08:19
1 | GBX-000073 | 1245779 | GEARBOX OIL, Oil Sample | 2016-02-26 11:19 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS II | NGINKINGER |  | 2016-02-29 08:17
9 | WTG-0095-NDGP-0000 | 1275058 | Replace GBX Lube Pump Motor | 2016-05-26 08:24 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-03-31 13:41
1 | WTG-0017-0000 | 1275205 | GEARBOX OIL, Oil Sample | 2016-05-26 17:03 | Closed | GBXOIL | GBXOILSAMP | MIAMI 1 | KYARNOLD |  | 2016-05-27 07:20
2 | WTG-0026-NDGP-0000 | 1426526 | Oil Pump Inversion | 2016-09-09 08:18 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | RBEBOUT |  | 2016-09-12 08:40
2 | WTG-0031-NDGP-0000 | 1343137 | GEARBOX OIL PARTICLE COUNTER INSTALLATION | 2016-07-08 09:10 | Closed | GBXOIL | GBXPARTINS | WOLVERINE CREEK | DSTEO |  | 2016-12-14 16:35
1 | WTG-0106-NDGP-0000 | 1356706 | GEARBOX Mag Sweep and Oil Sample | 2016-08-02 08:50 | Closed | GBXOIL | GBXOILSAMP | SCEXP | DWEINGARDT |  | 2016-08-03 18:02
1 | WTG-0059-0000 | 1402780 | Gearbox leak - inspect on next climb | 2016-08-19 07:44 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | CAL RIDGE |  | 2017-02-06 22:02
4 | WTG-0203B-NDGP-0000 | 1487371 | GEARBOX OIL, Fix oil leak(Continued clean-up from previous leak) | 2016-09-14 17:16 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2016-10-05 14:39
1 | WTG-0099-0000 | 1342033 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-07-06 08:05 | Closed | GBXOIL | GBXOILCOOL | CAL RIDGE | JLAPPIN |  | 2016-08-31 08:06
4 | WTG-0098-NDGP-0000 | 1233411 | GEARBOX OIL, Replace oil pump | 2016-01-26 16:18 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2016-02-01 13:14
1 | WTG-0111-NDGP-0000 | 1664850 | Gearbox Oil Work/Issue | 2017-01-30 15:20 | Closed | GBXOIL | EM52 | RONCEVAUX | OGALLANT |  | 2017-01-30 16:18
1 | WTG-0097-NDG0-0000 | 1664853 | EM: Gearbox oil level too low alarm | 2017-01-30 15:18 | Closed | GBXOIL | EM425 | RONCEVAUX | MGILLIS |  | 2017-02-24 10:45
9 | GBX-00043E | 1281140 | Radiator Oil Cooler Leak - Nanjing | 2016-06-09 09:20 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2016-07-15 15:53
1 | WTG-0204-NDG0-0000 | 1547690 | GEARBOX OIL, Fix oil leak | 2016-09-21 18:05 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE |  | 2018-03-08 15:47
1 | WTG-0017-NDG0-0000 | 1237478 | GEARBOX OIL, Fix oil leak | 2016-02-02 09:27 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CHADDIX |  | 2016-09-07 16:29
1 | WTG-0108-0000 | 1659500 | GEARBOX OIL, Fix oil leak | 2017-01-13 17:18 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2019-04-09 11:16
3 | WTG-0002-NDGP-0000 | 1607239 | Install Winergy Oil Pump Inversion Kit | 2016-11-22 06:28 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MMCCABE |  | 2016-11-23 12:40
4 | WTG-0029A-NDGP-0000 | 1600182 | Oil leaking between pump and filter housings | 2016-11-04 15:44 | Closed | GBXOIL |  | FORWARD | FORWARD |  | 2016-11-07 10:16
2 | WTG-0064-NDGP-0000 | 1600021 | WTG 0064 gearbox radiator has small leak | 2016-11-04 10:08 | Closed | GBXOIL | GBXOILCOOL | TURKEY TRACK | MGROTJAN |  | 2017-03-03 09:29
3 | WTG-0003-NDGP-0000 | 1613528 | Winergy Oil Pump Inversion Kit | 2016-11-30 06:38 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MMCCABE |  | 2016-11-30 14:41
3 | WTG-0004-NDGP-0000 | 1613529 | Winergy Oil Pump Inversion Kit | 2016-11-30 06:41 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MMCCABE |  | 2016-12-06 14:02
1 | WTG-0136-0000 | 1649619 | GEARBOX OIL, Replace oil cooler hose | 2016-12-28 14:26 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-01-18 07:33
1 | WTG-0037-NDGP-0000 | 1068209 | Gearbox Oil Sample (Special) | 2014-12-01 14:02 | Closed | GBXOIL | GBXOILSAMP | GRAND RIDGE | MCONWELL |  | 2015-02-04 15:10
4 | WTG-0096-0000 | 1262260 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-04-20 16:06 | Closed | GBXOIL | GBXOILCOOL | FORWARD | CMITCHELL |  | 2016-04-21 08:48
1 | GBX-000094 | 1141296 | EM: Gear oil temperature switching contact | 2015-05-22 17:28 | Closed | GBXOIL | EM72 | PRAIRIE BREEZE | CHADDIX |  | 2015-06-02 12:27
9 | WTG-0027-NDG0-0000 | 1160197 | Gearbox Oil Change | 2015-07-08 19:45 | Closed | GBXOIL | GBXOILCHG | MIAMI 1 | THARDIN |  | 2015-12-18 15:47
9 | WTG-0129-NDG0-0000 | 1160199 | Gearbox Oil Change | 2015-07-08 19:49 | Closed | GBXOIL | GBXOILCHG | MIAMI 1 | THARDIN |  | 2015-12-18 15:51
2 | WTG-0037-NDGP-0000 | 1161613 | OIL COOLER HOSE, GEARBOX OIL, Fix oil leak | 2015-07-17 12:57 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ACARR |  | 2015-07-20 08:40
1 | WTG-0040-0000 | 1179941 | GEARBOX OIL, Oil Sample | 2015-09-07 17:21 | Closed | GBXOIL | GBXOILSAMP | CAL RIDGE | BDAILY |  | 2015-09-08 08:58
2 | WTG-0001-NDGP-0000 | 1209710 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2015-11-24 09:30 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2015-12-02 10:42
4 | WTG-0049-NDGP-0000 | 1242768 | GEARBOX OIL, Replace pump motor | 2016-02-12 16:08 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2016-10-18 14:34
1 | WTG-0019-0000 | 1091840 | Gearbox oil level low | 2015-02-06 09:01 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JBRADDOCK |  | 2015-02-10 12:33
4 | WTG-0070-NDGP-0000 | 1254460 | GEARBOX OIL, Replace gear oil pump due to leak | 2016-03-26 16:30 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2016-04-13 11:56
9 | WTG-0005-0000 | 1239427 | GEARBOX OIL, Secondary filter system installation | 2016-02-05 08:14 | Closed | GBXOIL | GBXFILTINS | RATTLESNAKE 1 | JGASTON |  | 2016-02-16 07:53
2 | WTG-0106-0000 | 1245628 | GEARBOX OIL, Oil Sample | 2016-02-26 07:00 | Closed | GBXOIL | GBXOILSAMP | GRATIOT | SSTGERMAINE |  | 2016-03-04 07:10
4.2 | WTG-0010-NDGP-0000 | 1280129 | GEARBOX OIL, Replace pump | 2016-06-03 15:24 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2016-06-09 09:10
2 | WTG-0063-0000 | 1114757 | GEARBOX OIL, Fix oil leak | 2015-03-31 08:32 | Closed | GBXOIL | GBXOILLEAK | MCADOO | BJAMESON |  | 2015-04-03 10:07
4 | WTG-0086-NDGP-0000 | 1262830 | GEARBOX OIL, Replace oil pump | 2016-04-22 10:11 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2016-04-27 15:12
1 | WTG-0303-0000 | 1272650 | GEARBOX OIL, Fix oil leak | 2016-05-16 17:08 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | DTILLIS |  | 2017-01-25 16:31
4.2 | WTG-0132-NDG0-0000 | 1001504 | Pre-Gearbox Oil Change Detergent Add | 2014-05-08 15:51 | Closed | GBXOIL |  | GREXP | R5 |  | 2015-02-13 14:58
4 | WTG-0017-HP00-0000 | 1136204 | GEARBOX OIL, Fix oil leak- Pitch Drive Leaking Oil | 2015-05-04 16:45 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | CWADE |  | 2019-01-15 08:40
1 | WTG-0083-0000 | 1279538 | GEARBOX OIL, Oil Sample | 2016-06-02 15:47 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | JGASTON |  | 2016-06-03 15:10
1 | WTG-0047-0000 | 1164948 | Filter housing air bleeder hose | 2015-07-30 10:48 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2015-11-01 10:51
1 | WTG-0056-0000 | 1171505 | GEARBOX OIL, Replace oil cooler | 2015-08-13 15:51 | Closed | GBXOIL | GBXOILCOOL | GRAND RIDGE | MJACOBS |  | 2015-12-09 18:41
1 | WTG-0031-NDGP-0000 | 1194759 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2015-10-29 16:17 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2015-12-02 10:43
2 | WTG-0007-NDGP-0000 | 1205914 | Replace Topbox Side Hose from Cooler to Thermal Bypass Housing | 2015-11-17 05:39 | Closed | GBXOIL | GBXOILLEAK | FORWARD | CMITCHELL |  | 2015-12-28 09:10
1 | WTG-0143-0000 | 1243955 | Pall filter housing leak | 2016-02-18 09:16 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | TLOVE |  | 2016-02-19 07:33
2 | WTG-0084-NDGP-0000 | 1249682 | GEARBOX OIL, Particle counter troubleshooting | 2016-03-02 10:45 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2016-03-25 09:22
2 | WTG-0100-NDGP-0000 | 1249683 | GEARBOX OIL, Particle counter troubleshooting | 2016-03-02 10:47 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2016-03-31 10:26
2 | WTG-0102-NDGP-0000 | 1249684 | GEARBOX OIL, Particle counter troubleshooting | 2016-03-02 10:48 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2016-03-25 11:19
2 | WTG-0103-NDGP-0000 | 1249685 | GEARBOX OIL, Particle counter troubleshooting | 2016-03-02 10:48 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2016-03-25 11:19
2 | WTG-0031-NDG0-0000 | 1249686 | Install Poseidon gearbox oil particle troubleshooting | 2016-03-02 10:49 | Closed | GBXOIL | GBXPARTINS | STANTON | MSNOW |  | 2016-03-21 15:32
3 | WTG-0044-NDGP-0000 | 1600804 | Install Winergy oil pump inversion kit | 2016-11-07 09:16 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2016-11-17 13:57
9 | WTG-0067-NDG0-0000 | 1600806 | Tower Clean Up Needed | 2016-11-07 12:24 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2017-04-11 10:18
9 | WTG-0070-NDG0-0000 | 1600807 | Tower Clean Up Needed - Inspect | 2016-11-07 12:26 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2016-11-09 12:07
3 | WTG-0074-NDG0-0000 | 1600882 | GEARBOX OIL, Oil Sample-Special | 2016-11-07 13:45 | Closed | GBXOIL | GBXOILSAMP | MCADOO | RROBERTS |  | 2016-11-07 14:15
9 | WTG-0015-0000 | 1656727 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2017-01-09 08:32 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CRWADE | 30 | 2017-01-26 15:20
1 | WTG-0063-0000 | 1613828 | GEARBOX OIL, Replace oil cooler hose | 2016-11-30 14:14 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2017-10-30 10:13
3 | WTG-0007-NDGP-0000 | 1613838 | Winergy Oil Pump Inversion Kit | 2016-11-30 11:46 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2017-04-25 11:04
4.2 | WTG-0131-NDG0-0000 | 1001407 | In-House GearBox Oil Change Out | 2014-05-08 15:43 | Closed | GBXOIL |  | GREXP | R5 |  | 2015-03-02 15:19
9 | WTG-0011-0000 | 1610739 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-11-28 11:25 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ | 30 | 2017-01-26 15:20
2 | WTG-0037-NDGP-0000 | 964242 | WTG #37_Replace leaking oil cooler | 2014-03-07 08:10 | Closed | GBXOIL |  | FORWARD | TALVARADO |  | 2015-05-08 14:56
2 | GBX-000029 | 1096537 | Oil Sample | 2015-02-23 17:00 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | FANAYA |  | 2015-05-06 11:48
2 | GBX-000042 | 1096538 | Oil Sample | 2015-02-23 17:11 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | FANAYA |  | 2015-05-24 14:59
2 | WTG-0096-NDGP-0000 | 1107222 | Change Jensen System Filter | 2015-03-11 14:29 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE | CBORER |  | 2015-07-20 16:37
1 | WTG-0028-NDGP-0000 | 1093043 | Offline Filter Installation | 2015-02-11 08:54 | Closed | GBXOIL | GBXFILTINS | MIAMI 1 | LPORTER |  | 2015-02-17 13:14
1 | WTG-0129-NDGP-0000 | 1093045 | Offline Filter Installation | 2015-02-11 09:00 | Closed | GBXOIL | GBXFILTINS | MIAMI 1 | LPORTER |  | 2015-02-17 13:16
1 | WTG-0154-NDGP-0000 | 1093047 | Offline Filter Installation | 2015-02-11 09:02 | Closed | GBXOIL | GBXFILTINS | MIAMI 1 | LPORTER |  | 2015-02-17 16:17
1 | WTG-0093-NDGP-0000 | 1129037 | GEARBOX OIL, Fix oil leak | 2015-04-22 07:48 | Closed | GBXOIL | GBXOILLEAK | MCADOO | MGIVENS |  | 2015-04-23 10:21
1 | WTG-0019-0000 | 1128985 | pall filter replacement | 2015-04-21 17:21 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KYARNOLD |  | 2015-04-21 18:25
5 | WTG-0033-HPA3-0000 | 1112835 | WTG#33_Pitch Drive Leak from Plug Axis 3 | 2015-03-27 07:54 | Closed | GBXOIL | GBXOILLEAK | FORWARD | NZIRBEL |  | 2015-07-17 11:01
4 | WTG-0019A-NDG0-0000 | 1592389 | GEARBOX OIL, Add/Top-Off 5 gallons | 2016-10-24 12:25 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2016-10-28 15:23
1 | GBX-000086 | 1134226 | No errors | 2015-05-01 08:35 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | AMITCHELL |  | 2015-05-01 16:34
9 | WTG-0028-NDG0-0000 | 1160198 | Gearbox Oil Change | 2015-07-08 19:48 | Closed | GBXOIL | GBXOILCHG | MIAMI 1 | THARDIN |  | 2015-12-18 15:52
9 | WTG-0155-NDG0-0000 | 1160200 | Gearbox Oil Change | 2015-07-08 19:49 | Closed | GBXOIL | GBXOILCHG | MIAMI 1 | THARDIN |  | 2015-12-21 07:21
9 | WTG-0154-NDG0-0000 | 1160201 | Gearbox Oil Change | 2015-07-08 20:00 | Closed | GBXOIL | GBXOILCHG | MIAMI 1 | THARDIN |  | 2015-12-18 15:53
1 | WTG-0095-ND00-0000 | 1150673 | GEARBOX OIL, Fix oil leak | 2015-06-15 13:34 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CDOHMEN |  | 2015-06-16 12:26
1 | WTG-0037-NDG0-0000 | 1171599 | GEARBOX OIL, Oil Sample | 2015-08-14 09:45 | Closed | GBXOIL | GBXOILSAMP | GRAND RIDGE | NSCHAEFER |  | 2015-08-14 15:52
1 | WTG-0108-0000 | 1092981 | Nacelle Oil Leak | 2015-02-10 17:20 | Closed | GBXOIL | GBXOILLEAK | SCEXP | TZWIRN |  | 2015-07-06 13:42
5 | GBX-000077 | 1096567 | GEARBOX OIL, Oil Sample | 2015-02-24 07:54 | Closed | GBXOIL | GBXOILSAMP | PRAIRIE BREEZE | LHINKLE |  | 2015-02-24 16:59
9 | WTG-0069-0000 | 1177652 | Install AMSOIL Labels on DTA & Gearbox of Turbines that have been converted | 2015-09-01 11:20 | Closed | GBXOIL | GBXOILCHG | GOLDTHWAITE | DDIAZ |  | 2016-07-01 14:45
9 | WTG-0079-0000 | 1177655 | Install AMSOIL Labels on DTA & Gearbox of Turbines that have been converted | 2015-09-01 11:27 | Closed | GBXOIL | GBXOILCHG | GOLDTHWAITE | DDIAZ |  | 2016-02-29 09:00
1 | WTG-0004-NDG0-0000 | 1180804 | GEARBOX OIL, Oil Sample | 2015-09-11 08:10 | Closed | GBXOIL | GBXOILSAMP | FORWARD | GOTKIN |  | 2015-09-14 13:53
1 | WTG-0003-0000 | 1107238 | gearbox oil filter leak | 2015-03-11 15:14 | Closed | GBXOIL | GBXOILLEAK | MCADOO | JZARATE |  | 2015-03-12 10:32
9 | WTG-0035-0000 | 1640283 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-12-09 11:11 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ | 30 | 2017-02-06 13:01
9 | WTG-0061-0000 | 1218137 | GEARBOX, Oil Change | 2015-12-06 09:05 | Closed | GBXOIL | GBXOILCHG | BUCKEYE | CWADE |  | 2016-01-12 16:19
2 | WTG-0007-NDGP-0000 | 1221974 | GEARBOX OIL, Particle counter installation | 2015-12-17 12:16 | Closed | GBXOIL | GBXPARTINS | MCADOO | MSNOW |  | 2016-02-22 08:46
2 | WTG-0010-NDGP-0000 | 1221973 | GEARBOX OIL, Particle counter installation | 2015-12-17 12:15 | Closed | GBXOIL | GBXPARTINS | MCADOO | MSNOW |  | 2016-02-22 08:46
2 | WTG-0006-NDGP-0000 | 1221975 | GEARBOX OIL, Particle counter installation | 2015-12-17 11:16 | Closed | GBXOIL | GBXPARTINS | JUDITH GAP | MSNOW |  | 2016-01-29 10:31
5 | WTG-0001-NDGP-0000 | 1221979 | GEARBOX OIL, Particle counter installation | 2015-12-17 11:19 | Closed | GBXOIL | GBXPARTINS | SPRING CANYON | MSNOW |  | 2017-06-08 10:50
4.2 | WTG-0037-NDGP-0000 | 1221976 | GEARBOX OIL, Particle counter installation | 2015-12-17 12:17 | Closed | GBXOIL | GBXPARTINS | FORWARD | MSNOW |  | 2017-01-16 14:37
2 | WTG-0028-NDGP-0000 | 1259687 | GEARBOX OIL, Particle counter installation | 2016-04-05 10:01 | Closed | GBXOIL | GBXPARTINS | MCADOO | MSNOW |  | 2016-04-21 15:21
1 | WTG-0124-0000 | 1675305 | GEARBOX OIL, Fix oil leak | 2017-02-23 07:59 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | DLANGDON |  | 2017-04-03 14:03
2 | WTG-0011-NDG0-0000 | 1696840 | GEARBOX OIL, Add/Top-Off | 2017-04-20 12:46 | Closed | GBXOIL | GBXOILADD | PRAIRIE BREEZE | PRAIRIE BREEZE |  | 2017-10-06 16:37
4 | WTG-0008-NDG0-0000 | 1852929 | Add 5 gallons of oil | 2018-03-19 14:00 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2018-03-20 09:26
1 | WTG-0093-NDGP-0000 | 1703735 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:29 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | DSLITTLE |  | 2017-05-22 11:09
4 | WTG-0061-NDGP-0000 | 1707483 | Replace Leaking Lube Pump | 2017-05-12 12:07 | Closed | GBXOIL |  | FORWARD | FORWARD |  | 2017-05-17 13:39
1 | WTG-0032-ND00-0000 | 1708445 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2017-05-16 16:42 | Closed | GBXOIL | GBXOILCOOL | SPRING CANYON | SPRINGCANYON |  | 2017-06-30 16:43
4 | WTG-0089-NDGP-0000 | 1709684 | Lube Pump Leak | 2017-05-22 14:17 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2017-05-31 10:01
4 | WTG-0043-NDG0-0000 | 1740032 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 16:52 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-06-29 09:12
4.2 | WTG-0056A-NDGP-0000 | 1221977 | GEARBOX OIL, Particle counter installation | 2015-12-17 12:18 | Closed | GBXOIL | GBXPARTINS | FORWARD | MSNOW |  | 2017-01-16 14:36
5 | WTG-0026-NDGP-0000 | 1221978 | GEARBOX OIL, Particle counter installation | 2015-12-17 11:19 | Closed | GBXOIL | GBXPARTINS | SPRING CANYON | MSNOW |  | 2017-06-08 10:50
1 | WTG-0041-0000 | 1136753 | oil leak on oil distributor plate | 2015-05-06 15:44 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | BCRUTCHFIELD |  | 2015-08-24 09:20
5 | WTG-0043-0000 | 1160561 | GEARBOX OIL, Fix oil leak | 2015-07-10 10:17 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2015-08-19 18:25
9 | WTG-0002-0000 | 1237890 | GEARBOX OIL, Secondary filter system installation | 2016-02-02 12:29 | Closed | GBXOIL | GBXFILTINS | RATTLESNAKE 1 | JGASTON |  | 2016-02-09 07:44
3 | WTG-0034-NDGP-0000 | 1665810 | GEARBOX OIL, Replace oil pump | 2017-01-31 14:46 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2018-07-17 08:13
1 | WTG-0110-NDG0-0000 | 1660032 | EM: Gearbox oil level too low | 2017-01-17 19:01 | Closed | GBXOIL | EM51 | RONCEVAUX | CRO EAST |  | 2017-02-06 15:37
1 | WTG-0009-NDG0-0000 | 1038308 | Gearbox Oil Sample (Special) | 2014-09-02 14:19 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | MCONWELL |  | 2015-03-03 09:06
1 | WTG-0095-0000 | 1124166 | Gearbox Oil Work/Issue | 2015-04-15 13:14 | Closed | GBXOIL | GBXOILLEAK | MCADOO | BJAMESON |  | 2015-04-21 07:36
1 | WTG-0112-0000 | 1135776 | GEARBOX OIL, Oil Sample | 2015-05-04 09:11 | Closed | GBXOIL | GBXOILSAMP | TURKEY TRACK | JBRILEY |  | 2015-05-07 16:00
1 | WTG-0028-0000 | 1138869 | GEARBOX OIL, Oil Sample | 2015-05-13 08:20 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | RIRVING |  | 2015-05-14 11:49
1 | WTG-0023-NDGP-0000 | 1172483 | Replace Nanjing Oil Filter Housing | 2015-08-19 07:00 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | DPANFIL |  | 2015-08-21 09:15
3 | WTG-0048-0000 | 1191129 | Inspect / replace oil cooling motor contactors 26K3 and 34K5 | 2015-10-14 10:05 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | MSTONER |  | 2015-10-23 07:03
5 | WTG-0048-NDG0-0000 | 1191131 | GEARBOX OIL, Add/Top-Off | 2015-10-14 10:27 | Closed | GBXOIL | GBXOILADD | WILLOW CREEK | MSTONER |  | 2015-10-28 13:43
2 | WTG-0100-NDGP-0000 | 1219206 | GEARBOX OIL, Particle counter installation | 2015-12-09 15:29 | Closed | GBXOIL | GBXPARTINS | TURKEY TRACK | MSNOW |  | 2016-01-22 14:35
1 | WTG-0040-0000 | 1403138 | Gearbox oil sample | 2016-08-19 15:58 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | KIRBY |  | 2016-08-30 16:46
1 | WTG-0024-0000 | 1222615 | GEARBOX OIL, Fix oil leak | 2015-12-22 13:12 | Closed | GBXOIL | GBXOILLEAK | STANTON | DKEETON |  | 2015-12-22 15:44
1 | WTG-0041-NDG0-0000 | 1103754 | Oil Sample | 2015-03-06 16:11 | Closed | GBXOIL | GBXOILSAMP | GRAND RIDGE | BBROWN |  | 2015-03-24 06:49
1 | WTG-0045-NDG0-0000 | 1103755 | Oil Sample | 2015-03-06 16:17 | Closed | GBXOIL | GBXOILSAMP | GRAND RIDGE | BBROWN |  | 2015-03-24 06:49
1 | WTG-0084-0000 | 1283433 | Gearbox Cooling System - Mechanical Issue | 2016-06-20 08:01 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | JDWILLIAMS |  | 2016-06-28 14:04
9 | GBX-000129 | 1161110 | Gearbox Oil Change | 2015-07-14 10:04 | Closed | GBXOIL | GBXOILCHG | MIAMI 1 | KYARNOLD |  | 2015-10-20 09:09
9 | GBX-000027 | 1161184 | Gearbox Oil Change | 2015-07-14 17:00 | Closed | GBXOIL | GBXOILCHG | MIAMI 1 | JHAVENS |  | 2015-10-20 09:09
9 | GBX-000028 | 1161185 | Gearbox Oil Change | 2015-07-14 17:01 | Closed | GBXOIL | GBXOILCHG | MIAMI 1 | JHAVENS |  | 2015-10-20 09:09
9 | GBX-000154 | 1161186 | Gearbox Oil Change | 2015-07-14 17:03 | Cancelled | GBXOIL | GBXOILCHG | MIAMI 1 | JHAVENS |  | 2015-07-18 08:51
9 | GBX-000155 | 1161187 | Gearbox Oil Change | 2015-07-14 17:03 | Closed | GBXOIL | GBXOILCHG | MIAMI 1 | JHAVENS |  | 2015-10-20 09:09
9 | WTG-0058-NDB0-0000 | 1182851 | Oil leak found on Gearbox NGC to repair | 2015-09-25 15:54 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | DDIAZ |  | 2015-10-24 11:40
1 | WTG-0123-NDG0-0000 | 1001592 | Post-Gearbox Oil Change Oil Sample | 2014-05-08 15:52 | Closed | GBXOIL | GBXOILSAMP | GREXP | R5 |  | 2015-02-13 14:44
1 | GBX-000048 | 1228863 | Pall Filter Housing Leak | 2016-01-05 20:06 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CHADDIX |  | 2016-01-08 17:30
1 | WTG-0081-0000 | 1230930 | GEARBOX OIL, Replace oil cooler seal | 2016-01-14 10:28 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | MHUFF |  | 2017-03-17 07:43
2 | WTG-0025-0000 | 1230780 | Slow leak from bolt at the bottom of gearbox. | 2016-01-13 11:06 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2017-05-07 23:48
1 | WTG-0122-0000 | 1246066 | GEARBOX OIL, Oil Sample | 2016-02-26 16:04 | Closed | GBXOIL | GBXOILSAMP | CAL RIDGE | SBATLEY |  | 2017-01-12 07:07
3 | WTG-0039-NDG0-0000 | 1240407 | GEARBOX OIL, Oil Sample | 2016-02-08 14:58 | Closed | GBXOIL | GBXOILSAMP | JUDITH GAP | RCARSON |  | 2016-02-09 09:08
4 | WTG-0032-ND00-0000 | 1598486 | GEARBOX OIL, Add/Top-Off | 2016-11-01 13:41 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2016-11-03 10:09
1 | WTG-0048-NDGP-0000 | 1252705 | Winergy Gearbox Oil Pump and Motor Inversion Kit | 2016-03-15 13:08 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MMCCABE |  | 2016-03-17 09:49
2 | WTG-0041A-NDGP-0000 | 1255712 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-03-29 20:21 | Closed | GBXOIL | GBXOILCOOL | FORWARD | ACASPER |  | 2016-04-05 14:54
4 | WTG-0010-NDGP-0000 | 1255792 | GEARBOX OIL, Replace gear oil pump | 2016-03-30 10:32 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KDRAKE |  | 2016-03-30 10:41
1 | WTG-0083-NDG0-0000 | 1660506 | gearbox oil level too low | 2017-01-18 08:07 | Closed | GBXOIL | EM225 | RONCEVAUX | OSIROIS |  | 2017-02-06 15:28
5 | WTG-0098-NDGP-0000 | 1666189 | GEARBOX OIL, Replace (do216 33a1) | 2017-01-31 10:54 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2017-07-24 10:20
2 | WTG-0089-NDGP-0000 | 1234605 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2016-01-29 09:49 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2016-02-01 09:43
9 | WTG-0018-0000 | 1648055 | Hose Leak Found on Radiator after Nanjing Bolt retro | 2016-12-27 14:30 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CSEIDER | 30 | 2016-12-28 13:43
1 | WTG-0080-0000 | 1671740 | GEARBOX OIL, Fix oil leak | 2017-02-14 10:39 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MIAMI |  | 2017-02-15 07:46
4 | WTG-0023A-NDGP-0000 | 1674626 | GEARBOX OIL, Oil leak around gear oil pump | 2017-02-22 11:08 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2017-02-27 12:31
5 | WTG-0014-0000 | 1674465 | Clean up oil leak- See comments | 2017-02-22 08:16 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | MSTONER |  | 2017-05-30 15:56
1 | WTG-0024-0000 | 1675225 | Pic of gearbox and radiator | 2017-02-23 09:13 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BDIAZ |  | 2017-02-24 11:45
2 | WTG-0006-NDGP-0000 | 1676564 | Oil Pump Inversion | 2017-02-27 10:59 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | DSTEO |  | 2018-02-09 18:03
1 | WTG-0001-0000 | 1676612 | REPLACE Inlet Hose | 2017-02-27 12:49 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | MWINGLER |  | 2018-02-28 11:50
1 | WTG-0083-0000 | 1683578 | GEARBOX OIL, Replace oil cooler hose | 2017-03-12 10:00 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2017-03-14 07:28
1 | WTG-0015-0000 | 1686915 | GEARBOX OIL, Replace oil cooler filter material | 2017-03-27 11:14 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | MIAMI |  | 2017-07-18 07:25
1 | WTG-0079-0000 | 1687619 | GEARBOX OIL, Replace oil cooler hose | 2017-03-29 10:38 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MIAMI |  | 2017-03-30 07:18
1 | WTG-0010-0000 | 1689384 | Heat exchange hose leaks | 2017-03-31 14:37 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CHADDIX |  | 2017-11-17 11:22
9 | WTG-0065-NDG0-0000 | 1693386 | GEARBOX rotor side seal replacement | 2017-04-06 13:56 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JUDITHGAP |  | 2017-09-01 14:03
1 | WTG-0025-NDGP-0000 | 1696327 | GEARBOX OIL, Oil Sample | 2017-04-18 09:48 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS I | MSNOW |  | 2017-09-01 15:46
1 | WTG-0031-NDGP-0000 | 1696326 | GEARBOX OIL, Oil Sample | 2017-04-18 09:44 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS I | MSNOW |  | 2017-05-15 16:13
1 | WTG-0062-0000 | 1696212 | GEARBOX OIL, Oil Sample | 2017-04-17 16:14 | Closed | GBXOIL | GBXOILSAMP | RATTLESNAKE 1 | RATTLESNAKE |  | 2017-04-19 09:19
1 | WTG-0026-NDG0-0000 | 1697110 | GEARBOX OIL, Fix oil leak | 2017-04-21 15:13 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | BWHEELER |  | 2017-04-30 13:28
1 | WTG-0044-0000 | 1703715 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:15 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDEWEESE |  | 2017-05-22 11:09
1 | WTG-0081-0000 | 1703716 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:15 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | IAREBALO |  | 2017-05-22 11:09
1 | WTG-0045-0000 | 1703717 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:19 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDEWEESE |  | 2017-05-22 11:09
1 | WTG-0033-0000 | 1703721 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:20 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDEWEESE |  | 2017-09-07 12:11
5 | WTG-0080-0000 | 1703724 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:20 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDKEY |  | 2017-05-22 11:09
1 | WTG-0087-NDG0-0000 | 1703729 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:25 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | IMORALES |  | 2017-05-22 11:09
1 | WTG-0039-0000 | 1703726 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:20 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | JDEWEESE |  | 2017-09-07 12:12
1 | WTG-0084-0000 | 1703728 | GEARBOX OIL, Fix oil leak | 2017-05-02 09:20 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | IAREBALO |  | 2017-05-22 11:09
1 | GBX-000038 | 1706135 | GEARBOX OIL, Fix oil leak | 2017-05-05 15:51 | Closed | GBXOIL | GBXOILLEAK | FORWARD | CMITCHELL |  | 2017-05-10 11:42
4 | WTG-0063A-NDG0-0000 | 1706074 | GEARBOX OIL, Add/Top-Off | 2017-05-05 13:29 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2017-05-10 11:42
1 | WTG-0005-NDG0-0000 | 1706821 | GEARBOX OIL, Fix oil leak | 2017-05-09 11:24 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | DTILLIS |  | 2018-12-20 08:08
3 | WTG-0010-NDGP-0000 | 1708118 | GEARBOX OIL pump inversion, Replace oil pump | 2017-05-15 18:11 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | LHATVELDT |  | 2017-05-16 16:57
1 | WTG-0067-N000-0000 | 1708123 | EM: Gearbox oil overtemperature | 2017-05-15 18:39 | Closed | GBXOIL | EM77 | WAKE 1 | ZMOWERY |  | 2017-05-22 11:08
1 | WTG-0219-0000 | 1709239 | GEARBOX OIL, Fix oil leak, radiator hose | 2017-05-20 14:02 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE |  | 2017-12-05 15:59
1 | WTG-0220-0000 | 1709240 | GEARBOX OIL, Fix oil leak, seam on gearbox | 2017-05-20 14:05 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE |  | 2017-12-05 15:59
1 | WTG-0307-0000 | 1708916 | GEARBOX OIL, Fix oil leak | 2017-05-18 13:41 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2017-12-05 15:59
1 | WTG-0152-0000 | 1709130 | GEARBOX OIL, Fix oil leak | 2017-05-19 15:25 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KMCLELAND |  | 2017-05-23 07:23
3 | WTG-0027-NDGP-0000 | 1709670 | Install low oil cut out/ Oil Sample Valve | 2017-05-22 14:06 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-06-07 09:20
3 | WTG-0039-NDGP-0000 | 1709674 | Install low oil cut out/ Oil Sample Valve | 2017-05-22 14:12 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-10-13 16:41
3 | WTG-0020-NDGP-0000 | 1709671 | Install low oil cut out/ Oil Sample Valve | 2017-05-22 14:07 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-09-29 15:30
3 | WTG-0028-NDGP-0000 | 1709672 | Install low oil cut out/ Oil Sample Valve | 2017-05-22 14:08 | Closed | GBXOIL | GBXFILTINS | WILLOW CREEK | MSTONER | 1 | 2017-09-15 14:56
2 | WTG-0021-0000 | 1709817 | GEARBOX OIL, Secondary filter system installation | 2017-05-23 08:33 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | BUCKEYE |  | 2017-06-12 11:35
1 | WTG-0221-0000 | 1711296 | GEARBOX OIL, Fix oil leak, radiator hose | 2017-05-25 18:26 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2017-12-05 15:59
1 | WTG-0225-0000 | 1715755 | GEARBOX OIL, Fix oil leak | 2017-06-01 16:56 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE |  | 2017-12-05 15:59
3 | WTG-0082-NDGP-0000 | 1734534 | GEARBOX OIL, Secondary filter system element change, valve | 2017-06-08 09:46 | Closed | GBXOIL | GBXFILTELEM | FORWARD | GOTKIN |  | 2017-06-14 11:54
4 | WTG-0034-0000 | 1738393 | GEARBOX OIL, Fix oil leak | 2017-06-22 14:27 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | ACASON |  | 2017-10-09 12:45
1 | WTG-0238-0000 | 1738312 | GEARBOX OIL, Fix oil leak, radiator hose | 2017-06-22 07:55 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE |  | 2017-12-05 15:59
4 | WTG-0001-NDG0-0000 | 1740035 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 16:58 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-07-05 16:12
4 | WTG-0003-NDG0-0000 | 1740036 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 16:58 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-06-28 16:02
4 | WTG-0046-NDG0-0000 | 1740027 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 16:50 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-11-10 07:50
1 | WTG-0063-NDG0-0000 | 1740029 | GEARBOX OIL, Secondary filter system installation | 2017-06-27 16:52 | Closed | GBXOIL | GBXFILTINS | GUNSIGHT | CHUBBARD |  | 2017-06-27 17:05
1 | WTG-0318-0000 | 1759019 | GEARBOX OIL, Fix oil leak | 2017-08-07 11:39 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | PRAIRIE BREEZE |  | 2018-02-13 17:41
1 | WTG-0K01-0000 | 1784487 | GEARBOX OIL, Oil Sample | 2017-10-06 09:31 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2017-10-09 09:36
1 | WTG-0G05-0000 | 1784500 | GEARBOX OIL, Oil Sample | 2017-10-06 09:33 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2017-10-06 11:16
1 | WTG-0F06-0000 | 1784508 | GEARBOX OIL, Oil Sample | 2017-10-06 09:34 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2017-10-06 11:16
1 | WTG-0070-0000 | 1824716 | GEARBOX OIL, Fix oil leak | 2018-01-12 15:17 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | ALUNA |  | 2018-01-23 15:43
1 | WTG-0031-NDG0-0000 | 1808649 | Install Poseidon gearbox oil particle counter | 2017-12-06 10:05 | Closed | GBXOIL | GBXPARTINS | STANTON | MSNOW |  | 2019-01-25 07:51
1 | WTG-0063-NDG0-0000 | 1852864 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2018-03-19 09:48 | Closed | GBXOIL | GBXOILCOOL | MCADOO | MCADOO |  | 2018-03-27 10:37
4 | WTG-0059A-NDG0-0000 | 1853696 | GEARBOX OIL, Add/Top-Off 5gal | 2018-03-22 15:19 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2018-03-27 12:44
4.2 | WTG-0075-NDGP-0000 | 1853753 | Replace Gearbox Heat Exchanger | 2018-03-23 07:32 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2018-06-29 06:56
1 | WTG-0046-0000 | 1853570 | GEARBOX OIL, Fix oil leak | 2018-03-21 16:04 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | WBAUGUS |  | 2018-03-22 09:40
1 | WTG-0006-0000 | 1853702 | GEARBOX OIL, Fix oil leak | 2018-03-22 16:40 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | RWALL |  | 2018-04-02 14:18
1 | WTG-0043-0000 | 1853568 | GEARBOX OIL, Fix oil leak | 2018-03-21 15:51 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | WBAUGUS |  | 2018-03-22 09:40
4 | WTG-0072A-NDGP-0000 | 1860412 | Empty 1gal pail under gearbox | 2018-04-04 18:03 | In Progress | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN
5 | WTG-0072A-NDGP-0000 | 1860411 | Oil cooler fan motor | 2018-04-04 17:59 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2020-01-23 14:49
1 | WTG-0035-ND00-0000 | 1862398 | Gearbox Oil Work/Issue | 2018-04-09 17:13 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 11:56
1 | WTG-0002-ND00-0000 | 1862664 | Gearbox Oil Work/Issue | 2018-04-10 17:25 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TMORRIS |  | 2018-07-20 11:45
5 | WTG-0070-0000 | 1864099 | Add 7 gallons of GBX oil | 2018-04-17 14:49 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2018-08-13 14:53
1 | WTG-0062-0000 | 1865090 | Gearbox Oil Work/Issue | 2018-04-20 15:56 | Closed | GBXOIL | GBXOILLEAK | STANTON | STANTON |  | 2018-04-25 07:50
9 | WTG-0081-0000 | 1865956 | Clean oil leak | 2018-04-24 12:11 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2018-11-07 15:39
1 | WTG-0060-0000 | 1866508 | GEARBOX OIL, Fix oil leak | 2018-04-25 14:54 | Closed | GBXOIL | GBXOILLEAK | BETHEL | BETHEL |  | 2018-04-26 17:42
4 | WTG-0211A-ND00-0000 | 1867151 | GEARBOX OIL, Add/Top-Off | 2018-04-26 12:06 | Closed | GBXOIL | GBXOILADD | FORWARD | CMITCHELL |  | 2018-05-02 10:30
1 | WCEC | 1869430 | Obtain Oil Samples | 2018-05-01 12:21 | Closed | GBXOIL | GBXOILSAMP | WOLVERINE CREEK | WOLVERINECREEK |  | 2018-05-10 16:00
1 | WTG-0067-0000 | 1871457 | GEARBOX OIL, Fix oil leak | 2018-05-03 21:08 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | CRWADE |  | 2018-05-14 15:07
1 | WTG-0123-NDG0-0000 | 1741020 | EM: Gearbox oil overtemperature | 2017-06-29 15:47 | Closed | GBXOIL | EM77 | WAKE 1 | IMORALES |  | 2017-06-30 11:53
9 | WTG-0136-NDG0-0000 | 1759860 | GEARBOX, Oil Change | 2017-08-10 16:29 | Cancelled | GBXOIL | GBXOILCHG | CAMP SPRINGS II | JSULLIVAN |  | 2017-08-24 14:34
9 | WTG-0148-NDG0-0000 | 1759863 | GEARBOX, Oil Change | 2017-08-10 16:33 | Cancelled | GBXOIL | GBXOILCHG | CAMP SPRINGS II | JSULLIVAN |  | 2017-08-24 14:33
9 | WTG-0163-NDG0-0000 | 1759865 | GEARBOX, Oil Change | 2017-08-10 16:36 | Cancelled | GBXOIL | GBXOILCHG | CAMP SPRINGS II | JSULLIVAN |  | 2017-08-24 14:32
1 | WTG-0F08-0000 | 1759793 | GEARBOX OIL, Replace oil cooler | 2017-08-10 04:14 | Closed | GBXOIL | GBXOILCOOL | HIGH SHELDON | BEUSCHER |  | 2017-08-14 08:20
1 | WTG-0105-NDGP-0000 | 1759574 | GEARBOX OIL, Oil Sample | 2017-08-09 11:28 | Closed | GBXOIL | GBXOILSAMP | CAMP SPRINGS II | MSNOW |  | 2017-08-10 08:58
9 | WTG-0003-0000 | 1759611 | rFSA Claim - Pitch Tube Replacement by GE | 2017-08-09 14:24 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2017-09-12 13:21
2 | WTG-0062-NDG0-0000 | 1761183 | Gearbox Oil Secondary Filter System Element Change | 2017-08-15 15:15 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GBOTT | 1 | 2017-08-16 07:03
2 | WTG-0077-NDG0-0000 | 1761185 | Gearbox Oil Secondary Filter System Element Change | 2017-08-15 15:18 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GBOTT | 1 | 2017-08-16 07:03
4 | WTG-0072A-NDG0-0000 | 1763746 | GEARBOX OIL, Add 5 gals | 2017-08-17 12:51 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2017-11-27 09:32
4 | WTG-0097-0000 | 1764043 | GEARBOX OIL, Replace oil pump | 2017-08-21 10:39 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2017-08-22 11:37
2 | WTG-0081-0000 | 1764074 | GEARBOX OIL, Secondary filter system element change | 2017-08-21 14:37 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-08-22 10:09
2 | WTG-0008-NDGP-0000 | 1763981 | gearbox oil cooler leaking | 2017-08-20 16:37 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2018-11-15 08:20
1 | WTG-0109-NDGP-0000 | 1765055 | GEARBOX OIL, Oil Sample | 2017-08-23 09:09 | Closed | GBXOIL | GBXOILSAMP | BUCKEYE | MSNOW |  | 2017-08-25 10:45
5 | WTG-0023-NDGP-0000 | 1765489 | Reinstall CCJensen on new Najing GBX | 2017-08-24 13:45 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | MSTONER |  | 2017-10-09 13:14
2 | WTG-0076-0000 | 1765511 | GEARBOX OIL, Secondary filter system element change | 2017-08-24 15:02 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-08-25 06:59
4.2 | WTG-0083-0000 | 1770599 | GEARBOX OIL, Secondary filter system element change | 2017-09-05 14:07 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT |  | 2017-09-06 15:12
4 | WTG-0083-NDG0-0000 | 1771519 | GEARBOX OIL, Add/Top-Off | 2017-09-07 08:02 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2017-09-22 10:47
1 | WTG-0013-NDG0-0000 | 1772849 | GEARBOX OIL, Fix oil leak | 2017-09-08 14:48 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | RWALL |  | 2018-08-22 13:59
2 | WTG-0007-NDGP-0000 | 1773038 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2017-09-10 18:38 | Closed | GBXOIL | GBXOILCOOL | TURKEY TRACK | JBRILEY |  | 2017-09-15 16:44
1 | WTG-0016-0000 | 1774379 | GEARBOX OIL, Fix oil leak | 2017-09-14 14:44 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | JCHEUVRONT |  | 2017-09-25 14:08
9 | WTG-0106-0000 | 1775016 | TERP GBX Oil Change | 2017-09-15 15:23 | Closed | GBXOIL | GBXOILCHG | PRAIRIE BREEZE | AMELENGU | 1 | 2017-10-31 16:57
1 | WTG-0003-0000 | 1775983 | Replaced Cooler Outlet Hose | 2017-09-19 17:25 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2017-09-20 10:49
1 | WTG-0003-0000 | 1775985 | Replaced oil filter housing | 2017-09-19 17:34 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2017-09-20 10:49
1 | WTG-0003-0000 | 1775984 | Replaced Cooler to thermal bypass manifold hose | 2017-09-19 17:27 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | FANAYA |  | 2017-09-20 10:49
4 | WTG-0089-NDG0-0000 | 1776708 | Clean up nacelle after oil leak | 2017-09-21 16:52 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2017-09-25 08:42
4.2 | WTG-0106-NDGP-0000 | 1776758 | Replace Gearbox Cooler Duct | 2017-09-22 07:32 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2017-12-07 06:57
1 | WTG-0G10-NDG0-0000 | 1784176 | GEARBOX OIL, Particle counter installation | 2017-10-05 11:15 | Closed | GBXOIL | GBXPARTINS | BEECH RIDGE | SCLARK |  | 2017-10-26 10:22
1 | WTG-0J06-0000 | 1786161 | Re-Install posiden counter | 2017-10-11 10:36 | Closed | GBXOIL | GBXOILCOOL | HIGH SHELDON | CSTRZELEC |  | 2017-10-12 09:08
2 | WTG-0024-NDG0-0000 | 1787523 | T24 Amsoil 320 | 2017-10-16 10:00 | Closed | GBXOIL | GBXOILADD | VANTAGE | VANTAGE |  | 2017-10-16 17:14
4 | WTG-0035-NDG0-0000 | 1788374 | GEARBOX OIL, Add/Top-Off 5 gals | 2017-10-18 16:17 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2018-03-02 16:11
1 | WTG-0083-NDGP-0000 | 1788269 | Leaking pall filter housing | 2017-10-18 08:32 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE |  | 2017-11-06 16:28
1 | WTG-0070-0000 | 1788841 | GEARBOX OIL, Fix oil leak | 2017-10-21 15:29 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2017-10-23 15:16
2 | WTG-0A02-0000 | 1789589 | CT-320 Oil Samples | 2017-10-24 14:19 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2017-10-24 14:52
2 | WTG-0G04-0000 | 1789594 | CT-320 Oil Samples | 2017-10-24 14:30 | Closed | GBXOIL | GBXOILSAMP | HIGH SHELDON | BEUSCHER |  | 2017-10-24 14:51
5 | WTG-0063A-0000 | 1793711 | GEARBOX OIL, Fix oil leak/Clean decks | 2017-10-29 14:47 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2017-10-30 16:05
2 | WTG-0106-NDGP-0000 | 1793412 | Gearbox Oil Secondary Filter System Element Change | 2017-10-27 08:23 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | JCAPEN |  | 2017-10-27 15:10
2 | WTG-0105-NDGP-0000 | 1793411 | Gearbox Oil Secondary Filter System Element Change | 2017-10-27 08:20 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | JCAPEN |  | 2017-10-30 07:08
2 | WTG-0037-NDGP-0000 | 1793542 | GEARBOX OIL, Particle counter Troubleshooting | 2017-10-27 10:56 | Cancelled | GBXOIL | GBXPARTINS | FORWARD | MSNOW |  | 2018-02-20 11:34
1 | BMEC | 1795871 | WTG013 - High Gear Oil Temp | 2017-10-31 07:58 | Closed | GBXOIL |  | BUFFALO MOUNT | CLAWSON |  | 2017-12-14 15:14
4 | WTG-0006-NDG0-0000 | 1798157 | GEARBOX OIL, Fix oil leak | 2017-11-03 12:57 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2017-11-30 14:02
1 | WTG-0007-NDG0-0000 | 1800846 | GEARBOX OIL, Fix oil leak,GBX Warranty | 2017-11-13 09:54 | Closed | GBXOIL | GBXOILLEAK | MCADOO | RROBERTS |  | 2018-08-02 13:49
1 | WTG-0114-0000 | 1801091 | Replace sweating hose | 2017-11-14 09:23 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BSHOOK |  | 2017-12-05 08:53
4 | WTG-0004-NDG0-0000 | 1802474 | GEARBOX OIL, Add/Top-Off (about 5 gallons) | 2017-11-21 16:03 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2018-04-13 13:58
2 | WTG-0007-NDG0-0000 | 1802609 | GEARBOX OIL, Replace oil pump motor | 2017-11-22 12:09 | Cancelled | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2018-12-07 10:16
2 | WTG-0099-NDGP-0000 | 1804994 | Gearbox Oil Secondary Filter System Element Change | 2017-11-30 14:45 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT | 1 | 2017-12-04 06:55
2 | WTG-0100-NDGP-0000 | 1804995 | Gearbox Oil Secondary Filter System Element Change | 2017-11-30 14:47 | Closed | GBXOIL | GBXFILTELEM | GRATIOT | GRATIOT | 1 | 2017-12-04 06:55
1 | WTG-0120-0000 | 1808041 | GEARBOX OIL, Fix oil leak | 2017-12-05 11:33 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2017-12-06 07:45
2 | WTG-0020-0000 | 1810027 | Add Oil to Gearbox | 2017-12-12 08:40 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2017-12-20 10:32
5 | WTG-0055A-0000 | 2173837 | Lube pump rebuild / replace coupler | 2020-01-15 14:13 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2020-01-17 11:04
1 | WTG-0109-N000-0000 | 1810791 | Needs new secondary pump | 2017-12-13 16:17 | Cancelled | GBXOIL | GBXFILTINS | GREXP | MFERRARO |  | 2023-06-29 13:12
2 | WTG-0087-0000 | 1814404 | Add Oil to Gearbox | 2017-12-15 10:11 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:44
4.2 | WTG-0132-ND00-0000 | 1816553 | Replace leaking gearbox heat exchanger | 2017-12-28 14:36 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2018-01-29 13:29
2 | WTG-0020-0000 | 1821853 | Add Oil to Gearbox | 2017-12-11 09:12 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:04
2 | WTG-0022-0000 | 1821854 | Add Oil to Gearbox | 2017-12-12 09:15 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 12:03
2 | WTG-0036-0000 | 1821861 | Add Oil to Gearbox | 2017-12-12 09:23 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-09 16:35
2 | WTG-0203B-NDGP-0000 | 1821783 | GEARBOX OIL, Replace oil pump | 2018-01-08 17:20 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2018-01-12 15:00
2 | WTG-0089-0000 | 1821627 | Add Oil to Gearbox | 2018-01-05 08:09 | Closed | GBXOIL | GBXOILADD | BUCKEYE | BUCKEYE |  | 2018-01-08 10:56
4 | WTG-0061-NDG0-0000 | 1832464 | GEARBOX OIL, Add/Top-Off 5 gals | 2018-01-29 18:36 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2018-05-30 09:32
2 | WTG-0E03-NDGP-0000 | 1837993 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:19 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-04-12 14:31
2 | WTG-0G04-NDGP-0000 | 1837997 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:24 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-03-05 08:03
2 | WTG-0H09-NDGP-0000 | 1838003 | GEARBOX OIL, Secondary filter system installation | 2018-02-05 14:30 | Closed | GBXOIL | GBXFILTINS | BEECH RIDGE | BEECHRIDGE |  | 2018-04-02 16:55
5 | WTG-0043-NDG0-0000 | 1839110 | GEARBOX OIL, Add/Top-Off | 2018-02-09 15:15 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2018-05-11 14:11
2 | WTG-0016-NDGP-0000 | 1841101 | Replace gear oil pump | 2018-02-20 08:52 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2018-04-13 15:37
2 | WTG-0013-NDG0-0000 | 1842193 | GEARBOX OIL, Add Oil due to CCJ Leak | 2018-02-23 16:11 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2018-02-26 12:54
1 | WTG-0011-NDGP-0000 | 1849602 | EM: Gearbox oilpressure mechanical pump not OK | 2018-03-05 14:57 | Closed | GBXOIL | EM256 | MCADOO | MCADOO |  | 2018-03-05 15:54
2 | SITE-VWEC | 1856636 | Shop CCJ Filter Change | 2018-03-28 12:50 | Closed | GBXOIL | GBXFILTELEM | VANTAGE | SENGLAND |  | 2018-03-28 17:13
1 | WTG-0023-ND00-0000 | 1862390 | Gearbox Oil Work/Issue | 2018-04-09 17:11 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 11:55
1 | WTG-0024-ND00-0000 | 1862391 | Gearbox Oil Work/Issue | 2018-04-09 17:12 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 11:55
1 | WTG-0007-ND00-0000 | 1862316 | Gearbox Oil Work/Issue | 2018-04-09 16:37 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TMORRIS |  | 2018-07-20 11:48
1 | WTG-0021-ND00-0000 | 1862314 | Gearbox Oil Work/Issue | 2018-04-09 16:25 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TMORRIS |  | 2018-07-20 11:54
1 | WTG-0013-ND00-0000 | 1862317 | Gearbox Oil Work/Issue | 2018-04-09 16:38 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TMORRIS |  | 2018-07-20 11:49
2 | WTG-0063-ND00-0000 | 1862320 | Gearbox Oil Work/Issue | 2018-04-09 17:00 | Closed | GBXOIL |  | RATTLESNAKE 1 | JTHOMPSON |  | 2018-07-20 12:09
1 | WTG-0074-0000 | 1862865 | Gearbox Oil Work/Issue | 2018-04-11 17:37 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BDIAZ |  | 2018-07-20 12:26
1 | WTG-0003-0000 | 1862867 | Gearbox Oil Work/Issue | 2018-04-11 17:37 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | BDIAZ |  | 2018-07-20 11:46
1 | WTG-0098-ND00-0000 | 1862882 | Gearbox Oil Work/Issue | 2018-04-11 17:37 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TCARD |  | 2018-07-20 12:37
1 | WTG-0088-ND00-0000 | 1862884 | Gearbox Oil Work/Issue | 2018-04-11 17:44 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | TCARD |  | 2018-07-20 12:35
4 | WTG-0057-NDG0-0000 | 1864110 | GEARBOX OIL, Add/Top-Off 5 gals | 2018-04-17 16:48 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2018-04-23 14:41
4 | WTG-0213-0000 | 1864857 | Replace 2 Oil Lines | 2018-04-20 07:29 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2019-04-29 17:38
1 | WTG-0113-0000 | 1865136 | GEARBOX OIL, Fix oil leak | 2018-04-21 15:09 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | CROLAND |  | 2018-05-04 16:57
2 | WTG-0065-0000 | 2032439 | GEARBOX OIL, radiator hose needs replaced WC# 2979166 | 2019-02-05 13:14 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | UPSTREAM |  | 2019-08-01 17:03
1 | WTG-0024-0000 | 1873959 | GEARBOX OIL, Fix oil leak | 2018-05-11 13:30 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | JDWILLIAMS |  | 2019-05-13 15:50
1 | WTG-0090-NDGP-0000 | 1873955 | GEARBOX OIL, Replace oil pump motor | 2018-05-11 15:55 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2018-05-30 10:19
1 | WTG-0073-0000 | 1892564 | GEARBOX OIL, Sweating Hose | 2018-06-12 09:51 | Cancelled | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | CPRUIT
5 | WTG-0024-NDG0-0000 | 1893465 | Fix oil leak, leaking from front low speed shaft | 2018-06-14 18:00 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | FORWARD
4 | WTG-0040A-NDG0-0000 | 1923699 | Secondary filter, Fix oil leak | 2018-07-11 17:30 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2018-07-23 10:36
1 | WTG-0221-0000 | 1923776 | GEARBOX OIL, Fix oil leak | 2018-07-11 18:00 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | DTILLIS |  | 2019-01-11 16:30
5 | WTG-0061-NDGP-0000 | 1925247 | Oil Pump Replacement | 2018-07-16 15:38 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2018-11-16 09:36
2 | WTG-0085-NDGP-0000 | 1925225 | Replace gearbox oil pump motor | 2018-07-16 13:17 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2018-08-22 15:52
2 | WTG-0011-0000 | 1936248 | Gearbox breather replacement | 2018-08-13 22:43 | Cancelled | GBXOIL | GBXFILTELEM | CAL RIDGE | JDALTON
1 | WTG-0042-0000 | 1940006 | GEARBOX OIL, Fix oil leak, secondary pump housing leak | 2018-08-21 08:30 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | TURKEY TRACK |  | 2018-12-11 23:00
1 | WTG-0043-0000 | 1943524 | GEARBOX OIL, Secondary filter system installation | 2018-08-31 14:49 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | MLEGLEITER |  | 2018-09-17 10:40
1 | WTG-0026-0000 | 1948809 | oil filter housing leaking | 2018-09-12 15:27 | Closed | GBXOIL | GBXOILLEAK | CAL RIDGE | CAL RIDGE |  | 2019-06-24 16:18
4 | WTG-0022-NDBS-0000 | 1959786 | Hyd oil leak. Replaced pressure gauge | 2018-10-10 14:48 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2018-10-12 13:04
1 | WTG-0011-0000 | 1961113 | Replace Cooler Outlet Hose | 2018-10-16 09:38 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2019-01-10 16:14
1 | WTG-0098-0000 | 1961788 | GEARBOX OIL, Fix oil leak | 2018-10-18 15:11 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | TURKEY TRACK |  | 2018-11-26 14:53
1 | WTG-0035-NDGP-0000 | 1983169 | GEARBOX OIL, Fix oil leak | 2018-11-13 09:08 | Cancelled | GBXOIL | GBXOILLEAK | GRAND RIDGE | GRAND RIDGE |  | 2023-06-29 13:12
4 | WTG-0030-NDG0-0000 | 1983160 | Need oil catch pail under planteary | 2018-11-13 07:58 | Closed | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN |  | 2019-11-18 12:08
2 | WTG-0030-NDGP-0000 | 1983157 | GEARBOX OIL, Replace oil cooler | 2018-11-13 07:47 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2020-02-10 15:52
1 | WTG-0113-NDG0-0000 | 1984015 | GEARBOX OIL, Fix oil leak | 2018-11-16 09:05 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2018-12-02 11:18
1 | WTG-0027-0000 | 1991075 | GEARBOX OIL, Fix oil leak | 2018-12-03 14:32 | Closed | GBXOIL | GBXOILLEAK | RATTLESNAKE 1 | JGASTON |  | 2018-12-06 12:05
2 | WTG-0018-0000 | 1992324 | GEARBOX OIL, Add/Top-Off | 2018-12-04 16:47 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NSCHMEIDLER |  | 2019-02-14 08:03
5 | WTG-0207-0000 | 1993029 | GEARBOX OIL, Fix oil leak | 2018-12-06 17:32 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE |  | 2019-12-06 13:23
4 | WTG-0072A-NDG0-0000 | 1994015 | GEARBOX OIL, Add/Top-Off 5 Gal | 2018-12-11 08:30 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2019-04-22 12:38
4 | GBX-737000005474 | 2011864 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000005476 | 2011865 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000005477 | 2011866 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | SYS-WTG-BUCK | 2011807 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL | GBXOILSAMP | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-FDMD-00R5-H207 | 2011867 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-FDMD-00R5-H224 | 2011868 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-FDMD-4021 | 2011869 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-FDMD-4026 | 2011870 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-FDMD-4054 | 2011871 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004103 | 2011858 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004105 | 2011859 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004106 | 2011860 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004114 | 2011861 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004118 | 2011862 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004119 | 2011863 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | WTG-0205-NDG0-0000 | 2012520 | Add 5 gallons of oil | 2019-01-07 14:17 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2019-01-10 16:29
4 | WTG-0014-NDG0-0000 | 2019512 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
2 | WTG-0067-0000 | 1871541 | GEARBOX OIL, Add/Top-Off | 2018-05-04 08:39 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | CRWADE |  | 2020-05-19 14:13
1 | WTG-0032-NDG0-0000 | 1881466 | Oil leak | 2018-06-02 15:38 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | TURKEY TRACK |  | 2018-07-30 12:29
1 | WTG-0024-0000 | 1887683 | Oil Leak | 2018-06-05 17:01 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | AHOFFMANN |  | 2018-06-26 15:38
1 | GBX-000017 | 1893445 | GEARBOX OIL, Remove Secondary filter system | 2018-06-14 16:22 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | RCARSON |  | 2018-06-15 14:02
1 | WTG-0043-NDG0-0000 | 1895183 | Reprogram Particle Counter IP Address | 2018-06-22 10:49 | Closed | GBXOIL | GBXPARTINS | GUNSIGHT | RPATEL |  | 2018-10-29 17:16
1 | WTG-0016-NDG0-0000 | 1921679 | GEARBOX OIL, Fix oil leak | 2018-07-05 17:20 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | SPRINGCANYON |  | 2018-07-07 13:08
1 | WTG-0058-0000 | 1928905 | GEARBOX OIL, Fix oil leak | 2018-07-26 15:09 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE |  | 2019-02-15 17:09
2 | WTG-0125-NDGP-0000 | 1930786 | secondary oil filter element change | 2018-07-31 07:19 | Closed | GBXOIL | GBXFILTELEM | GREXP | GRAND RIDGE |  | 2018-08-02 00:45
1 | WTG-0063-NDGP-0000 | 1934539 | Install secondary filtration system on gearbox oil | 2018-08-08 12:20 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-02-28 11:23
1 | WTG-0069-NDGP-0000 | 1934546 | Install secondary filtration system on gearbox oil | 2018-08-08 12:26 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-02-11 11:42
1 | WTG-0070-NDGP-0000 | 1934547 | Install secondary filtration system on gearbox oil | 2018-08-08 12:26 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-02-08 10:53
1 | WTG-0072-NDGP-0000 | 1934552 | Install secondary filtration system on gearbox oil | 2018-08-08 12:27 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2018-09-13 17:19
1 | WTG-0074-NDGP-0000 | 1934554 | Install secondary filtration system on gearbox oil | 2018-08-08 12:28 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-02-01 15:05
1 | WTG-0079-NDGP-0000 | 1934559 | Install secondary filtration system on gearbox oil | 2018-08-08 12:30 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-01-25 07:50
1 | WTG-0080-NDGP-0000 | 1934560 | Install secondary filtration system on gearbox oil | 2018-08-08 12:30 | Closed | GBXOIL | GBXFILTINS | STANTON | LCOPELAND | 1 | 2019-01-21 15:15
1 | WTG-0010-0000 | 1936120 | GEARBOX OIL, Oil Sample | 2018-08-13 15:47 | Closed | GBXOIL | GBXOILSAMP | CAL RIDGE | CAL RIDGE |  | 2019-03-07 08:59
4 | WTG-0056A-NDGP-0000 | 1936261 | GEARBOX OIL, Filter needs catch basin | 2018-08-14 06:13 | Closed | GBXOIL | GBXOILCOOL | FORWARD | MPEARSON |  | 2018-12-12 09:44
1 | WTG-0070-NDGP-0000 | 1936273 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2018-08-10 10:13 | Closed | GBXOIL | GBXOILCOOL | CAMP SPRINGS I | JSANCHEZ |  | 2018-08-15 09:18
1 | WTG-0117-NDGP-0000 | 1939681 | GEARBOX OIL, Fix oil leak | 2018-08-18 15:35 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2018-12-02 11:14
2 | WTG-0062-NDGP-0000 | 1948838 | GEARBOX OIL, Replace motor for lube pump | 2018-09-12 17:21 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2019-06-14 14:01
4 | WTG-0205-NDGP-0000 | 1952528 | GEARBOX OIL, Catch tray needed | 2018-09-25 08:22 | Closed | GBXOIL | GBXFILTELEM | FORWARD | KLEFFELMAN |  | 2019-05-03 10:24
5 | WTG-0016-0000 | 1965137 | Retro, GBX oil pump coupler inspection hole | 2018-10-29 15:01 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2019-01-07 11:55
4 | WTG-0065-NDG0-0000 | 1982439 | GEARBOX OIL, Add/Top-Off5 gals/leak che k | 2018-11-08 15:36 | Closed | GBXOIL | GBXOILADD | FORWARD | MPEARSON |  | 2019-01-21 16:22
1 | WTG-0052-NDG0-0000 | 1991139 | GEARBOX OIL, Fix oil leak | 2018-12-03 18:55 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JUDITHGAP |  | 2018-12-07 10:20
1 | WTG-0077-0000 | 1995174 | GEARBOX OIL, Fix oil leak | 2018-12-12 18:17 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE | PRAIRIE BREEZE |  | 2018-12-20 08:08
1 | WTG-0085-NDG0-0000 | 1995167 | GEARBOX OIL, Particle counter installation | 2018-12-12 17:26 | Closed | GBXOIL | GBXPARTINS | GREXP | RPPATEL |  | 2019-01-30 10:35
1 | WTG-0033-NDG0-0000 | 1995170 | GEARBOX OIL, Particle counter installation | 2018-12-12 17:42 | Closed | GBXOIL | GBXPARTINS | GUNSIGHT | RPPATEL |  | 2019-01-17 19:02
1 | WTG-0036-NDG0-0000 | 1995173 | GEARBOX OIL, Particle counter installation | 2018-12-12 17:44 | Closed | GBXOIL | GBXPARTINS | GUNSIGHT | RPPATEL |  | 2019-01-18 15:08
2 | WTG-0213-NDG0-0000 | 2003242 | GEARBOX OIL, Particle counter installation | 2018-12-19 14:44 | Closed | GBXOIL | GBXPARTINS | FORWARD | SCLARK |  | 2019-01-23 13:03
1 | JGEC-WTG-001 | 2005066 | GEARBOX OIL, Secondary filter system installation | 2018-12-26 10:50 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | MPRATER |  | 2019-02-27 10:16
4 | GBX-737000004077 | 2011852 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004078 | 2011853 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004079 | 2011854 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004081 | 2011855 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004085 | 2011856 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
4 | GBX-737000004086 | 2011857 | 2019 Maintenance Cycle GBX Oil Sample | 2019-01-04 16:43 | Closed | GBXOIL |  | BUCKEYE | LLANG-PARSON |  | 2024-06-17 11:28
1 | WTG-0E10-NDGP-0000 | 2015808 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2019-01-08 12:30 | Closed | GBXOIL | GBXOILCOOL | HIGH SHELDON | CGREIS |  | 2019-04-08 09:45
4 | WTG-0204A-NDGP-0000 | 2016091 | Oil Cooler vent tube | 2019-01-09 12:35 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2019-05-06 12:37
4 | WTG-0030-NDG0-0000 | 2019528 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0031-NDG0-0000 | 2019529 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0032-NDG0-0000 | 2019530 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0033-NDG0-0000 | 2019531 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0034-NDG0-0000 | 2019532 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0035-NDG0-0000 | 2019533 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0036-NDG0-0000 | 2019534 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0037-NDG0-0000 | 2019535 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0038-NDG0-0000 | 2019536 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0039-NDG0-0000 | 2019537 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0040-NDG0-0000 | 2019538 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0041-NDG0-0000 | 2019539 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0042-NDG0-0000 | 2019540 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0043-NDG0-0000 | 2019541 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0044-NDG0-0000 | 2019542 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0045-NDG0-0000 | 2019543 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0012-NDG0-0000 | 2019510 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0013-NDG0-0000 | 2019511 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0015-NDG0-0000 | 2019513 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0016-NDG0-0000 | 2019514 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0017-NDG0-0000 | 2019515 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0018-NDG0-0000 | 2019516 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0019-NDG0-0000 | 2019517 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0098-NDG0-0000 | 2019596 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0020-NDG0-0000 | 2019518 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0021-NDG0-0000 | 2019519 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0093-NDG0-0000 | 2019591 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0094-NDG0-0000 | 2019592 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0095-NDG0-0000 | 2019593 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0096-NDG0-0000 | 2019594 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0097-NDG0-0000 | 2019595 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0099-NDG0-0000 | 2019597 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0100-NDG0-0000 | 2019598 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0101-NDG0-0000 | 2019599 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0102-NDG0-0000 | 2019600 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0103-NDG0-0000 | 2019601 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | WTG-0104-NDG0-0000 | 2019602 | 2019 Gearbox Oil Samples | 2019-01-10 13:48 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2020-05-08 11:26
4 | GBX-000028 | 2027444 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
5 | WTG-0047-NDG0-0000 | 2024500 | 5 gallons amsoil needed | 2019-01-22 07:54 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2019-03-18 15:59
4 | WTG-0046-NDGP-0000 | 2025698 | Oil cooler needs filter | 2019-01-25 09:23 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2019-05-29 11:27
4 | GBX-000022 | 2027438 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000024 | 2027439 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000025 | 2027440 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000026 | 2027442 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000027 | 2027443 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000029 | 2027445 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
4 | GBX-000030 | 2027446 | 2019 GBX OIL SAMPLE ANALYSIS SERVICES | 2019-01-29 15:41 | Closed | GBXOIL |  | WILLOW CREEK | SBROWNING |  | 2020-03-04 16:42
2 | WTG-0085-NDG0-0000 | 2027843 | GEARBOX OIL, Inspect filter | 2019-01-30 09:34 | Closed | GBXOIL | GBXFILTELEM | GREXP | SCLARK |  | 2019-04-04 09:54
1 | WTG-0076-0000 | 2038815 | GEARBOX OIL, Secondary filter system installation | 2019-02-19 16:44 | Closed | GBXOIL | GBXFILTINS | GREXP | GRAND RIDGE |  | 2019-02-19 17:03
4 | WTG-0018-NDG0-0000 | 2040333 | Add 2-3 gallons of Amsoil to GBX | 2019-02-25 16:52 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-07-11 16:12
2 | WTG-0024-NDGP-0000 | 2041595 | Secondary oil system troubleshooting | 2019-02-28 09:45 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | JUDITHGAP |  | 2019-03-20 16:58
4 | WTG-0030-NDGP-0000 | 2048445 | GEARBOX OIL, Add/Top-Off 5 gals | 2019-03-04 15:34 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2019-03-08 15:22
4 | WTG-0032-NDG0-0000 | 2049735 | Add about 6 gallons of Amsoil to GBX | 2019-03-05 15:49 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2019-03-08 15:44
4 | WTG-0012-NDG0-0000 | 2052625 | GEARBOX OIL, Add/Top-Off 5 Gallons of Amsoil | 2019-03-15 14:18 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2019-07-10 07:50
4 | WTG-0007-NDGP-0000 | 2053975 | GEARBOX OIL, Add/Top-Off | 2019-03-22 16:56 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2019-07-02 08:54
1 | WTG-0112-0000 | 2053982 | GEARBOX OIL, Fix oil leak | 2019-03-22 17:36 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SCEXP |  | 2019-09-05 13:57
1 | WTG-0017-0000 | 2055888 | 2019 Padmount Oil Sample | 2019-03-27 15:32 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2020-08-06 14:28
1 | WTG-0008-0000 | 2055898 | 2019 Padmount Oil Sample | 2019-03-27 15:35 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-04-18 13:37
1 | WTG-0061-0000 | 2060882 | GEARBOX OIL, Oil Sample | 2019-04-03 12:46 | Closed | GBXOIL | GBXOILSAMP | BISHOP HILL | BISHOP HILL |  | 2019-04-04 10:13
1 | WTG-0059-0000 | 2061788 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2019-04-04 08:31 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | SMILLER |  | 2019-04-05 10:22
5 | WTG-0004-NDG0-0000 | 2064399 | GEARBOX OIL, Add 5 gal oil | 2019-04-10 17:42 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2019-04-15 15:23
4 | WTG-0059A-NDG0-0000 | 2065558 | GEARBOX OIL, Add about 5 Gallons Amsoil | 2019-04-16 16:42 | Closed | GBXOIL |  | FORWARD | JLAWRENCE |  | 2019-04-24 15:05
3 | WTG-0093-NDGP-0000 | 2065923 | Gearbox running too hot | 2019-04-18 08:20 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-05-30 17:03
3 | WTG-0094-NDG0-0000 | 2065924 | Gearbox running too hot | 2019-04-18 08:21 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-05-30 07:57
1 | WTG-0099-NDG0-0000 | 2068690 | GEARBOX OIL, Particle counter installation | 2019-04-25 13:59 | Closed | GBXOIL | GBXPARTINS | MCADOO | RPPATEL |  | 2019-05-07 12:18
1 | WTG-0046-NDG0-0000 | 2068691 | GEARBOX OIL, Particle counter installation | 2019-04-25 14:02 | Closed | GBXOIL | GBXPARTINS | MCADOO | RPPATEL |  | 2020-09-09 15:20
2 | WTG-0061-NDG0-0000 | 2075750 | GEARBOX OIL, Particle counter installation | 2019-05-09 12:32 | Closed | GBXOIL | GBXPARTINS | GRAND RIDGE | SCLARK |  | 2019-05-31 09:23
4.2 | WTG-0091-NDGP-0000 | 2075688 | Replace Gearbox Heat Exchanger | 2019-05-09 08:40 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2019-06-28 07:02
2 | WTG-0045-0000 | 2078682 | Add Gearbox Oil | 2019-05-22 17:34 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | GOLDTHWAITE |  | 2019-10-30 13:00
3 | WTG-0100-NDG0-0000 | 2081782 | Gearbox running too hot | 2019-05-31 10:50 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-07-03 07:56
1 | WTG-0226-NDGP-0000 | 2163271 | GEARBOX OIL, Fix oil leak | 2019-12-17 17:30 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NSCHINDLER |  | 2020-02-07 16:06
1 | WTG-0202-0000 | 2092869 | GEARBOX OIL, Fix oil leak - Cooler Oil Plug | 2019-06-14 12:14 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | AHOFFMANN |  | 2019-08-21 16:37
4.2 | WTG-0129-NDGP-0000 | 2094161 | Replace Gearbox Heat Exchanger | 2019-06-20 07:32 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2019-07-16 09:08
1 | WTG-0005-0000 | 2153385 | Drain oil catch basin | 2019-11-19 17:15 | Closed | GBXOIL | BLANK | JUDITH GAP | JUDITHGAP |  | 2020-02-19 14:07
4 | WTG-0011-NDG0-0000 | 2100136 | GEARBOX OIL, Add/Top-Off about 7 Gallons | 2019-07-02 11:36 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-07-02 16:35
5 | WTG-0004-0000 | 2102123 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2019-07-08 16:50 | Closed | GBXOIL | GBXOILCOOL | TURKEY TRACK | JBRILEY |  | 2021-07-12 10:28
1 | WTG-0107-NDG0-0000 | 2102847 | GEARBOX OIL, Fix oil leak | 2019-07-12 07:24 | Cancelled | GBXOIL | GBXOILLEAK | GREXP | GRAND RIDGE |  | 2023-06-29 13:16
1 | WTG-0033-0000 | 2107645 | 2019 Padmount Oil Sample | 2019-07-29 09:46 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-17 14:55
1 | WTG-0009-NDG0-0000 | 2108933 | Gearbox oil pump leak | 2019-07-31 16:13 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | VANTAGE |  | 2019-08-01 09:58
8 | WTG-0017-NDG0-0000 | 2117245 | Add oil additive to main gearbox | 2019-08-25 07:00 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | CSLY |  | 2019-08-27 08:12
2 | WTG-0053-NDG0-0000 | 2117108 | Secondary filter system re-installation | 2019-08-23 15:12 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | JUDITHGAP |  | 2019-08-26 15:55
2 | WTG-0034-NDG0-0000 | 2122607 | gearbox running too hot | 2019-09-04 08:22 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-09-11 08:59
2 | WTG-0051-NDG0-0000 | 2122608 | gearbox running too hot | 2019-09-04 08:23 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-10-04 08:27
2 | WTG-0077-NDG0-0000 | 2122610 | gearbox running too hot | 2019-09-04 08:24 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-10-18 08:15
2 | WTG-0088-NDG0-0000 | 2122612 | gearbox running too hot | 2019-09-04 08:25 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-10-22 17:20
2 | WTG-0066-NDG0-0000 | 2122609 | gearbox running too hot | 2019-09-04 08:24 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-10-14 08:59
2 | WTG-0087-NDG0-0000 | 2122611 | gearbox running too hot | 2019-09-04 08:25 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2019-10-25 08:04
4.2 | WTG-0059-NDGP-0000 | 2126190 | Replace Gearbox Heat Exchanger | 2019-09-12 15:29 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GRATIOT |  | 2019-11-20 06:52
2 | WTG-0002-0000 | 2125916 | GEARBOX OIL, Add/Top-Off | 2019-09-11 09:46 | Closed | GBXOIL | GBXOILADD | GORDON BUTTE | JJUTILA |  | 2019-09-17 16:59
9 | WTG-0301-NDG0-0000 | 2128177 | GEARBOX, Oil Change | 2019-09-23 10:23 | Closed | GBXOIL | GBXOILCHG | BISHOP HILL III | TCASTEEL |  | 2019-10-14 07:53
9 | WTG-0302-NDG0-0000 | 2128178 | GEARBOX, Oil Change | 2019-09-23 10:25 | Closed | GBXOIL | GBXOILCHG | BISHOP HILL III | TCASTEEL |  | 2019-10-24 11:14
5 | WTG-0055A-NDG0-0000 | 2128290 | GEARBOX OIL, Add About 5 Gallons of Amsoil | 2019-09-23 16:47 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-01-17 10:10
3 | SYS-WTG-WIEC | 2129078 | GEARBOX OIL, Oil Sample, Annual | 2019-09-25 12:22 | Closed | GBXOIL | GBXOILSAMP | WILLOW CREEK | MSTONER |  | 2019-09-25 12:24
2 | WTG-0052-NDG0-0000 | 2133100 | GEARBOX OIL, Add/Top-Off | 2019-10-01 16:27 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2019-10-18 09:45
1 | WTG-0061-0000 | 2134418 | PALL Filter Housing Leak | 2019-10-03 14:41 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2020-10-20 08:00
2 | WTG-0027-NDG0-0000 | 2134441 | Oil add 5 gallons | 2019-10-03 15:40 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2019-10-04 16:22
1 | WTG-0059-0000 | 2134417 | rFSA Claim: Leaking pitch tube seals | 2019-10-03 14:40 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-22 11:26
1 | WTG-0052-0000 | 2135721 | GEARBOX OIL, Fix oil leak | 2019-10-06 23:20 | Closed | GBXOIL | GBXOILLEAK | SANTA RITA EAST | MCALVERT |  | 2019-10-14 10:38
2 | WTG-0026-NDGP-0000 | 2037064 | GEARBOX OIL, Fix oil leak | 2019-02-15 09:23 | Closed | GBXOIL | GBXOILLEAK | VANTAGE | VANTAGE |  | 2019-03-18 17:06
2 | WTG-0032-NDGP-0000 | 2049736 | Gear oil pump leaking at flange to filter pot | 2019-03-05 15:52 | Closed | GBXOIL | GBXOILLEAK | FORWARD | FORWARD |  | 2019-03-08 15:45
5 | WTG-0040A-NDG0-0000 | 2052515 | GEARBOX OIL, Add/Top-Off | 2019-03-15 07:17 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2019-03-18 16:04
| WTG-0041-0000 | 2055469 | Gearbox Oil Leak - Bottom Side of GBX | 2019-03-26 09:40 | Closed | GBXOIL | GBXOILLEAK | BETHEL | CWADE |  | 2019-08-14 13:26
1 | WTG-0018-0000 | 2055887 | 2019 Padmount Oil Sample | 2019-03-27 15:26 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2019-09-09 09:43
1 | WTG-0054-0000 | 2064072 | Rear gearbox slipring seal leaking | 2019-04-09 10:45 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | SOSTERLOH |  | 2021-08-30 15:13
5 | WTG-0022-NDG0-0000 | 2103526 | Need fitting on drain valve to secondary filter hose | 2019-07-15 18:34 | Closed | GBXOIL | GBXFILTINS | CAMP SPRINGS I | CAMP SPRINGS |  | 2020-08-14 07:46
1 | WTG-0118-0000 | 2104183 | GEARBOX OIL LEVEL SWITCH REPLACEMENT | 2019-07-18 08:31 | Closed | GBXOIL | GBXOILLEAK | CAMP SPRINGS II | JHAVENS |  | 2020-12-15 09:28
2 | WTG-0110-NDG0-0000 | 2105658 | GEARBOX OIL, Particle counter troubleshooting | 2019-07-24 12:16 | Closed | GBXOIL | GBXPARTTS | TURKEY TRACK | RPPATEL |  | 2019-11-04 16:55
1 | WTG-0032-0000 | 2107652 | 2019 Padmount Oil Sample | 2019-07-29 09:51 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-17 14:50
1 | WTG-0030-0000 | 2107651 | 2019 Padmount Oil Sample | 2019-07-29 09:51 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-21 17:45
1 | WTG-0034-0000 | 2107644 | 2019 Padmount Oil Sample | 2019-07-29 09:45 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-17 15:10
1 | WTG-0031-0000 | 2107646 | 2019 Padmount Oil Sample | 2019-07-29 09:46 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-21 17:45
1 | WTG-0026-0000 | 2107640 | 2019 Padmount Oil Sample | 2019-07-29 09:44 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | GOLDTHWAITE |  | 2021-12-07 11:24
2 | WTG-0065-NDGP-0000 | 2114384 | Replace Leaking Oil Cooler | 2019-08-14 13:21 | Cancelled | GBXOIL | GBXOILCOOL | GRAND RIDGE | GRAND RIDGE |  | 2023-06-29 13:16
8 | WTG-0019-NDG0-0000 | 2117246 | Add oil additive to main gearbox | 2019-08-25 06:00 | Closed | GBXOIL | GBXOILCHG | ORANGEVILLE | CSLY |  | 2019-08-27 08:14
4 | WTG-0212-NDG0-0000 | 2118524 | 5 gallons oil add | 2019-08-27 15:49 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2020-01-08 10:47
2 | WTG-0054-0000 | 2126975 | rFSA: GE Gearbox Additive | 2019-09-17 17:55 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | GOLDTHWAITE |  | 2019-09-25 15:35
2 | WTG-0066-0000 | 2126976 | rFSA: GE Gearbox Additive | 2019-09-17 17:57 | Closed | GBXOIL | GBXOILADD | GOLDTHWAITE | GOLDTHWAITE |  | 2019-09-25 15:35
1 | WTG-0020-0000 | 2127678 | GEARBOX OIL, Fix oil leak | 2019-09-19 15:26 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | GRAND RIDGE |  | 2019-09-19 15:30
5 | WTG-0087-NDG0-0000 | 2133761 | GEARBOX OIL, Add/Top-Off 5gals | 2019-10-02 13:37 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2020-01-17 10:13
1 | WTG-0303-0000 | 2136941 | Belly full of oil | 2019-10-11 19:42 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | AHOFFMANN |  | 2019-10-30 15:21
4 | WTG-0024-0000 | 2138130 | GEARBOX OIL, Add/Top-Off 5 Gallons Amsoil | 2019-10-18 20:51 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-11-18 12:40
5 | WTG-0017-0000 | 2141906 | GEARBOX OIL, Add 5 Gallons | 2019-10-25 16:14 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-01-31 12:46
4 | WTG-0022-NDG0-0000 | 2144483 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2019-10-31 08:10 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2020-05-26 14:24
2 | WTG-0029-NDG0-0000 | 2144517 | gearbox running too hot | 2019-10-31 09:26 | Closed | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2020-01-07 09:25
2 | WTG-0076-NDG0-0000 | 2147492 | GEARBOX OIL, Particle counter troubleshooting | 2019-11-06 10:18 | Closed | GBXOIL | GBXPARTTS | STANTON | RPPATEL |  | 2020-03-04 15:41
1 | WTG-0006-0000 | 2148162 | GEARBOX OIL, Fix oil leak | 2019-11-08 12:13 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | ECOPELAND |  | 2019-11-12 08:49
1 | WTG-0045-NDGP-0000 | 2152461 | GEARBOX OIL, Replace pump coupling | 2019-11-13 13:45 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2019-11-18 12:49
1 | WTG-0004-NDGP-0000 | 2152418 | WTG 4 Oil Sample | 2019-11-13 15:33 | Closed | GBXOIL | GBXOILSAMP | GORDON BUTTE | MPRATER |  | 2019-11-13 16:32
1 | WTG-0007-0000 | 2152451 | GEARBOX OIL, Fix oil leak | 2019-11-13 16:51 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | STAYLOR |  | 2019-11-29 00:44
2 | WTG-0085-0000 | 2164456 | GEARBOX OIL, Add/Top-Off | 2019-12-23 15:24 | Closed | GBXOIL | GBXOILADD | BUCKEYE | CHORN |  | 2020-03-30 07:32
1 | WTG-0G07-0000 | 2154353 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2019-11-22 07:27 | Closed | GBXOIL | GBXOILCOOL | HIGH SHELDON | BEUSCHER |  | 2019-11-25 08:02
1 | WTG-0203-0000 | 2154947 | GEARBOX OIL, Fix oil leak, radiator hose | 2019-11-25 08:33 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2019-12-23 15:42
1 | WTG-0223-0000 | 2159634 | GEARBOX OIL, Fix oil leak | 2019-12-04 16:58 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | AHOFFMANN |  | 2020-10-13 13:39
1 | WTG-0004-NDG0-0000 | 2162292 | WTG 4 Gearoil Level Low Detected | 2019-12-12 16:01 | Closed | GBXOIL | GBXOILLEAK | GORDON BUTTE | MPRATER |  | 2019-12-13 15:34
9 | GREXP | 2163630 | GEARBOX, Oil Change - WTG 112 - Gearbox Express Warranty | 2019-12-18 17:34 | Ready to Schedule | GBXOIL | GBXOILCHG | GEARBOX EXPRESS | MCOURTNEY
2 | WTG-0314-0000 | 2163614 | GEARBOX OIL, Fix oil leak | 2019-12-18 15:47 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | NHEITHOFF |  | 2020-02-17 14:53
1 | WTG-0J06-NDGP-0000 | 2246957 | GEARBOX OIL, Particle counter removal | 2020-07-15 13:53 | Closed | GBXOIL | GBXPARTREM | BEECH RIDGE | RPPATEL |  | 2020-08-27 08:28
5 | WTG-0010-0000 | 2173671 | GEARBOX OIL, Add/Top-Off | 2020-01-15 11:07 | Closed | GBXOIL | GBXOILADD | FORWARD | JWERNER |  | 2020-01-17 11:05
1 | WTG-0112-0000 | 2233256 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2020-06-04 09:54 | Closed | GBXOIL | GBXOILCOOL | BUCKEYE | BUCKEYE |  | 2022-01-03 14:31
1 | WTG-0041-0000 | 2174475 | rFSA Claim: Leaking pitch tube seals | 2020-01-17 15:17 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-21 17:43
1 | WTG-0010-0000 | 2174473 | rFSA Claim: Leaking pitch tube seals | 2020-01-17 15:15 | Cancelled | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-17 12:49
4 | WTG-0058-NDG0-0000 | 2184528 | GEARBOX OIL, Add/Top-Off 5 gals | 2020-02-06 08:00 | Closed | GBXOIL | GBXOILADD | FORWARD | FORWARD |  | 2020-07-20 08:06
2 | WTG-0092-NDG0-0000 | 2184539 | gearbox running too hot | 2020-02-06 08:18 | Cancelled | GBXOIL | GBXOILCOOL | JUDITH GAP | JUDITHGAP |  | 2020-02-27 16:08
1 | WTG-0212-0000 | 2189060 | GEARBOX OIL, Fix oil leak | 2020-02-19 14:34 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NHEITHOFF |  | 2020-10-13 13:37
1 | WTG-0001-0000 | 2189494 | GEARBOX OIL, Fix oil leak | 2020-02-21 15:15 | Closed | GBXOIL | GBXOILLEAK | BETHEL | EAVILA |  | 2020-02-21 16:46
4 | WTG-0030-NDG0-0000 | 2192537 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4.2 | WTG-0100-NDGP-0000 | 2238701 | GEARBOX OIL, Replace oil cooler | 2020-06-26 09:19 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | CBENNETT |  | 2020-10-06 06:51
4 | WTG-0018-0000 | 2140958 | GEARBOX OIL, Add 5 Gallons of Amsoil | 2019-10-23 16:08 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2019-10-25 09:59
4 | WTG-0025-0000 | 2225257 | GEARBOX OIL, Add/Top-Off | 2020-05-20 11:27 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-05-26 14:56
1 | WTG-0119-0000 | 2143239 | GEARBOX OIL, Fix oil leak | 2019-10-28 09:25 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KMCLELAND |  | 2019-10-30 07:37
1 | GBX-000017 | 2148102 | Oil hose replacement | 2019-11-08 07:46 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | CSLY |  | 2019-11-12 08:50
4.1 | WTG-0037-NDGP-0000 | 2153143 | GEARBOX OIL, Secondary filter oil leak | 2019-11-18 16:03 | Closed | GBXOIL | GBXFILTINS | FORWARD | MPEARSON |  | 2021-11-18 09:56
2 | WTG-0032-NDG0-0000 | 2153324 | GEARBOX OIL, Follow Up Oil Sample | 2019-11-19 11:03 | Closed | GBXOIL | GBXOILSAMP | BETHEL | CMORALES |  | 2019-12-05 16:16
1 | WTG-0030-0000 | 2247585 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2020-07-18 17:04 | Closed | GBXOIL | GBXOILCOOL | MCADOO | MCADOO |  | 2020-07-20 14:20
4 | WTG-0097-0000 | 2159603 | GEARBOX OIL, Add oil | 2019-12-04 15:44 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-03-01 14:36
1 | WTG-0025-0000 | 2164192 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2019-12-20 15:00 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | WOLVERINECREEK |  | 2020-01-10 17:22
1 | WTG-0081-0000 | 2174478 | rFSA Claim: Leaking pitch tube seals | 2020-01-17 16:10 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2023-02-22 11:12
1 | WTG-0313-0000 | 2186355 | GEARBOX OIL, Fix oil leak | 2020-02-10 09:29 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | RKUDERA |  | 2020-10-13 12:53
1 | WTG-0013-0000 | 2191300 | ZF Shim Retro/LOTO Verification | 2020-02-27 09:05 | Closed | GBXOIL | BLANK | UPSTREAM | PRAIRIE BREEZE2 |  | 2020-03-11 12:07
4 | WTG-0020-NDG0-0000 | 2192527 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0021-NDG0-0000 | 2192528 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0022-NDG0-0000 | 2192529 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0023-NDG0-0000 | 2192530 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0024-NDG0-0000 | 2192531 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0025-NDG0-0000 | 2192532 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0037-NDG0-0000 | 2192544 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0038-NDG0-0000 | 2192545 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0039-NDG0-0000 | 2192546 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0040-NDG0-0000 | 2192547 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0041-NDG0-0000 | 2192548 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0042-NDG0-0000 | 2192549 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0043-NDG0-0000 | 2192550 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0044-NDG0-0000 | 2192551 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0026-NDG0-0000 | 2192533 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0027-NDG0-0000 | 2192534 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0028-NDG0-0000 | 2192535 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0029-NDG0-0000 | 2192536 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0031-NDG0-0000 | 2192538 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0032-NDG0-0000 | 2192539 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0033-NDG0-0000 | 2192540 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0034-NDG0-0000 | 2192541 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0035-NDG0-0000 | 2192542 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0036-NDG0-0000 | 2192543 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0082-NDG0-0000 | 2192589 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0079-NDG0-0000 | 2192586 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0080-NDG0-0000 | 2192587 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0081-NDG0-0000 | 2192588 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0083-NDG0-0000 | 2192590 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0084-NDG0-0000 | 2192591 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0088-NDG0-0000 | 2192595 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0085-NDG0-0000 | 2192592 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0086-NDG0-0000 | 2192593 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0087-NDG0-0000 | 2192594 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0089-NDG0-0000 | 2192596 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0090-NDG0-0000 | 2192597 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0091-NDG0-0000 | 2192598 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0092-NDG0-0000 | 2192599 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0093-NDG0-0000 | 2192600 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0094-NDG0-0000 | 2192601 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0098-NDG0-0000 | 2192605 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0095-NDG0-0000 | 2192602 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0096-NDG0-0000 | 2192603 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0097-NDG0-0000 | 2192604 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0099-NDG0-0000 | 2192606 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0100-NDG0-0000 | 2192607 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0101-NDG0-0000 | 2192608 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0102-NDG0-0000 | 2192609 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0103-NDG0-0000 | 2192610 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
4 | WTG-0104-NDG0-0000 | 2192611 | 2020 Gearbox Oil Samples | 2020-01-08 11:44 | Closed | GBXOIL |  | BETHEL | SLEWALLEN |  | 2021-02-09 10:39
1 | WTG-0075-0000 | 2222249 | Replace Gearbox Hose | 2020-05-12 15:25 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2020-07-08 13:20
2 | WTG-0061-0000 | 2222641 | Add Oil to Gearbox | 2020-05-13 17:04 | Closed | GBXOIL | GBXOILADD | BUCKEYE | NSCHMEIDLER |  | 2020-07-27 18:06
2 | WTG-0064-0000 | 2225412 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2020-05-21 15:22 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCRESSWELL |  | 2020-07-06 14:39
1 | WTG-0060-0000 | 2235830 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2020-06-13 11:54 | Closed | GBXOIL | GBXOILCOOL | SANTA RITA EAST | SANTA RITA EAST |  | 2020-07-06 09:34
4.2 | WTG-0081-0000 | 2201089 | Oil Cooler Leak | 2020-03-25 15:29 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | CBRUCE |  | 2020-03-27 09:42
1 | WTG-003W-0000 | 2201348 | GEARBOX OIL, Replace oil pump motor | 2020-03-26 13:13 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | ABRADSHAW |  | 2020-03-31 11:53
1 | WTG-0041-0000 | 2208588 | GEARBOX OIL, Fix oil leak | 2020-04-16 14:52 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2020-05-01 16:14
5 | GBX-HAN-EH802C-004/LM0003 | 2209759 | WTG011 - Check filter for debris | 2020-04-22 14:41 | Closed | GBXOIL | BLANK | BUFFALO MOUNT | SCLARK |  | 2020-10-15 12:33
1 | WTG-0040-0000 | 2217531 | GEARBOX OIL, Fix oil leak | 2020-04-30 15:23 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH |  | 2020-05-01 16:09
2 | WTG-0033-NDGP-0000 | 2237932 | GEARBOX OIL, Particle counter removal | 2020-06-24 14:33 | Closed | GBXOIL | GBXPARTREM | GUNSIGHT | RPPATEL |  | 2021-04-07 22:05
2 | WTG-0036-NDGP-0000 | 2237934 | GEARBOX OIL, Particle counter removal | 2020-06-24 14:37 | Closed | GBXOIL | GBXPARTREM | GUNSIGHT | RPPATEL |  | 2020-07-09 15:38
4.2 | WTG-0103-0000 | 2237938 | GEARBOX OIL, Replace oil cooler | 2020-06-24 14:47 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCRESSWELL |  | 2020-08-27 07:33
2 | WTG-0021-0000 | 2237930 | GEARBOX OIL, Fix oil leak - Pitch Tube Seal WC# 3801048 | 2020-06-24 14:26 | Cancelled | GBXOIL | GBXOILLEAK | UPSTREAM | NHEITHOFF |  | 2023-04-13 10:12
1 | WTG-0016-0000 | 2247977 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:25 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-09-14 16:32
2 | WTG-0035-NDGP-0000 | 2237933 | GEARBOX OIL, Particle counter removal | 2020-06-24 14:36 | Closed | GBXOIL | GBXPARTREM | GUNSIGHT | RPPATEL |  | 2020-09-24 16:35
1 | WTG-0115-0000 | 2245777 | GEARBOX OIL, Fix oil leak | 2020-07-10 15:48 | Closed | GBXOIL | GBXOILLEAK | SCEXP | SPRINGCANYON |  | 2020-12-18 15:58
1 | WTG-0006-0000 | 2247970 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:22 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-08-25 14:10
1 | WTG-0008-0000 | 2247971 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:23 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-08-25 14:10
1 | WTG-0009-0000 | 2247972 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:23 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-08-27 09:10
1 | WTG-0010-0000 | 2247973 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:24 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-09-04 10:33
1 | WTG-0011-0000 | 2247974 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:24 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-08-27 09:10
1 | WTG-0014-0000 | 2247975 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:24 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-08-28 15:43
1 | WTG-0015-0000 | 2247976 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:24 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-09-02 09:44
1 | WTG-0029-0000 | 2247987 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:28 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-03-19 07:45
1 | WTG-0031-0000 | 2247988 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:28 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-01-28 15:28
1 | WTG-0032-0000 | 2247989 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:29 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-02 08:32
1 | WTG-0033-0000 | 2247990 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:29 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-09-17 13:57
1 | WTG-0035-0000 | 2247991 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:29 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-02 15:50
1 | WTG-0040-0000 | 2247995 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:30 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-26 09:06
1 | WTG-0037-0000 | 2247992 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:29 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-23 08:46
1 | WTG-0038-0000 | 2247993 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:30 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-07 09:13
1 | WTG-0039-0000 | 2247994 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:30 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-09-23 11:08
1 | WTG-0041-0000 | 2247996 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:31 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-03-25 08:48
1 | WTG-0042-0000 | 2247997 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:32 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2021-01-25 08:56
1 | WTG-0045-0000 | 2247998 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:32 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-07 14:24
1 | WTG-0046-0000 | 2247999 | GEARBOX OIL, Fix oil leak | 2020-07-20 10:32 | Closed | GBXOIL | GBXOILLEAK | BETHEL | DWOOD |  | 2020-10-20 15:23
1 | WTG-0011-NDG0-0000 | 2248468 | Reinstall secondary filter system | 2020-07-22 17:23 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | JUDITHGAP |  | 2020-07-23 13:29
3 | WTG-0044-NDG0-0000 | 2256962 | gearbox coupler inspection port | 2020-08-07 17:03 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2020-10-22 15:58
3 | WTG-0053-NDG0-0000 | 2256963 | gearbox coupler inspection port | 2020-08-07 17:03 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | JUDITHGAP |  | 2020-08-14 09:03
4 | WTG-0095-NDGP-0000 | 2257726 | CCJensen Leaking | 2020-08-11 12:12 | Closed | GBXOIL | GBXFILTINS | FORWARD | KLEFFELMAN |  | 2023-01-30 10:54
1 | WTG-0202-0000 | 2259656 | GEARBOX OIL, Fix oil leak | 2020-08-18 16:44 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | JSTAHLECKER |  | 2020-10-13 13:37
4.2 | WTG-0076-NDGP-0000 | 2274375 | GEARBOX OIL, Replace oil cooler | 2020-08-26 10:41 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | JCRESSWELL |  | 2020-11-04 06:49
2 | WTG-0017-NDGP-0000 | 2284852 | GEARBOX OIL, Secondary filter system element change | 2020-09-15 08:26 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | JUDITHGAP |  | 2020-12-17 16:58
1 | WTG-0041-0000 | 2909328 | GEARBOX OIL, Hose leak | 2022-04-06 12:54 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2023-03-20 12:00
4.2 | WTG-0217-0000 | 2286911 | Re-Install secondary filtration system on gearbox oil | 2020-09-26 08:02 | Ready to Schedule | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2
5 | WTG-0227-0000 | 2286915 | Install secondary filtration system on gearbox oil | 2020-09-26 08:04 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-08-15 12:29
1 | WTG-0304-0000 | 2247701 | GEARBOX OIL, Fix oil leak | 2020-07-20 08:24 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | AHOFFMANN |  | 2020-08-25 11:17
3 | WTG-0001-NDG0-0000 | 2253049 | gearbox coupler inspection port | 2020-08-01 16:53 | Closed | GBXOIL | GBXOILADD | GORDON BUTTE | JUDITHGAP |  | 2020-08-26 08:17
3 | WTG-0002-NDG0-0000 | 2253050 | gearbox coupler inspection port | 2020-08-01 16:55 | Closed | GBXOIL | GBXOILADD | GORDON BUTTE | JUDITHGAP |  | 2021-08-27 08:56
3 | WTG-0003-NDG0-0000 | 2253051 | gearbox coupler inspection port | 2020-08-01 16:56 | Closed | GBXOIL | GBXOILADD | GORDON BUTTE | JUDITHGAP |  | 2021-05-19 08:06
3 | WTG-0004-NDG0-0000 | 2253052 | gearbox coupler inspection port | 2020-08-01 16:59 | Closed | GBXOIL | GBXOILADD | GORDON BUTTE | JUDITHGAP |  | 2021-05-17 08:21
3 | WTG-0005-NDG0-0000 | 2253053 | gearbox coupler inspection port | 2020-08-01 16:59 | Closed | GBXOIL | GBXOILADD | GORDON BUTTE | JUDITHGAP |  | 2020-08-13 08:11
3 | WTG-0006-NDG0-0000 | 2253054 | gearbox coupler inspection port | 2020-08-01 17:00 | Closed | GBXOIL | GBXOILADD | GORDON BUTTE | JUDITHGAP |  | 2021-08-20 08:16
1 | WTG-0227-0000 | 2324365 | GEARBOX OIL, Fix oil leak | 2020-12-11 12:27 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | RKUDERA |  | 2021-05-13 15:32
4 | WTG-0211A-0000 | 2258545 | GEARBOX OIL, Replace oil pump | 2020-08-13 16:17 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2020-08-19 11:40
1 | WTG-0034-0000 | 2281122 | Pitch Tube Seal & O-ring Replacement | 2020-09-01 17:24 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MMCCABE |  | 2021-12-03 09:56
1 | WTG-0034-0000 | 2281123 | High Speed Shaft Seal Replacement | 2020-09-01 17:26 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MMCCABE |  | 2021-12-03 10:25
1 | WTG-0034-0000 | 2281124 | Oil Pump & Motor Inversion | 2020-09-01 17:27 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MMCCABE |  | 2021-09-09 12:25
5 | WTG-0221-0000 | 2286912 | Install secondary filtration system on gearbox oil | 2020-09-26 08:04 | Ready to Schedule | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2
5 | WTG-0225-0000 | 2286913 | Install secondary filtration system on gearbox oil | 2020-09-26 08:04 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-12-10 07:36
5 | WTG-0226-0000 | 2286914 | Install secondary filtration system on gearbox oil | 2020-09-26 08:04 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-08-15 12:29
5 | WTG-0228-0000 | 2286916 | Install secondary filtration system on gearbox oil | 2020-09-26 08:04 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-08-15 12:29
5 | WTG-0229-0000 | 2286917 | Install secondary filtration system on gearbox oil | 2020-09-26 08:05 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2024-07-09 13:03
1 | WTG-0058-0000 | 2292466 | EM: Gearbox oil pressure too low | 2020-10-06 15:05 | Closed | GBXOIL |  | GRATIOT | JDETWILER |  | 2020-10-08 06:54
2 | WTG-0045-NDGP-0000 | 2293013 | GEARBOX OIL, Replace gbx oil pump | 2020-10-08 14:00 | Closed | GBXOIL | GBXOILCOOL | FORWARD | FORWARD |  | 2020-10-14 12:14
5 | WTG-0003A-0000 | 2295279 | Flip Oil Thermal Bypass Valve | 2020-10-16 12:54 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2020-10-20 11:03
5 | WTG-0313-NDG0-0000 | 2311087 | REPLACE FAILED CJC Secondary Oil Filtration System | 2020-11-10 14:46 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2023-02-10 09:13
5 | WTG-0314-NDG0-0000 | 2311088 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:47 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2021-05-13 15:30
5 | WTG-0318-NDG0-0000 | 2311092 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:47 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-09-03 14:00
1 | WTG-0051-0000 | 2311154 | GEARBOX OIL, Fix oil leak | 2020-11-11 07:45 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | BEUSCHER |  | 2020-11-16 07:58
5 | WTG-0311-NDG0-0000 | 2311085 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:46 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-09-03 14:00
5 | WTG-0306-NDG0-0000 | 2311080 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:44 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-07-16 15:12
5 | WTG-0307-NDG0-0000 | 2311081 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:44 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-08-27 12:16
5 | WTG-0301-NDG0-0000 | 2311073 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:40 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2023-10-31 16:18
5 | WTG-0302-NDG0-0000 | 2311075 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:43 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2021-11-03 15:44
5 | WTG-0303-NDG0-0000 | 2311076 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:43 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-08-27 12:16
5 | WTG-0312-NDG0-0000 | 2311086 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:46 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-09-03 14:00
5 | WTG-0315-NDG0-0000 | 2311089 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:47 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-07-09 13:03
5 | WTG-0316-NDG0-0000 | 2311090 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:47 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-09-13 12:32
5 | WTG-0317-NDG0-0000 | 2311091 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:47 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2025-02-04 07:36
5 | WTG-0304-NDG0-0000 | 2311077 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:43 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-12-31 15:09
5 | WTG-0305-NDG0-0000 | 2311079 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:43 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-12-31 15:09
1 | WTG-0004-0000 | 2336456 | GEARBOX OIL, Fix oil leak | 2021-01-07 14:20 | Closed | GBXOIL | GBXOILLEAK | MCADOO | AHILL2 |  | 2021-01-07 14:24
2 | WTG-0019-NDGP-0000 | 2346152 | GEARBOX OIL, Particle counter troubleshooting | 2021-01-29 11:28 | Closed | GBXOIL | GBXPARTTS | WILLOW CREEK | RPPATEL |  | 2022-03-08 14:01
4 | WTG-0059-0000 | 2372088 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
1 | WTG-0208-0000 | 2286740 | GEARBOX OIL, Fix oil leak, Nanjing hose | 2020-09-25 09:07 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | PRAIRIE BREEZE2 |  | 2021-08-30 15:01
4 | WTG-0026-0000 | 2291169 | GEARBOX OIL, Add about 5 gallons | 2020-10-02 17:02 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2020-10-20 10:59
1 | WTG-0059-0000 | 2295100 | PALL Filter Housing Leak | 2020-10-15 15:24 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | GOLDTHWAITE |  | 2021-12-07 11:24
1 | WTG-0085-NDG0-0000 | 2438897 | GEARBOX OIL, Fix oil leak | 2021-06-17 16:15 | Closed | GBXOIL | GBXOILLEAK | MCADOO | LMARSHALL |  | 2021-06-21 09:09
5 | WTG-0308-NDG0-0000 | 2311082 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:44 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-07-30 10:47
5 | WTG-0309-NDG0-0000 | 2311083 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:45 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-06-05 13:31
5 | WTG-0310-NDG0-0000 | 2311084 | Install CJC Secondary Oil Filtration System | 2020-11-10 14:45 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2021-11-03 15:44
5 | WTG-0319-NDG0-0000 | 2311094 | CJC Filter System, Motor Locked | 2020-11-10 14:47 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-09-13 12:32
5 | WTG-0320-NDG0-0000 | 2311095 | Install CJC Secondary Oil Filtration System/90 Degree Fitting | 2020-11-10 14:48 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | PRAIRIE BREEZE2 |  | 2024-09-03 14:00
5 | WTG-0028-NDGP-0000 | 2312995 | GEARBOX OIL, Replace oil pump | 2020-11-18 17:23 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | SENGLAND |  | 2021-04-08 09:52
1 | WTG-0014-NDGP-0000 | 2361918 | GEARBOX OIL, Fix oil leak | 2021-02-08 20:08 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | ZMILLER |  | 2021-02-09 15:38
4 | WTG-0051-0000 | 2372080 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0052-0000 | 2372081 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0053-0000 | 2372082 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0054-0000 | 2372083 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0055-0000 | 2372084 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0056-0000 | 2372085 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0057-0000 | 2372086 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0058-0000 | 2372087 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0060-0000 | 2372089 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0061-0000 | 2372090 | 2021 Gearbox Oil Samples | 2021-02-09 11:33 | Closed | GBXOIL |  | BETHEL | NCLOYD |  | 2022-01-04 15:24
4 | WTG-0004-0000 | 2374407 | GEARBOX OIL, Add about 5 Gallons | 2021-02-18 16:37 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-06-18 07:50
4 | WTG-0097-NDGP-0000 | 2376099 | Gear oil pump is leaking. Spider gear | 2021-02-24 15:47 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2021-03-01 14:59
1 | BMEC-WTG-011 | 2374270 | wtg011 low oil level | 2021-02-17 11:48 | Closed | GBXOIL |  | BUFFALO MOUNT | CLAWSON |  | 2021-03-03 13:16
5 | WTG-0072A-0000 | 2374308 | 5 gallons oil | 2021-02-17 14:49 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2021-10-05 06:36
4 | WTG-0081-0000 | 2380281 | GEARBOX OIL, Add/Top-Off 5 Gallons/Clean up | 2021-03-04 07:24 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2021-07-15 06:35
5 | WTG-0074-0000 | 2380923 | GEARBOX OIL, Fix oil leak | 2021-03-04 16:04 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | DTILLIS |  | 2024-11-08 15:06
5 | WTG-0212-0000 | 2380714 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2021-03-04 13:39 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-04-05 06:50
1 | WTG-0085-0000 | 2383497 | Clean oil leak | 2021-03-16 08:25 | Closed | GBXOIL | GBXOILLEAK | SANTA RITA EAST | CPERRY |  | 2021-09-01 08:43
1 | WTG-0209-NDGP-0000 | 2384054 | GEARBOX OIL, Fix oil leak | 2021-03-18 16:15 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | DGORDON |  | 2021-05-13 15:32
2 | WTG-0029-0000 | 2394671 | GEARBOX OIL, Fix oil leak | 2021-03-31 12:07 | Closed | GBXOIL | GBXOILLEAK | TURKEY TRACK | JBRILEY |  | 2023-09-15 15:05
1 | WTG-0154-NDGP-0000 | 2394102 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2021-03-30 08:31 | Closed | GBXOIL | GBXOILCOOL | CAMP SPRINGS II | BEDEN |  | 2023-05-09 11:55
1 | WTG-0007-NDG0-0000 | 2399556 | GEARBOX OIL, Fix oil leak | 2021-04-07 13:58 | Cancelled | GBXOIL | GBXOILLEAK | GORDON BUTTE | JUDITHGAP |  | 2021-08-18 16:48
9 | WTG-0068-NDG0-0000 | 2402294 | GEARBOX, Oil Change | 2021-04-21 13:14 | Closed | GBXOIL | GBXOILCHG | BLOOMING GROVE | DGEORGE |  | 2021-04-30 10:24
9 | WTG-0016-NDG0-0000 | 2402296 | GEARBOX, Oil Change | 2021-04-21 13:31 | Closed | GBXOIL | GBXOILCHG | BLOOMING GROVE | DGEORGE |  | 2021-04-28 10:39
5 | WTG-0240-0000 | 2407001 | GEARBOX OIL, Fix oil leak | 2021-05-02 11:37 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NMCFARLAND |  | 2021-11-03 15:43
3 | WTG-0007-0000 | 2411808 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL |  | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
3 | WTG-0013-0000 | 2411810 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL |  | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
3 | WTG-0021-0000 | 2411811 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL |  | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
3 | WTG-0073-0000 | 2411812 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL |  | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
3 | WTG-0075-0000 | 2411814 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL |  | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
3 | WTG-0076-0000 | 2411815 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL |  | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
3 | WTG-0077-0000 | 2411817 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL |  | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
3 | WTG-0093-0000 | 2411819 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL |  | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
3 | WTG-0096-0000 | 2411820 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL |  | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
3 | WTG-0098-0000 | 2411822 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL |  | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
3 | WTG-0099-0000 | 2411823 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL |  | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
3 | WTG-0109-0000 | 2411825 | 2021_DEUEL HARVEST_RENENE_GBX OIL CHANGE (GE 2.3-90m) x12 | 2021-05-07 14:00 | Closed | GBXOIL |  | DEUEL HARVEST | KBJORKLUND |  | 2021-05-25 14:36
2 | WTG-0022-0000 | 2418786 | GEARBOX OIL, Replace oil pump | 2021-05-13 16:08 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2021-05-28 09:04
1 | WTG-0111-0000 | 2429745 | GEARBOX OIL, Fix oil leak | 2021-06-05 11:21 | Closed | GBXOIL | GBXOILLEAK | BETHEL | ZMCCASLAND |  | 2023-06-06 13:04
2 | WTG-0077-NDB0-0000 | 2929986 | CMS Main Bearing Borescope | 2022-05-11 10:47 | Closed | CMS | CMSMBBORE | THUNDERHEAD | AMITCHELL |  | 2022-06-15 15:52
1 | WTG-0008-NDG0-0000 | 2470538 | GEARBOX OIL, Add/Top-Off | 2021-07-29 12:39 | Closed | GBXOIL | GBXOILADD | ORANGEVILLE | JROULIER |  | 2021-10-05 14:22
5 | WTG-0076-0000 | 2476117 | Gearbox vibration | 2021-08-09 14:23 | Closed | CMS | BLANK | SANTA RITA EAST | CBILLIG |  | 2021-09-22 14:51
5 | WTG-0088-0000 | 2476121 | Gearbox vibration | 2021-08-09 14:52 | Closed | CMS | BLANK | SANTA RITA EAST | CBILLIG |  | 2021-08-17 15:24
2 | WTG-0215-0000 | 2577016 | GEARBOX OIL, Fix oil leak | 2021-09-10 08:17 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | RKUDERA |  | 2022-09-28 14:19
4.1 | WTG-0027-NDGP-0000 | 2616108 | Replace gear oil pump spider insert | 2021-10-12 14:06 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2022-03-18 06:55
2 | WTG-0050-0000 | 2616556 | MAIN BEARING, Main bearing borescope inspection | 2021-10-14 11:54 | Closed | CMS | CMSMBBORE | MAVERICK | CBILLIG |  | 2023-03-27 11:57
2 | WTG-0012-0000 | 2616577 | Small Winergy inspection port Gasket needed | 2021-10-14 13:29 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2022-08-29 10:17
4 | WTG-0039-0000 | 2616579 | GEARBOX OIL, Replace oil hoses, orange and yellow Winergy | 2021-10-14 12:57 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2022-09-14 09:36
4 | WTG-0032-0000 | 2617516 | Secondary filter leak | 2021-10-18 10:04 | Closed | GBXOIL | GBXFILTELEM | FORWARD | KLEFFELMAN |  | 2022-04-26 09:01
1 | WTG-0004-0000 | 2624081 | GEARBOX OIL, Fix oil leak hose replacement | 2021-10-26 18:15 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JHAVENS |  | 2021-12-09 15:59
2 | WTG-0064-0000 | 2929983 | GEARBOX OIL, Add/Top-Off | 2022-05-11 10:37 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | TWIEDEMEIER |  | 2022-11-04 12:24
2 | GBX-00062 | 2632150 | CMS Gearbox Borescope | 2021-11-03 12:46 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2022-09-12 12:06
2 | WTG-0026-0000 | 2633706 | Gearbox borescope | 2021-11-08 08:42 | Closed | CMS | CMSGBXBORE | BETHEL | JGARLAND |  | 2021-11-08 14:57
4 | WTG-0038-0000 | 2644358 | GEARBOX OIL, Add/Top-Off | 2021-11-10 12:31 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2021-11-11 12:44
4 | WTG-0038-0000 | 2644359 | Replace gearbox oil pump coupler | 2021-11-10 12:33 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JLAWRENCE |  | 2021-11-11 12:44
2 | WTG-0021-NDGP-0000 | 2644966 | replace oil filter | 2021-11-12 11:58 | Closed | GBXOIL | GBXFILTELEM | BLOOMING GROVE | MWILSON |  | 2021-11-15 08:55
2 | WTG-0024-NDGP-0000 | 2644967 | replace oil filter | 2021-11-12 12:05 | Closed | GBXOIL | GBXFILTELEM | BLOOMING GROVE | MWILSON |  | 2021-11-15 08:55
2 | GBX-00064 | 2645291 | CMS Gearbox Borescope | 2021-11-15 13:54 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | CBILLIG |  | 2021-12-14 08:34
4 | WTG-0021-0000 | 2645408 | Secondary filter leak | 2021-11-15 16:17 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2022-04-10 17:24
2 | WTG-0038-0000 | 2651883 | GENERATOR, Bearing Grease Flush | 2021-11-30 12:50 | Closed | CMS | GENBRGFLUSH | UPSTREAM | CBILLIG |  | 2022-08-31 16:59
2 | WTG-0053-0000 | 2652831 | CMS Gearbox Borescope | 2021-12-01 10:02 | Closed | CMS | CMSGBXBORE | BETHEL | MHERRERA |  | 2021-12-02 15:21
2 | WTG-0008-0000 | 2653856 | CMS Main Bearing Borescope | 2021-12-01 16:18 | Closed | CMS | CMSMBBORE | MCADOO | TRUDE |  | 2021-12-03 09:23
2 | WTG-0006-ND00-0000 | 2655654 | CMS HSS Check | 2021-12-03 15:44 | Cancelled | CMS | CMSHSS | GORDON BUTTE | CBILLIG |  | 2022-01-27 16:03
2 | WTG-0004-0000 | 2679558 | CMS Main Bearing Borescope | 2021-12-17 14:14 | Closed | CMS | CMSMBBORE | MCADOO | TRUDE |  | 2022-01-06 13:48
4 | WTG-0039-0000 | 2927581 | Change primary GBX oil filter | 2022-05-03 13:57 | Closed | GBXOIL | GBXFILTELEM | FORWARD | JLAWRENCE |  | 2022-05-10 09:34
2 | GBX-00028 | 2717470 | CMS Gearbox Borescope | 2022-01-11 11:08 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2022-06-28 12:23
4.2 | WTG-0082-0000 | 2716380 | GBX Hose Replacement | 2022-01-07 08:09 | Cancelled | GBXOIL | GBXOILADD | FORWARD | DMONROE |  | 2022-07-05 08:31
1 | WTG-0011-0000 | 2379655 | GEARBOX OIL, Secondary filter system not working/ UPS batteries | 2021-03-03 04:30 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | SBAY |  | 2023-02-13 14:26
1 | WTG-003W-0000 | 2379504 | PALL Filter Housing Leak | 2021-03-02 14:01 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH |  | 2022-03-02 13:53
1 | WTG-0007-0000 | 2380264 | WTG007 - GEARBOX OIL, Fix oil leak in hub | 2021-03-04 06:11 | Closed | GBXOIL | GBXOILLEAK | BUFFALO MOUNT | SBAY |  | 2021-04-06 10:23
4 | WTG-0065-NDGP-0000 | 2393988 | Replace oil pump spider gear | 2021-03-30 07:03 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2021-08-19 06:47
1 | WTG-0043-NDGP-0000 | 2405593 | GEARBOX OIL, Fix oil leak | 2021-04-28 12:46 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2021-04-29 07:04
2 | WTG-0035-0000 | 2427236 | GEARBOX OIL, Fix oil leak | 2021-06-01 16:56 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | NMCFARLAND |  | 2022-08-31 17:01
4 | WTG-0057-0000 | 2465221 | Replace blue hose on gearbox | 2021-07-12 13:27 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2022-06-24 07:09
2 | WTG-0335-NDG0-0000 | 2465674 | GEARBOX OIL, Secondary filter system element change | 2021-07-14 15:03 | Cancelled | GBXOIL | GBXFILTELEM | BISHOP HILL III | KCOOPER |  | 2023-05-16 14:51
1 | WTG-0010-0000 | 2468593 | GEARBOX OIL, Fix oil leak | 2021-07-23 16:46 | Cancelled | GBXOIL | GBXOILLEAK | JUDITH GAP | PMAGER |  | 2022-08-04 16:05
9 | WTG-039E-0000 | 2473768 | GEARBOX, Oil Change | 2021-08-03 15:47 | Closed | GBXOIL | GBXOILCHG | GOLDTHWAITE | ZMILLER |  | 2021-08-26 08:33
1 | WTG-0031-0000 | 2477210 | GEARBOX OIL, Fix oil leak | 2021-08-11 19:59 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | LHATVELDT |  | 2021-09-07 08:22
5 | WTG-0022-0000 | 2516237 | Snap Ring Inspection | 2021-08-17 16:36 | Cancelled | CMS | BLANK | UPSTREAM | CBILLIG |  | 2022-09-01 16:00
1 | WTG-0009-NDG0-0000 | 2575086 | GEARBOX OIL, Secondary filter system Vent Hose Replacement | 2021-09-03 14:15 | Closed | GBXOIL | GBXFILTINS | VANTAGE | CCUSACK |  | 2022-06-01 15:28
2 | WTG-0038-0000 | 2575705 | CMS Generator Bearing Check | 2021-09-07 11:44 | Closed | CMS | CMSGENB | UPSTREAM | CBILLIG |  | 2021-11-30 12:46
5 | WTG-0003-0000 | 2575724 | CMS Generator Bearing Check | 2021-09-07 11:51 | Closed | CMS | CMSGENB | UPSTREAM | CBILLIG |  | 2022-02-10 12:00
1 | WTG-0I08-NDGP-0000 | 2578343 | Gearbox oil pressure too low | 2021-09-15 07:23 | Closed | GBXOIL | GBXOILCOOL | HIGH SHELDON | CSLY |  | 2021-09-16 14:29
4 | WTG-0210A-0000 | 2578787 | GEARBOX OIL, Replace gbx hoses | 2021-09-16 13:24 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2022-01-24 09:09
1 | WTG-0350-0000 | 2578929 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2021-09-17 08:45 | Closed | GBXOIL | GBXOILCOOL | BISHOP HILL III | MBELCHER |  | 2021-09-23 09:18
2 | WTG-0077-0000 | 2581092 | CMS HSS Check | 2021-09-24 11:32 | Cancelled | CMS | CMSHSS | DEUEL HARVEST | CBILLIG |  | 2022-09-21 17:11
5 | WTG-0072A-0000 | 2609181 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2021-10-04 11:31 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2021-10-05 06:42
4.2 | WTG-0022-NDG0-0000 | 2609581 | Gbx hose replacement | 2021-10-04 13:47 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2022-04-08 09:25
4 | WTG-0022-NDGP-0000 | 2609583 | Secondary oil filter leak | 2021-10-04 13:59 | Closed | GBXOIL | GBXFILTINS | FORWARD | KLEFFELMAN |  | 2022-04-08 09:26
2 | WTG-0045-0000 | 2613915 | CMS Inspection per GE request | 2021-10-06 10:31 | Closed | CMS | CMSINSP | BLOOMING GROVE | CBILLIG |  | 2022-12-15 12:12
4 | WTG-0032-0000 | 2617515 | 5 gallons oil add | 2021-10-18 10:01 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2022-04-26 09:00
5 | WTG-00A5-0000 | 2628617 | CMS HSS Check | 2021-10-29 13:36 | Closed | CMS | CMSHSS | COYOTE RIDGE | CBILLIG |  | 2022-01-03 09:32
5 | WTG-00E1-0000 | 2628619 | CMS Main Bearing Check | 2021-10-29 13:58 | Closed | CMS | CMSMB | TATANKA RIDGE | CBILLIG |  | 2022-01-03 09:32
2 | WTG-00I2-0000 | 2628625 | CMS Gearbox Borescope | 2021-10-29 14:14 | Closed | CMS | CMSGBXBORE | TATANKA RIDGE | CBILLIG |  | 2022-01-03 09:33
2 | WTG-0049-0000 | 2643930 | Gearbox oil pressure too low | 2021-11-08 15:56 | Closed | GBXOIL | GBXOILADD | WAKE 1 | GDELAFUENTE |  | 2021-11-09 12:10
2 | WTG-00B3-0000 | 2645566 | CMS Main Bearing Borescope | 2021-11-16 10:41 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | CBILLIG |  | 2022-03-03 15:26
4 | WTG-0011-NDGP-0000 | 2646999 | Replace oil pump seal | 2021-11-18 10:05 | Closed | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | MCONDON |  | 2021-12-17 15:49
9 | WTG-0042-0000 | 2650301 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | ENGLISH FARMS | CMORALES |  | 2022-01-10 11:44
9 | WTG-0031-0000 | 2650302 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | ENGLISH FARMS | CMORALES |  | 2022-01-10 11:55
9 | WTG-0073-0000 | 2650303 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | ENGLISH FARMS | CMORALES |  | 2022-01-10 11:29
9 | WTG-0029-0000 | 2650304 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | ENGLISH FARMS | CMORALES |  | 2024-09-20 10:49
9 | WTG-0470-0000 | 2650305 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
9 | WTG-0440-0000 | 2650306 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
9 | WTG-0446-0000 | 2650307 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
9 | WTG-0481-0000 | 2650308 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
9 | WTG-0449-0000 | 2650309 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
9 | WTG-0456-0000 | 2650310 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
9 | WTG-0421-0000 | 2650311 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | WHISPERING WILL | CMORALES |  | 2024-06-14 09:51
5 | WTG-0012-0000 | 2650276 | GEARBOX OIL, Fix oil leak around lube pump | 2021-11-23 15:08 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2022-08-29 10:19
9 | WTG-0015-0000 | 2650278 | GEARBOX, Oil Change | 2021-11-23 15:25 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | CMORALES |  | 2024-01-31 09:05
5 | WTG-0028-NDB0-0000 | 2680694 | CMS Trouble Shoot (Invenergy request, non-GE) | 2021-12-20 15:32 | Cancelled | CMS | CMSTRBLSHOOT | BLOOMING GROVE | CBILLIG |  | 2022-02-07 15:05
1 | GBX-000027 | 2689624 | Low oil pressure | 2021-12-31 10:11 | Closed | GBXOIL | EM52 | ORANGEVILLE | BMEST |  | 2022-02-22 13:38
2 | WTG-0072-0000 | 2691458 | GEARBOX OIL, Add/Top-Off | 2022-01-04 08:57 | Closed | GBXOIL | GBXOILADD | MIAMI 1 | JGENN |  | 2023-11-09 07:43
1 | WTG-0020-0000 | 2717577 | GEARBOX OIL, Secondary filter system installation | 2022-01-11 16:54 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | LHATVELDT |  | 2022-01-13 10:57
4 | WTG-0089-0000 | 2804570 | GEARBOX OIL, Secondary filter system element change | 2022-02-22 07:28 | Closed | GBXOIL | GBXFILTELEM | FORWARD | DMONROE |  | 2022-08-29 10:20
5 | WTG-0061-0000 | 2802251 | GEARBOX OIL, Secondary filter system element change | 2022-02-11 09:59 | Closed | GBXOIL | GBXFILTELEM | FORWARD | TBUYESKE |  | 2022-06-10 08:53
2 | WTG-0010-NDG0-0000 | 2736549 | Add Amsoil | 2022-01-24 09:59 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2022-08-30 09:36
3.1 | SITE-PWRC | 2737328 | CMS Vibration | 2022-01-25 14:12 | Cancelled | CMS | ADMINS-THRD | POWER COUNTY | EKOTELOV |  | 2023-11-15 15:29
4 | WTG-0212-0000 | 2796637 | Hydraulic Hand Pump Replacement | 2022-02-08 09:54 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2022-07-22 08:02
2 | WTG-0030-0000 | 2811850 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2022-03-03 16:40 | Cancelled | GBXOIL | GBXOILCOOL | TURKEY TRACK | TLANDIN |  | 2023-03-30 08:37
1 | WTG-0227-0000 | 2811852 | GEARBOX OIL, Fix oil leak | 2022-03-03 14:13 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NMCFARLAND |  | 2022-04-10 15:38
1 | WTG-0055A-0000 | 2813237 | GEARBOX OIL, Replace Purple Hose | 2022-03-07 13:00 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-03-18 07:07
5 | GBX-00095 | 2909944 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-04-07 10:06 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-04-15 08:31
5 | WTG-00C7-0000 | 2919842 | CMS HSS Check | 2022-04-12 14:02 | Cancelled | CMS | CMSHSS | COYOTE RIDGE | CBILLIG |  | 2023-07-03 14:33
5 | WTG-0011-0000 | 2919860 | GEARBOX OIL, Replace oil filter | 2022-04-12 14:28 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-06-24 07:14
5 | WTG-0011-0000 | 2919865 | GEARBOX OIL, replace purple hose | 2022-04-12 14:35 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-06-24 07:15
5 | WTG-0046-0000 | 2920554 | Leaking hose | 2022-04-15 10:37 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | NMCFARLAND |  | 2024-05-21 13:02
4 | WTG-0205-NDGP-0000 | 2920597 | Replace red spider insert | 2022-04-15 14:41 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2022-07-22 08:09
1 | WTG-0073-0000 | 2920491 | Lube pump motor | 2022-04-15 07:58 | Closed | GBXOIL | GBXOILCOOL | UPSTREAM | AKERKMAN |  | 2022-07-14 16:44
4 | WTG-0081-NDGD-0000 | 2920586 | Replace puple hose | 2022-04-15 09:39 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-01-30 11:01
4 | WTG-0081-NDG0-0000 | 2920587 | Jensen filter is leaking | 2022-04-15 09:41 | Cancelled | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-07-05 08:43
4 | WTG-0081-NDGP-0000 | 2920588 | Replace red spider coupler | 2022-04-15 09:49 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-01-30 11:02
2 | WTG-0302-0000 | 2922049 | GEARBOX OIL, Oil Sample | 2022-04-21 16:02 | Closed | GBXOIL | GBXOILSAMP | PRAIRIE BREEZE3 | CMORRISON |  | 2022-08-31 16:45
2 | GBX-00115 | 2923282 | CMS Gearbox Borescope | 2022-04-25 16:30 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | CBILLIG |  | 2022-05-18 13:57
2 | WTG-0036-0000 | 2923260 | Replace orange, yellow, and purple gearbox hoses | 2022-04-25 15:26 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2022-10-21 12:38
5 | WTG-0036-0000 | 2923259 | GEARBOX OIL, Replace Primary Filter | 2022-04-25 10:56 | Closed | GBXOIL | GBXFILTELEM | FORWARD | ALANGKAU |  | 2022-06-10 09:07
5 | WTG-0064-0000 | 2924753 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-04-28 11:17 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2022-09-01 12:00
2 | GBX-00044 | 2928071 | GEARBOX OIL, Particle counter troubleshooting | 2022-05-05 10:34 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | CBILLIG |  | 2022-05-18 08:40
2 | GBX-00118 | 2928072 | GEARBOX OIL, Particle counter troubleshooting | 2022-05-05 10:36 | Closed | GBXOIL | GBXPARTTS | SANTA RITA EAST | CBILLIG |  | 2022-06-24 08:34
5 | WTG-0005-NDGP-0000 | 2928054 | GEARBOX OIL, Replace oil pump | 2022-05-05 09:43 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | PMASAKI |  | 2023-02-20 13:00
5 | WTG-3021-0000 | 2930896 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-05-12 13:06 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-23 10:12
5 | WTG-0005-0000 | 2930916 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-05-12 15:14 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | CBILLIG |  | 2022-08-23 10:19
5 | WTG-0019-0000 | 2930918 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-05-12 15:17 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | CBILLIG |  | 2022-08-23 10:20
1 | WTG-043E-0000 | 2931626 | GEARBOX OIL, Fix oil leak | 2022-05-16 14:42 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH |  | 2022-06-17 10:23
1 | WTG-0210-0000 | 2937486 | GEARBOX OIL, Fix oil leak | 2022-05-23 15:14 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | AHOFFMANN |  | 2023-01-06 10:42
5 | WTG-0052-0000 | 2940497 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-01 14:51 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | CBILLIG |  | 2022-08-26 13:10
1 | WTG-0063-NDG0-0000 | 2943935 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-10 13:23 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2022-07-07 12:53
1 | WTG-0064-NDG0-0000 | 2943936 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-10 13:25 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2022-07-07 12:53
2 | GBX-000045 | 2943884 | Gearbox Cooling system issue | 2022-06-10 11:04 | Closed | GBXOIL | EM1203 | WILLOW CREEK | ADBROWN |  | 2022-06-15 15:45
1 | WTG-0057-NDG0-0000 | 2943934 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-10 13:16 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-07-18 14:36
5 | WTG-0030-0000 | 2946065 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-16 11:35 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-07-18 14:34
5 | WTG-0042-0000 | 2946066 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-16 11:35 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-07-18 14:34
5 | WTG-0054-0000 | 2946067 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-16 11:35 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-07-18 14:33
4 | WTG-0001-0000 | 3121554 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2023-05-03 13:31 | Closed | GBXOIL | GBXOILADD | FORWARD | DMONROE |  | 2023-11-14 11:02
1 | WTG-0011-0000 | 2962044 | Inspect GBX for Oil Leak | 2022-07-19 10:19 | Closed | GBXOIL | GBXOILLEAK | SUNDANCE | CPRUIT |  | 2023-07-18 15:46
5 | WTG-2030-0000 | 2971143 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-02 13:56 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-06-13 10:58
5 | WTG-2112-0000 | 2971148 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-02 13:56 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-01-27 14:02
5 | WTG-2118-0000 | 2971149 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-02 13:56 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-01-27 14:03
5 | WTG-2121-0000 | 2971150 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-02 13:56 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-10 11:08
5 | WTG-2049-0000 | 2971144 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-02 13:56 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-21 14:35
5 | WTG-2109-0000 | 2971147 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-02 13:56 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-10 11:08
5 | WTG-2123-0000 | 2971151 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-02 13:56 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-23 10:10
5 | WTG-1002-0000 | 2972540 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-04 16:50 | Cancelled | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2022-12-08 13:45
1 | WTG-0023-NDG0-0000 | 2801916 | CMS Gearbox Inspection per GE request | 2022-02-10 15:24 | Closed | CMS | CMSINSP | GOLDTHWAITE | JCULLITY |  | 2022-06-29 08:01
4 | WTG-0098-0000 | 2802953 | GEARBOX OIL, Secondary filter system element change | 2022-02-15 11:27 | Closed | GBXOIL | GBXFILTELEM | FORWARD | ALANGKAU |  | 2022-09-16 09:41
4 | WTG-0073-0000 | 3066187 | GEARBOX OIL, Add/Top-Off 8-10 Gallons | 2023-01-09 10:51 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-01-30 11:44
4 | WTG-0089-0000 | 2802930 | Jensen pump leaking at the pump seal | 2022-02-15 11:38 | Closed | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE |  | 2022-02-22 07:31
4 | WTG-0017-0000 | 2802772 | GEARBOX OIL, Top Off & Cleanup After Leak | 2022-02-15 07:20 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JJENSEMA |  | 2022-04-10 17:30
1 | WTG-0125-0000 | 2802282 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2022-02-11 14:01 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | MHUFF |  | 2022-02-16 14:51
4 | WTG-0090-0000 | 2803541 | GEARBOX OIL, Secondary filter system element change | 2022-02-17 12:22 | Closed | GBXOIL | GBXFILTELEM | FORWARD | ALANGKAU |  | 2022-09-14 09:37
4 | WTG-0095-NDGP-0000 | 2727267 | Drill hole to inspect gear oil pump coupler | 2022-01-18 14:58 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2022-07-05 08:32
5 | WTG-0066-0000 | 2753889 | Replace red elastomer insert on oil pump coupler | 2022-02-01 11:04 | Closed | GBXOIL | GBXOILCOOL | FORWARD | ALANGKAU |  | 2022-02-03 10:36
4.1 | WTG-0028-0000 | 2789043 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0029-0000 | 2789044 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0030-0000 | 2789045 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0075-0000 | 2789090 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0076-0000 | 2789091 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0077-0000 | 2789092 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0078-0000 | 2789093 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0079-0000 | 2789094 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0080-0000 | 2789095 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
4.1 | WTG-0081-0000 | 2789096 | 2021 Gearbox Oil Samples | 2022-02-02 15:12 | Closed | GBXOIL |  | BETHEL | ESTEPANOVIC |  | 2024-04-04 08:38
2 | WTG-0034-0000 | 2800160 | CMS Gearbox Borescope | 2022-02-08 16:03 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2022-08-31 16:46
9 | WTG-0081-0000 | 2810575 | GEARBOX OIL, Fix oil leak, high speed seal | 2022-03-01 18:32 | Ready to Schedule | GBXOIL | GBXOILLEAK | UPSTREAM | RKUDERA |  | 2024-04-11 13:04
1 | WTG-0F10-0000 | 2813048 | CMS Gearbox Borescope | 2022-03-07 10:49 | Cancelled | CMS | CMSGBXBORE | JAYHAWK | CBILLIG |  | 2022-04-08 11:30
4.2 | WTG-0078-0000 | 2891858 | GEARBOX OIL, Replace oil cooler | 2022-03-25 14:58 | Closed | GBXOIL | GBXOILCOOL | GRATIOT | GBOTT |  | 2022-07-20 06:46
4 | WTG-0021-0000 | 2892532 | GEARBOX OIL, Replace hoses (see comments) | 2022-03-28 12:14 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2022-04-10 17:52
5 | GBX-00095 | 2909943 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-04-07 10:03 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-05-09 09:48
5 | WTG-0061-0000 | 2919881 | Replace CMS 60M100 Monitor | 2022-04-12 15:59 | Cancelled | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-09-19 10:06
4.2 | WTG-0111-NDGP-0000 | 2920530 | Install secondary filtration system on gearbox oil | 2022-04-15 09:08 | Closed | GBXOIL | GBXFILTINS | GRATIOT | GBOTT | 1 | 2022-04-19 07:40
1 | WTG-0045-0000 | 2927118 | GEARBOX OIL, Fix oil leak | 2022-05-02 18:24 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MLEGLEITER |  | 2023-03-20 12:15
5 | WTG-0018-0000 | 2924754 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-04-28 11:19 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-04-05 13:54
1 | WTG-0C03-0000 | 3017574 | Oil drip pan fix/looked into | 2022-09-14 14:57 | Ready to Schedule | GBXOIL | GBXPARTTS | JAYHAWK | CHORN
2 | WTG-0027-0000 | 2925580 | CMS Gearbox Borescope | 2022-04-28 21:51 | Closed | CMS | CMSGBXBORE | TURKEY TRACK | JMATHIS |  | 2023-09-15 15:09
2 | WTG-0006-NDGP-0000 | 2928233 | GEARBOX OIL, Add/Top-Off | 2022-05-05 15:42 | Closed | GBXOIL | GBXOILADD | VANTAGE | CCUSACK |  | 2022-08-18 15:43
3.1 | WTG-0054-NDG0-0000 | 3262525 | CMS sensor | 2024-01-30 14:46 | Closed | CMS | CMSINSP | ORANGEVILLE | BHUNTER |  | 2024-07-27 13:41
3 | WTG-2122-0000 | 2947969 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-21 10:30 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-06-13 11:00
5 | GEN-00099 | 2935237 | CMS Generator Bearing Check | 2022-05-17 17:05 | Closed | CMS | CMSGENB | SANTA RITA EAST | CBILLIG |  | 2022-05-18 15:08
2 | WTG-0045-NDB0-0000 | 2939810 | CMS Main Bearing Borescope | 2022-05-31 16:20 | Cancelled | CMS | CMSMBBORE | MAVERICK | CBILLIG |  | 2022-08-23 17:40
2 | GBX-00007 | 2939674 | GEARBOX OIL, Particle counter removal | 2022-05-31 09:55 | Closed | GBXOIL | GBXPARTREM | SANTA RITA EAST | CBILLIG |  | 2022-05-31 13:59
5 | WTG-0042-0000 | 2943206 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-08 10:13 | Cancelled | CMS | CMSTRBLSHOOT | DEUEL HARVEST | CBILLIG |  | 2022-09-21 10:49
5 | GEN-00048 | 2943207 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-08 10:17 | Cancelled | CMS | CMSTRBLSHOOT | DEUEL HARVEST | CBILLIG |  | 2022-09-21 11:05
5 | WTG-0016-NDB0-0000 | 2943943 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-06-10 14:28 | Cancelled | CMS | CMSTRBLSHOOT | DEUEL HARVEST | CBILLIG |  | 2023-03-27 11:46
5 | WTG-0011-0000 | 2946058 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-16 11:35 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-07-18 14:36
5 | WTG-0018-0000 | 2946059 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-16 11:35 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-07-18 14:35
5 | WTG-0019-0000 | 2946060 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-16 11:35 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2022-10-03 13:26
5 | WTG-0023-0000 | 2946061 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-16 11:35 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2022-10-03 13:26
5 | WTG-0025-0000 | 2946062 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-16 11:35 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-07-18 14:35
5 | WTG-0026-0000 | 2946063 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-16 11:35 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-07-18 14:35
5 | WTG-0027-0000 | 2946064 | GEARBOX OIL, Particle counter troubleshooting | 2022-06-16 11:35 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2022-10-03 13:25
2 | GBX-00033 | 2951115 | CMS Gearbox Borescope | 2022-06-29 15:38 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | CBILLIG |  | 2022-08-08 11:36
2 | GBX-00001 | 2950582 | GEARBOX OIL, Particle counter installation | 2022-06-28 12:14 | Closed | GBXOIL | GBXPARTINS | UPSTREAM | CBILLIG |  | 2022-08-09 14:57
2 | WTG-0038-NDG0-0000 | 2951361 | GEARBOX OIL, Add/Top-Off | 2022-06-30 11:07 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2022-11-08 12:32
1 | GBX-000028 | 2965700 | EM: Gearbox oil filter dirty (warning) | 2022-07-24 11:54 | Closed | GBXOIL | EM89 | CAMP SPRINGS I | BEDEN |  | 2022-07-28 11:28
5 | WTG-0030-0000 | 2970475 | GEARBOX OIL, Fix oil leak | 2022-08-01 13:04 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | AADAMS |  | 2023-10-23 22:55
5 | WTG-3055-NDB0-0000 | 2973165 | CMS Main Bearing Check | 2022-08-05 16:06 | Cancelled | CMS | CMSMB | TRAVERSE | CBILLIG |  | 2023-02-02 09:35
5 | WTG-0003-0000 | 2988827 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 10:49
5 | WTG-0007-0000 | 2988828 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 10:57
5 | WTG-0010-0000 | 2988829 | CMS Trouble Shoot (Invenergy request, non-GE) / SR# 6253028 | 2022-08-12 09:40 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-07-10 13:16
5 | WTG-0017-0000 | 2988831 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 10:45
5 | WTG-0018-0000 | 2988832 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 10:48
4 | WTG-0072A-0000 | 2988700 | GEARBOX OIL, Fix oil leak at Secondary | 2022-08-11 14:56 | Closed | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE |  | 2022-12-19 08:21
5 | WTG-0096-0000 | 2988841 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 11:00
5 | GEN-00038 | 2992349 | CMS Generator Bearing Check | 2022-08-18 15:04 | Closed | CMS | CMSGENB | UPSTREAM | CBILLIG |  | 2022-09-28 14:15
1 | WTG-0078-0000 | 3121775 | GEARBOX OIL, Fix oil leak | 2023-05-04 08:49 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | DBMINER |  | 2023-05-09 09:50
2 | WTG-0017-0000 | 3121848 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-04 09:39 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | ABARNDT |  | 2023-06-14 09:19
2 | GEN-00075 | 3028842 | CMS Generator Bearing Check | 2022-10-03 10:07 | Closed | CMS | CMSGENB | DEUEL HARVEST | CBILLIG |  | 2022-10-13 10:22
5 | GBX-00008 | 3032258 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-10-10 13:07 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | WDEAS |  | 2022-11-11 09:23
4 | WTG-0020-0000 | 3034434 | GEARBOX OIL, Add/Top-Off about 3-5 gallons | 2022-10-13 12:00 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-03-27 10:05
4 | WTG-0010-NDG0-0000 | 3036490 | Add/top off 5 gallons of oil | 2022-10-19 16:08 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2022-12-09 10:50
5 | WTG-0037-NDGP-0000 | 3036491 | Replace red spider for gear oil pump coulper | 2022-10-19 16:10 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-03-27 10:51
1 | WTG-0112-0000 | 3037100 | GEARBOX OIL, Oil Sample | 2022-10-17 08:06 | Cancelled | GBXOIL | GBXOILSAMP | MIAMI 1 | JFREEMAN |  | 2023-11-16 13:31
1 | WTG-0156-0000 | 3037101 | GEARBOX OIL, Oil Sample | 2022-10-17 07:07 | Closed | GBXOIL | GBXOILSAMP | MIAMI 1 | JFREEMAN |  | 2023-04-11 10:58
1 | WTG-0131-0000 | 3037102 | GEARBOX OIL, Oil Sample | 2022-10-17 08:09 | Cancelled | GBXOIL | GBXOILSAMP | MIAMI 1 | JFREEMAN |  | 2023-11-16 13:36
1 | WTG-0090-0000 | 3037103 | GEARBOX OIL, Oil Sample | 2022-10-17 08:10 | Closed | GBXOIL | GBXOILSAMP | MIAMI 1 | JFREEMAN |  | 2023-10-27 07:27
1 | WTG-0117-0000 | 3037104 | GEARBOX OIL, Oil Sample | 2022-10-17 08:10 | Closed | GBXOIL | GBXOILSAMP | MIAMI 1 | JFREEMAN |  | 2023-11-16 13:35
1 | WTG-0108-0000 | 3037105 | GEARBOX OIL, Oil Sample | 2022-10-17 08:11 | Cancelled | GBXOIL | GBXOILSAMP | MIAMI 1 | JFREEMAN |  | 2023-11-16 13:32
1 | WTG-0110-0000 | 3037106 | GEARBOX OIL, Oil Sample | 2022-10-17 08:12 | Cancelled | GBXOIL | GBXOILSAMP | MIAMI 1 | JFREEMAN |  | 2023-11-16 13:32
1 | WTG-0012-0000 | 3037107 | GEARBOX OIL, Oil Sample | 2022-10-17 08:13 | Cancelled | GBXOIL | GBXOILSAMP | MIAMI 1 | JFREEMAN |  | 2023-11-16 13:32
2 | WTG-0006-0000 | 3094978 | CMS Gearbox Borescope | 2023-03-08 17:53 | Closed | CMS | CMSGBXBORE | GORDON BUTTE | TWIEDEMEIER |  | 2023-03-27 11:48
5 | WTG-0052-NDG0-0000 | 3045780 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-11-15 11:51 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | CBILLIG |  | 2023-03-30 15:43
9 | WTG-0044-0000 | 3045988 | GEARBOX, Oil Change | 2022-11-15 18:33 | Closed | GBXOIL | SVCS-GBXOILCHG | BETHEL | EAVILA |  | 2022-11-29 12:22
9 | WTG-0067-0000 | 3045990 | GEARBOX, Oil Change | 2022-11-15 18:40 | Closed | GBXOIL | GBXOILCHG | BETHEL | EAVILA |  | 2022-11-30 08:44
9 | WTG-0118-0000 | 3045991 | GEARBOX, Oil Change | 2022-11-15 18:41 | Closed | GBXOIL | GBXOILCHG | BETHEL | EAVILA |  | 2023-03-20 12:27
9 | WTG-0065-0000 | 3049132 | GEARBOX, Oil Change | 2022-11-22 11:01 | Closed | GBXOIL | GBXOILCHG | BETHEL | AALEMAN |  | 2023-02-03 11:18
2 | WTG-0304-NDB0-0000 | 3051969 | CMS Main Bearing Borescope | 2022-11-30 15:02 | Cancelled | CMS | CMSMBBORE | BISHOP HILL III | CBILLIG |  | 2023-01-27 15:57
9 | WTG-0104-0000 | 3053729 | GEARBOX, Oil Change | 2022-12-05 09:08 | Closed | GBXOIL | GBXOILCHG | BETHEL | TMILLER2 |  | 2022-12-21 07:55
9 | WTG-0001-0000 | 3053730 | GEARBOX, Oil Change | 2022-12-05 09:13 | Closed | GBXOIL | GBXOILCHG | BETHEL | MRAHMAN |  | 2023-01-03 10:54
1 | BRG-000063 | 3053733 | CMS Main Bearing Borescope | 2022-12-05 09:43 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | CBILLIG |  | 2022-12-09 08:40
1 | WTG-0012-0000 | 3053651 | Low Oil Level | 2022-12-04 14:53 | Closed | GBXOIL |  | BUFFALO MOUNT | CREICE |  | 2022-12-30 15:38
9 | WTG-0115-0000 | 3055149 | GEARBOX, Oil Change | 2022-12-09 09:15 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-06-05 16:37
9 | WTG-0120-0000 | 3055150 | GEARBOX, Oil Change | 2022-12-09 09:16 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-01-23 08:50
9 | WTG-0008-0000 | 3055182 | GEARBOX, Oil Change | 2022-12-09 12:12 | Closed | GBXOIL | GBXOILCHG | BETHEL | AALEMAN |  | 2022-12-21 07:49
2 | WTG-0033-0000 | 3055190 | CMS Gearbox Borescope | 2022-12-09 13:00 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | ZMILLER |  | 2023-02-17 14:50
9 | WTG-0089-0000 | 3057309 | GEARBOX, Oil Change | 2022-12-15 10:50 | Closed | GBXOIL | GBXOILCHG | BETHEL | RGRADO |  | 2023-05-02 14:14
9 | WTG-0090-0000 | 3057310 | GEARBOX, Oil Change | 2022-12-15 10:54 | Closed | GBXOIL | GBXOILCHG | BETHEL | RGRADO |  | 2023-05-12 11:21
5 | WTG-0033-0000 | 3059465 | GEARBOX OIL, Add 8-10 Gallons | 2022-12-21 15:19 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2023-03-10 12:36
4 | WTG-0071A-0000 | 3063357 | GEARBOX OIL, Replace oil cooler hose (purple hose) | 2023-01-03 14:00 | Closed | GBXOIL | GBXOILCOOL | FORWARD | DMONROE |  | 2023-05-10 13:40
2 | WTG-1004-NDG0-0000 | 3067316 | CMS Gearbox Borescope | 2023-01-11 14:43 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2023-03-22 10:36
1 | WTG-0050-0000 | 3067258 | Poseidon install | 2023-01-11 11:37 | Cancelled | GBXOIL | GBXPARTINS | MAVERICK | MWEBER |  | 2023-01-11 13:46
2 | WTG-0014-0000 | 3068159 | MB Inspection | 2023-01-13 09:16 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-01-20 08:57
5 | WTG-0096-0000 | 3068006 | GEARBOX OIL, small leak at pump or filter | 2023-01-12 14:26 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-07-20 11:56
2 | WTG-0006-NDG0-0000 | 3068702 | Nanjing HSS Oil Leak Inspection | 2023-01-16 09:53 | Closed | GBXOIL | GBXOILADD | WAKE 1 | JCULLITY |  | 2023-01-20 11:10
2 | WTG-0066-NDG0-0000 | 3068703 | Nanjing HSS Oil Leak Inspection | 2023-01-16 09:53 | Closed | GBXOIL | GBXOILADD | WAKE 1 | JCULLITY |  | 2023-01-20 11:10
5 | WTG-0085-0000 | 3068807 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2023-01-16 13:58 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-04-20 15:37
1 | WTG-00E1-NDB0-0000 | 3070364 | CMS Main Bearing Borescope | 2023-01-19 17:49 | Closed | CMS | CMSMBBORE | TATANKA RIDGE | CMORRISON |  | 2023-02-28 16:19
5 | WTG-0024-NTV0-0000 | 3071067 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-23 09:50 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-01-27 09:31
5 | WTG-0051-NDD0-0000 | 3072469 | CMS Generator Bearing Check | 2023-01-26 13:52 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-04-08 09:11
5 | WTG-0062-NDB0-0000 | 3072464 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-26 13:47 | Closed | CMS | CMSTRBLSHOOT | BETHEL | CBILLIG |  | 2023-12-12 16:53
5 | WTG-0060-NDD0-0000 | 3072471 | CMS Generator Bearing Check | 2023-01-26 13:53 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-04-13 15:13
2 | WTG-0061-NDD0-0000 | 3072473 | CMS Generator Bearing Check | 2023-01-26 13:53 | Closed | CMS | CMSGENB | BETHEL | CBILLIG |  | 2023-03-28 13:09
2 | WTG-0108-0000 | 3073188 | CMS Main Bearing Borescope | 2023-01-27 08:38 | Closed | CMS | CMSMBBORE | BETHEL | ACHAVIRA |  | 2023-01-31 10:53
2 | GBX-00024 | 2981609 | CMS Gearbox Borescope | 2022-08-08 14:42 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | CBILLIG |  | 2022-08-22 11:11
4.1 | WTG-0070-0000 | 2986656 | GEARBOX OIL, Fix oil leak on secondary pump | 2022-08-08 15:02 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2023-01-30 11:34
5 | BRG-000048 | 2987883 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-09 11:14 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-08-10 08:05
5 | WTG-0079-0000 | 2988840 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 10:59
5 | WTG-0101-0000 | 2988842 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 10:38
5 | WTG-0031-0000 | 2988833 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 10:50
5 | WTG-0033-0000 | 2988834 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-02-06 10:50
5 | WTG-0035-0000 | 2988835 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-12 09:40 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | CBILLIG |  | 2023-04-05 14:50
5 | GBX-00048 | 3009762 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-08-30 11:00 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | CBILLIG |  | 2022-08-30 16:08
5 | WTG-0009-0000 | 3024216 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-09-20 14:56 | Closed | CMS | CMSTRBLSHOOT | GORDON BUTTE | CBILLIG |  | 2022-11-15 16:23
4 | WTG-0032-0000 | 3035716 | GEARBOX OIL, Add/Top-Off 5 gal or less | 2022-10-17 12:48 | Closed | GBXOIL | GBXOILADD | FORWARD | DMONROE |  | 2023-03-30 10:37
2 | WTG-0005-NDG0-0000 | 3035802 | GEARBOX OIL, Add/Top-Off | 2022-10-17 12:30 | Closed | GBXOIL | GBXOILADD | VANTAGE | CCUSACK |  | 2023-02-20 13:00
5 | WTG-2005-0000 | 3038846 | CMS Trouble Shoot (Invenergy request, non-GE) | 2022-10-27 14:52 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | CBILLIG |  | 2023-02-21 14:34
4 | WTG-0317-0000 | 3040204 | Gearbox hoses | 2022-10-31 16:17 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | NMCFARLAND |  | 2023-01-06 10:42
9 | WTG-0064-0000 | 3049129 | GEARBOX, Oil Change | 2022-11-22 10:55 | Closed | GBXOIL | GBXOILCHG | BETHEL | AALEMAN |  | 2023-04-14 16:24
4 | WTG-0239-0000 | 3050710 | GEARBOX OIL, Fix oil leak | 2022-11-28 16:13 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | THOLZ |  | 2023-03-13 11:45
9 | WTG-0070-0000 | 3054375 | GEARBOX, Oil Change | 2022-12-07 11:12 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-05-02 09:27
9 | WTG-0017-0000 | 3055151 | GEARBOX, Oil Change | 2022-12-09 09:22 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-02-16 16:16
9 | WTG-0018-0000 | 3055152 | GEARBOX, Oil Change | 2022-12-09 09:23 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-03-07 08:53
9 | WTG-0019-0000 | 3055154 | GEARBOX, Oil Change | 2022-12-09 09:28 | Closed | GBXOIL | GBXOILCHG | BETHEL | KWHATLEY |  | 2023-03-07 14:58
9 | WTG-0097-0000 | 3056511 | GEARBOX, Oil Change | 2022-12-13 15:32 | Closed | GBXOIL | GBXOILCHG | BETHEL | JGARLAND |  | 2023-03-23 09:14
9 | WTG-0096-0000 | 3056512 | GEARBOX, Oil Change | 2022-12-13 15:34 | Closed | GBXOIL | GBXOILCHG | BETHEL | JGARLAND |  | 2023-02-20 15:28
9 | WTG-0098-0000 | 3056513 | GEARBOX, Oil Change | 2022-12-13 15:35 | Closed | GBXOIL | GBXOILCHG | BETHEL | JGARLAND |  | 2023-06-06 13:47
9 | WTG-0099-0000 | 3056514 | GEARBOX, Oil Change | 2022-12-13 15:36 | Closed | GBXOIL | GBXOILCHG | BETHEL | JGARLAND |  | 2023-05-16 13:38
9 | WTG-0103-0000 | 3056515 | GEARBOX, Oil Change | 2022-12-13 15:36 | Closed | GBXOIL | GBXOILCHG | BETHEL | JGARLAND |  | 2023-06-06 13:46
9 | WTG-0085-0000 | 3057333 | GEARBOX, Oil Change | 2022-12-15 11:04 | Closed | GBXOIL | GBXOILCHG | BETHEL | RGRADO |  | 2023-03-15 09:15
2 | GBX-00016 | 3058275 | CMS Gearbox Borescope | 2022-12-19 11:51 | Closed | CMS | CMSGBXBORE | UPSTREAM | CBILLIG |  | 2023-02-03 15:53
9 | WTG-0068-0000 | 3060921 | GEARBOX, Oil Change | 2022-12-28 11:18 | Closed | GBXOIL | GBXOILCHG | BETHEL | ASANCHEZ |  | 2023-01-16 07:50
9 | WTG-0053-0000 | 3060929 | GEARBOX, Oil Change | 2022-12-28 11:55 | Closed | GBXOIL | GBXOILCHG | BETHEL | TMILLER2 |  | 2023-03-29 16:09
9 | SITE-UPLA | 3061092 | PARTS_CONSUMPTION_FSO_PROJECTS | 2022-12-28 12:21 | Closed | GBXOIL | GBXOILCHG | UPLAND PRAIRIE | SBARTHOLOMEW |  | 2022-12-28 12:30
9 | SYS-WTG | 3061097 | PARTS_CONSUMPTION_FSO_PROJECTS | 2022-12-28 12:21 | Closed | GBXOIL |  | UPLAND PRAIRIE | SBARTHOLOMEW |  | 2022-12-28 12:30
9 | WTG-0073-0000 | 3063746 | GEARBOX, Oil Change | 2023-01-04 09:03 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-05-02 13:51
9 | WTG-0075-0000 | 3063747 | GEARBOX, Oil Change | 2023-01-04 09:03 | Closed | GBXOIL | GBXOILCHG | BETHEL | ACHAVIRA |  | 2023-04-26 15:51
2 | WTG-0013-0000 | 3064763 | CMS Main Bearing Borescope | 2023-01-05 14:14 | Closed | CMS | CMSMBBORE | MAVERICK | GSHAFFER |  | 2023-01-06 10:14
2 | WTG-0026-0000 | 3064765 | CMS Main Bearing Borescope | 2023-01-05 14:17 | Closed | CMS | CMSMBBORE | MAVERICK | GSHAFFER |  | 2023-01-06 10:14
4 | WTG-0082-NDGP-0000 | 3067393 | Secondary pump seal replacement | 2023-01-11 15:08 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-01-30 14:41
4 | WTG-0082-NDGP-0000 | 3067394 | Poly sheet for oil catch pail | 2023-01-11 15:09 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-01-30 14:42
2 | WTG-0092-0000 | 3068108 | MB Inspection | 2023-01-12 19:34 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-01-20 08:57
2 | WTG-0027-0000 | 3068161 | MB INSPECTION | 2023-01-13 09:18 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | KTINOCO |  | 2023-01-20 08:57
5 | WTG-0213-NTV0-0000 | 3068790 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-16 12:59 | Cancelled | CMS | CMSTRBLSHOOT | BEECH RIDGE II | ABARNDT |  | 2023-01-16 13:18
4 | WTG-0086-0000 | 3068808 | Replace Purple GBX Hose | 2023-01-16 12:02 | Closed | GBXOIL | GBXOILCHG | FORWARD | DMONROE |  | 2023-08-02 09:53
2 | WTG-0012-NDG0-0000 | 3070209 | CMS Gearbox Borescope | 2023-01-19 08:02 | Closed | CMS | CMSGBXBORE | GRAND RIDGE | RLINN |  | 2024-09-11 16:31
5 | WTG-0205-0000 | 3071551 | GEARBOX OIL, Add/Top-Off 2 gallons | 2023-01-24 13:29 | Closed | GBXOIL | GBXOILADD | FORWARD | TBUYESKE |  | 2023-07-17 14:50
2 | WTG-0008-0000 | 3072407 | GEARBOX OIL, Particle counter troubleshooting | 2023-01-26 10:22 | Closed | GBXOIL | GBXPARTTS | MCADOO | WDEAS |  | 2023-02-24 14:50
1 | GBX-00027 | 3073297 | GEARBOX OIL, Particle counter installation | 2023-01-27 13:07 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | MWILSON |  | 2023-01-27 13:35
1 | GBX-00028 | 3073298 | GEARBOX OIL, Particle counter installation | 2023-01-27 13:10 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | MWILSON |  | 2023-01-27 13:37
1 | GBX-00021 | 3078584 | GEARBOX OIL, Particle counter installation | 2023-02-06 11:51 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | MWILSON |  | 2023-02-09 14:44
1 | GBX-00022 | 3078585 | GEARBOX OIL, Particle counter installation | 2023-02-06 11:58 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | MWILSON |  | 2023-02-09 14:39
2 | WTG-0096-NDGP-0000 | 3079727 | Oil cooler leak | 2023-02-08 16:30 | Closed | GBXOIL | ADMIN | GREXP | THUEY |  | 2024-01-10 16:12
5 | WTG-0087-NDG0-0000 | 3081488 | Purple hose replacement | 2023-02-13 14:18 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2023-03-07 11:35
5 | WTG-0006-0000 | 3085633 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-02-20 14:44 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-10-13 14:29
2 | WTG-0027-NDD0-0000 | 3085673 | CMS Generator Bearing Check | 2023-02-20 16:32 | Closed | CMS | CMSGENB | SUNDANCE | ABARNDT |  | 2023-03-14 16:13
4 | WTG-0098-0000 | 3085952 | GEARBOX OIL, Add/Top-Off 3-5 gallons | 2023-02-21 15:17 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-08-18 11:54
1 | WTG-00B1-NDB0-0000 | 3086720 | CMS Main Bearing Borescope | 2023-02-23 12:52 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | ABARNDT |  | 2023-03-30 15:03
3 | GEN-000046 | 3086591 | Gen Bearing Replacement | 2023-02-23 09:46 | Closed | CMS | CMSGENB | STANTON | JBYNUM |  | 2023-03-02 08:53
1 | WTG-00A2-NDB0-0000 | 3087678 | CMS Main Bearing Borescope | 2023-02-27 12:11 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | CBILLIG |  | 2023-03-23 17:48
2 | WTG-0058-0000 | 3088430 | CMS Gearbox Borescope | 2023-03-01 09:08 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | CSTRZELEC |  | 2023-03-06 11:47
2 | WTG-0011-NDG0-0000 | 3093038 | GEARBOX OIL, Add/Top-Off | 2023-03-03 15:37 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2023-08-17 14:12
4 | WTG-0043-0000 | 3093000 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-03-03 13:33 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-07-20 12:05
1 | WTG-0353-0000 | 3095366 | GEARBOX Replace oil cooler fan 2 speed motor number 1 | 2023-03-09 13:37 | Closed | GBXOIL | GBXOILCOOL | BISHOP HILL III | JPADILLA |  | 2023-03-15 11:49
2 | WTG-0088-NDG0-0000 | 3095270 | CMS Gearbox Borescope | 2023-03-09 13:09 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | ABARNDT |  | 2023-07-17 12:38
1 | WTG-0118-NDB0-0000 | 3096715 | CMS Main Bearing Borescope | 2023-03-10 10:28 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2023-04-10 10:46
2 | GBX-00088 | 3096769 | CMS Gearbox Borescope | 2023-03-10 14:11 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | MWILSON |  | 2023-03-28 11:20
1 | WTG-0036-NDB0-0000 | 3096733 | CMS Main Bearing Borescope | 2023-03-10 11:16 | Closed | CMS | CMSMBBORE | BETHEL | CBILLIG |  | 2023-03-13 15:05
1 | WTG-0003-NDB0-0000 | 3096734 | CMS Main Bearing Borescope | 2023-03-10 11:22 | Closed | CMS | CMSMBBORE | BETHEL | CBILLIG |  | 2023-04-21 14:43
1 | WTG-1070-0000 | 3096834 | Gear box leak | 2023-03-10 16:38 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | QCROUSE |  | 2023-04-14 16:10
4.2 | WTG-0048-0000 | 3097317 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2023-03-13 13:54 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-06-13 11:36
5 | WTG-0047-0000 | 3100208 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-17 10:23 | Closed | CMS | CMSTRBLSHOOT | BETHEL | CBILLIG |  | 2023-10-26 10:01
5 | WTG-0088-NTV0-0000 | 3100979 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-20 10:04 | Closed | CMS | CMSTRBLSHOOT | MAVERICK | ABARNDT |  | 2023-05-25 09:22
2 | WTG-0098-ND00-0000 | 3101530 | CMS Gearbox Borescope | 2023-03-21 14:11 | Closed | CMS | CMSGBXBORE | MIAMI 1 | WDEAS |  | 2023-11-21 07:26
3 | WTG-1035-NTV0-0000 | 3101535 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-21 14:38 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-08-18 14:24
3 | WTG-1091-NTV0-0000 | 3101538 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-21 14:46 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-06-05 10:40
2 | WTG-1131-NDB0-0000 | 3101539 | CMS Main Bearing Borescope | 2023-03-21 14:56 | Closed | CMS | CMSMBBORE | TRAVERSE | ABARNDT |  | 2023-03-28 12:01
1 | WTG-0078-NDB0-0000 | 3101734 | CMS Main Bearing Borescope | 2023-03-22 09:48 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2023-04-24 09:17
2 | GBX-00036 | 3102360 | GEARBOX OIL, Particle counter installation | 2023-03-24 09:35 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | CBILLIG |  | 2023-03-28 13:27
2 | GBX-00037 | 3102358 | GEARBOX OIL, Particle counter removal | 2023-03-24 09:34 | Closed | GBXOIL | GBXPARTREM | BLOOMING GROVE | CBILLIG |  | 2023-03-28 09:52
1 | WTG-0067-0000 | 3102467 | Secondary oil filtration, Fix oil leak | 2023-03-24 13:39 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | DMULLENS |  | 2023-04-26 15:53
5 | WTG-0031-NDG0-0000 | 3105835 | GEARBOX OIL, Add/Top-Off 5Gals | 2023-03-30 14:40 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2023-04-20 15:37
1 | WTG-0013-0000 | 3106121 | GEARBOX OIL, Fix oil leak | 2023-03-31 11:11 | Closed | GBXOIL | GBXOILLEAK | STANTON | JRIVERA |  | 2023-03-31 13:39
2 | WTG-0034-0000 | 3108559 | GEARBOX OIL, Replace oil pump and top off oil (5Gal) | 2023-04-04 15:18 | Closed | GBXOIL | GBXOILCOOL | FORWARD | JJENSEMA |  | 2023-04-07 10:17
2 | WTG-0046-0000 | 3109156 | CMS Gearbox Borescope | 2023-04-05 16:15 | Closed | CMS | CMSGBXBORE | PLYMOUTH | ABARNDT |  | 2023-05-25 09:27
2 | WTG-0061-0000 | 3111643 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-11 10:13 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-04-14 09:44
2 | WTG-0003-0000 | 3111647 | CMS Main Bearing Borescope | 2023-04-11 10:34 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | ABARNDT |  | 2023-04-20 10:49
5 | WTG-0D02-NDG0-0000 | 3112483 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-13 12:14 | Closed | CMS | CMSTRBLSHOOT | JAYHAWK | CBILLIG |  | 2023-05-02 08:27
5 | WTG-0074A-NDGP-0000 | 3113255 | Adjust gear oil pump coupler | 2023-04-14 16:52 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-06-13 11:38
5 | WTG-3050-0000 | 3492239 | Missing grease zerk | 2025-01-08 17:55 | Ready to Schedule | CMS | CMSMB | TRAVERSE | CHARDWICK
2 | WTG-0025-0000 | 3114111 | CMS Main Bearing Borescope | 2023-04-18 11:41 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2023-05-10 09:43
5 | WTG-0315-0000 | 3114186 | GEARBOX OIL, Fix oil leak, Lesking from seals, oil in belly | 2023-04-18 11:45 | Completed Awaiting Review | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | THOLZ |  | 2025-07-02 11:30
1 | WTG-0081-0000 | 3115088 | GEARBOX OIL, Secondary filter system installation | 2023-04-20 09:22 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | MSCHMITT |  | 2024-05-14 16:04
5 | WTG-0009-NDGP-0000 | 3115582 | Drill gear oil pump coupling inspection hole | 2023-04-21 13:30 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-07-20 12:12
1 | WTG-0089-0000 | 3116293 | GEARBOX OIL, Fix oil leak | 2023-04-25 10:48 | Ready to Schedule | GBXOIL | GBXOILLEAK | BUCKEYE | DBMINER |  | 2024-04-30 13:34
4 | WTG-0050-0000 | 3116349 | GEARBOX OIL, Replace seal between filter pot and bypass valve block | 2023-04-25 12:59 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2023-11-14 12:07
4 | WTG-0050-0000 | 3116350 | GEARBOX OIL, Secondary filter system leak usual spot | 2023-04-25 13:01 | Closed | GBXOIL | GBXFILTINS | FORWARD | KLEFFELMAN |  | 2023-11-14 12:07
5 | WTG-0J03-0000 | 3120163 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-01 14:21 | Closed | CMS | CMSTRBLSHOOT | JAYHAWK | ABARNDT |  | 2023-10-09 11:05
5 | WTG-0090-0000 | 3120524 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-02 09:33 | Closed | CMS | CMSTRBLSHOOT | MAVERICK | ABARNDT |  | 2023-05-25 09:24
1 | WTG-0083-0000 | 3123941 | GEARBOX OIL, Fix radiator leak | 2023-05-08 16:29 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | ZNASH |  | 2024-12-11 12:49
5 | WTG-0050-0000 | 3123815 | Main bearing sensors | 2023-05-08 13:38 | Closed | CMS | CMSMB | MAVERICK | JMILES |  | 2023-07-12 09:51
2 | WTG-0042-NDB0-0000 | 3123817 | CMS Main Bearing Borescope | 2023-05-08 13:42 | Closed | CMS | CMSMBBORE | UPSTREAM | CBILLIG |  | 2023-08-09 10:06
4 | WTG-0081-0000 | 3125375 | Drain oil catch bucket | 2023-05-11 12:08 | In Progress | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE |  | 2023-05-16 16:07
5 | WTG-0081-0000 | 3125359 | Leaking at spigot | 2023-05-11 12:10 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE |  | 2023-07-11 15:34
1 | WTG-0028-0000 | 3126189 | CMS Main Bearing Borescope | 2023-05-15 10:18 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2023-08-24 13:24
1 | WTG-0017-NDG0-0000 | 3126194 | GEARBOX OIL, Particle counter troubleshooting | 2023-05-15 10:37 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | CBILLIG |  | 2023-06-14 09:30
3.1 | WTG-0024-NDG0-0000 | 3262520 | CMS sensor | 2024-01-30 14:40 | Closed | CMS | CMSINSP | ORANGEVILLE | BHUNTER |  | 2024-03-28 09:58
4 | WTG-0047-NDG0-0000 | 3127643 | GEARBOX - Empty Ohain's Oil Bucket | 2023-05-17 15:31 | In Progress | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2023-08-18 12:10
5 | WTG-0209-0000 | 3130381 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-22 08:58 | Closed | CMS | CMSTRBLSHOOT | BEECH RIDGE II | ABARNDT |  | 2023-11-26 20:04
5 | WTG-1064-NTV0-0000 | 3073257 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-27 10:55 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-04-14 15:57
5 | WTG-3028-NTV0-0000 | 3073775 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-30 11:41 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-05-22 12:16
2 | WTG-00B1-0000 | 3073779 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-30 11:51 | Closed | CMS | CMSTRBLSHOOT | TATANKA RIDGE | CBILLIG |  | 2024-08-29 09:01
5 | WTG-3005-NTV0-0000 | 3073769 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-01-30 11:23 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-02-26 12:18
1 | WTG-0050-0000 | 3078254 | GEARBOX OIL, Fix oil leak | 2023-02-04 09:05 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | JWARREN |  | 2023-02-21 12:57
1 | WTG-0002-NDGP-0000 | 3078353 | GEARBOX OIL, Fix oil leak | 2023-02-04 07:57 | Closed | GBXOIL | GBXOILLEAK | ORANGEVILLE | CSTRZELEC |  | 2023-02-06 13:40
5 | WTG-0084-NDGP-0000 | 3078993 | GEARBOX OIL, Add 5gals | 2023-02-07 15:38 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2023-07-20 12:01
4 | WTG-0047-0000 | 3081493 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-02-13 14:49 | Cancelled | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-08-08 07:24
2 | WTG-0069-0000 | 3085501 | CMS HSS Check | 2023-02-20 10:32 | Closed | CMS | CMSHSS | BLOOMING GROVE | ABARNDT |  | 2023-02-21 10:12
2 | WTG-1072-NTV0-0000 | 3087652 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-02-27 11:23 | Closed | CMS | CMSHSS | TRAVERSE | ABARNDT |  | 2023-03-13 10:37
2 | WTG-0072-NDB0-0000 | 3093045 | CMS Main Bearing Borescope | 2023-03-03 15:56 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2023-05-25 09:37
3 | WTG-0024-NDD0-0000 | 3093053 | CMS Generator Bearing Check | 2023-03-03 15:57 | Closed | CMS | CMSGENB | PLYMOUTH | ABARNDT |  | 2023-06-01 08:11
5 | WTG-2101-0000 | 3093808 | CMS Generator Bearing Check | 2023-03-07 09:40 | Cancelled | CMS | CMSGENB | TRAVERSE | RMORRIS |  | 2023-03-07 10:33
1 | WTG-0015-NDB0-0000 | 3096735 | CMS Main Bearing Borescope | 2023-03-10 11:23 | Closed | CMS | CMSMBBORE | BETHEL | CBILLIG |  | 2023-03-20 14:33
1 | WTG-0119-NDB0-0000 | 3096736 | CMS Main Bearing Borescope | 2023-03-10 11:23 | Closed | CMS | CMSMBBORE | BETHEL | CBILLIG |  | 2023-05-24 14:17
5 | WTG-0026-NTV0-0000 | 3097551 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-14 10:49 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | ABARNDT |  | 2023-08-29 13:11
2 | WTG-0014-NDB0-0000 | 3097532 | CMS Main Bearing Borescope | 2023-03-14 10:38 | Closed | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2023-03-20 14:07
2 | WTG-0109-NDB0-0000 | 3097555 | CMS Main Bearing Check | 2023-03-14 11:14 | Closed | CMS | CMSMB | BETHEL | CBILLIG |  | 2023-09-27 15:47
2 | WTG-0004-NDG0-0000 | 3098850 | GEARBOX OIL, Particle counter troubleshooting | 2023-03-15 09:40 | Closed | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2024-07-15 07:25
4 | WTG-0016-NTV0-0000 | 3098845 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-15 09:07 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-03-20 10:37
4 | WTG-0064-NTV0-0000 | 3098846 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-15 09:11 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-03-24 09:44
2 | WTG-0026-NDG0-0000 | 3098851 | GEARBOX OIL, Particle counter troubleshooting | 2023-03-15 09:42 | Cancelled | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2023-06-30 10:56
2 | WTG-0083-NDG0-0000 | 3098853 | GEARBOX OIL, Particle counter troubleshooting | 2023-03-15 09:43 | In Progress | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG
2 | WTG-0084-NDG0-0000 | 3098854 | GEARBOX OIL, Particle counter troubleshooting | 2023-03-15 09:46 | Cancelled | GBXOIL | GBXPARTTS | MAVERICK | CBILLIG |  | 2024-12-18 07:31
1 | WTG-1100-NDG0-0000 | 3103118 | CMS HSS Inspection | 2023-03-27 09:36 | Closed | CMS | CMSHSS | TRAVERSE | CANGELORI |  | 2023-04-17 15:23
5 | WTG-0008-0000 | 3103302 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-27 16:39 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | ABARNDT |  | 2023-08-29 13:09
2 | WTG-3045-0000 | 3103796 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-03-28 12:30 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-02-26 12:26
1 | WTG-3024-0000 | 3110072 | GEARBOX OIL, Fix oil leak | 2023-04-07 14:06 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | ATHOMPSON |  | 2023-08-27 14:46
3 | WTG-0018-0000 | 3110862 | CMS Trouble Shoot (Invenergy request, non-GE) / SR# 6253088 & 6170202 | 2023-04-10 11:51 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2023-07-10 13:18
5 | WTG-0040A-NDGP-0000 | 3112379 | Secondary Oil Filter Leak | 2023-04-13 07:29 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2023-07-20 12:09
1 | WTG-0346-0000 | 3113537 | GEARBOX Replace oil cooler fan 2 speed motor number 1 | 2023-04-17 08:50 | Closed | GBXOIL | GBXOILCOOL | BISHOP HILL III | JPADILLA |  | 2023-04-17 13:21
3 | WTG-2062-0000 | 3113549 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-17 09:17 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2023-11-27 17:08
3 | WTG-1071-0000 | 3115499 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-04-21 11:05 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-09-09 10:35
5 | WTG-0009-NDGP-0000 | 3115553 | Replace hydraulic brake station hand pump | 2023-04-21 13:20 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2023-07-20 12:12
3 | WTG-0050-0000 | 3116347 | Oil sample needed | 2023-04-25 12:40 | Closed | GBXOIL | GBXOILSAMP | FORWARD | TBUYESKE |  | 2023-04-28 13:06
2 | WTG-00P6-NDG0-0000 | 3116820 | CMS Gearbox Borescope | 2023-04-26 10:47 | Closed | CMS | CMSGBXBORE | TATANKA RIDGE | CBILLIG |  | 2024-08-26 14:04
3 | WTG-0094-0000 | 3117990 | CMS Gearbox Borescope | 2023-04-28 11:05 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2023-08-22 08:57
5 | WTG-0010-0000 | 3119421 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-01 10:01 | Closed | CMS | CMSTRBLSHOOT | BLOOMING GROVE | ABARNDT |  | 2023-07-18 08:14
5 | WTG-3046-0000 | 3120709 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-02 14:18 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | JDKEY |  | 2023-08-02 12:04
2 | WTG-1028-0000 | 3132063 | CMS Main Bearing Borescope | 2023-05-24 11:43 | Closed | CMS | CMSMBBORE | TRAVERSE | ABARNDT |  | 2023-08-18 14:07
1 | WTG-0011-0000 | 3131924 | Posiedon inspection | 2023-05-24 09:41 | Closed | GBXOIL | GBXPARTTS | MAVERICK | MWEBER |  | 2023-07-08 11:18
1 | WTG-0012-0000 | 3131988 | Poseidon inspection | 2023-05-24 11:03 | Closed | GBXOIL | GBXPARTTS | MAVERICK | MWEBER |  | 2023-07-08 11:19
5 | WTG-0032-0000 | 3132274 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-05-24 15:23 | Closed | CMS | CMSTRBLSHOOT | BETHEL | CBILLIG |  | 2023-10-26 10:12
4 | WTG-0086-NDGP-0000 | 3132824 | Replace red spider insert on lube pump | 2023-05-25 12:48 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2023-08-02 09:54
1 | GBX-MOV-J51423 | 3133011 | WTG 005 LOW OIL LEVEL | 2023-05-26 08:42 | Closed | GBXOIL |  | BUFFALO MOUNT | VFRENCH |  | 2023-10-02 09:18
1 | WTG-0076-0000 | 3134308 | GEARBOX OIL, Fix oil leak | 2023-05-30 19:35 | Closed | GBXOIL | GBXOILLEAK | MAVERICK | AALATORRE |  | 2023-07-12 10:40
1 | WTG-0056-0000 | 3134407 | GEARBOX OIL, Particle counter troubleshooting | 2023-05-31 09:42 | Closed | GBXOIL | GBXPARTTS | MAVERICK | JMILES |  | 2023-07-12 10:09
1 | WTG-0034-0000 | 3135254 | Oil relief hose leak | 2023-06-01 11:05 | Closed | GBXOIL | GBXOILLEAK | WILLOW CREEK | CADAMS |  | 2023-06-08 15:23
5 | WTG-00K3-NDB0-0000 | 3141244 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-06-09 10:58 | Closed | CMS | CMSTRBLSHOOT | TATANKA RIDGE | CBILLIG |  | 2024-10-01 11:45
1 | WTG-0066-0000 | 3170893 | GEARBOX OIL, Fix oil leak | 2023-08-08 11:29 | Closed | GBXOIL | GBXOILLEAK | SUNDANCE | CPRUIT |  | 2023-10-04 13:30
2 | WTG-0048-NDG0-0000 | 3145234 | GEARBOX OIL, Add/Top-Off | 2023-06-21 16:18 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2024-04-29 12:53
1 | WTG-1134-0000 | 3145276 | GEARBOX OIL, Fix oil leak | 2023-06-21 17:17 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | ATHOMPSON |  | 2024-02-19 14:05
2 | WTG-0014-0000 | 3153567 | CMS Main Bearing Borescope | 2023-07-06 11:03 | Closed | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2023-07-18 10:30
1 | WTG-00E3-0000 | 3153099 | CMS Main Bearing Borescope | 2023-07-05 16:38 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | ABARNDT |  | 2023-07-07 18:12
3 | WTG-0E04-0000 | 3153968 | GEARBOX OIL, Particle counter troubleshooting | 2023-07-07 09:56 | Closed | GBXOIL | GBXPARTTS | JAYHAWK | ABARNDT |  | 2023-08-03 10:04
4 | WTG-0082-NDG0-0000 | 3154809 | Empty oil bucket under low speed shaft | 2023-07-10 10:46 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE
2 | WTG-0036-0000 | 3155613 | CMS Main Bearing Borescope | 2023-07-12 10:54 | Closed | CMS | CMSMBBORE | SUNDANCE | SDUNAVANT |  | 2023-07-18 12:36
3 | WTG-0074-0000 | 3157114 | CMS Gearbox Borescope | 2023-07-17 11:27 | Closed | CMS | CMSGBXBORE | UPSTREAM | ABARNDT |  | 2023-09-05 11:07
3 | WTG-0063-0000 | 3157123 | CMS Generator Bearing Check | 2023-07-17 12:12 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-08-28 14:44
3 | WTG-00E4-0000 | 3158239 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-07-19 11:24 | Closed | CMS | CMSTRBLSHOOT | TATANKA RIDGE | ABARNDT |  | 2024-02-29 15:01
5 | WTG-0043-NDGP-0000 | 3158721 | Replace red insert on gear oil pump | 2023-07-19 16:23 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2023-08-02 10:46
4 | WTG-0086-0000 | 3159432 | Add 5 Gallons of Oil & Replace Desiccant Filter | 2023-07-20 14:14 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2023-12-15 10:47
4.2 | WTG-0086-0000 | 3159435 | Replace Orange & Green GBX Oil Hose | 2023-07-20 14:17 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2024-06-10 09:43
2 | WTG-0094-0000 | 3160998 | CMS Gearbox Borescope | 2023-07-25 10:21 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | ABARNDT |  | 2023-09-20 08:43
2 | WTG-0103-0000 | 3169017 | CMS Main Bearing Borescope / SR# 6404968 | 2023-08-03 12:23 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2023-09-11 11:14
2 | WTG-0040-0000 | 3169016 | CMS Main Bearing Borescope/ SR# 6394242 | 2023-08-03 12:21 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2023-08-21 10:05
4 | WTG-0063A-0000 | 3170746 | Secondary filter leaking at shaft seal | 2023-08-08 07:15 | Cancelled | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2023-08-08 07:18
1 | WTG-0089-0000 | 3174848 | CMS Main Bearing Borescope | 2023-08-16 09:28 | Closed | CMS | CMSMBBORE | MAVERICK | AALATORRE |  | 2023-11-09 11:40
5 | WTG-3016-0000 | 3175135 | CMS Main Bearing Check | 2023-08-16 15:54 | Closed | CMS | CMSMB | TRAVERSE | JDKEY |  | 2024-01-05 12:26
5 | WTG-0026-NDB0-0000 | 3180163 | CMS Main Bearing Install | 2023-08-29 13:59 | Closed | CMS | CMSMB | SUNDANCE | TKORNELE |  | 2024-07-18 16:01
1 | WTG-0073-0000 | 3187412 | Poseidon inspection | 2023-09-07 15:14 | Closed | GBXOIL | GBXPARTTS | MAVERICK | JMILES |  | 2023-09-27 16:26
1 | WTG-0046-0000 | 3187380 | CMS Main Bearing Borescope | 2023-09-07 14:13 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2023-09-14 14:12
5 | WTG-0015-NT00-0000 | 3195409 | T15 CMS controler replaced by GE | 2023-09-22 13:17 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | TWESTERDAHL |  | 2023-09-22 13:33
3 | WTG-0061-0000 | 3197695 | CMS Generator Bearing Check | 2023-09-27 10:50 | Closed | CMS | CMSGENB | UPSTREAM | LXPEREZ |  | 2024-07-09 13:02
9 | SITE-WAKE1 | 3199666 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL | GBXOILCHG | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000074 | 3199894 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000075 | 3199895 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000076 | 3199896 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000077 | 3199897 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
1 | WTG-0001-0000 | 3200585 | CMS Main Bearing Borescope | 2023-10-03 11:34 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2023-10-09 09:04
1 | WTG-2001-0000 | 3130373 | No Errors | 2023-05-22 08:40 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | JCARTWRIGHT |  | 2023-05-24 09:09
1 | WTG-0009-0000 | 3131142 | Poseidon inspection | 2023-05-23 12:25 | Closed | GBXOIL | GBXPARTTS | MAVERICK | MWEBER |  | 2023-07-08 11:16
2 | WTG-0069-0000 | 3131949 | CMS Gearbox Borescope | 2023-05-24 10:38 | Cancelled | CMS | CMSGBXBORE | BLOOMING GROVE | ABARNDT |  | 2023-05-24 10:49
1 | WTG-0085-0000 | 3132247 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2023-05-24 10:39 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | SMILLER |  | 2023-05-30 09:49
1 | WTG-0084-0000 | 3137200 | Pich Axis 3 fault. Check WEPA | 2023-06-04 13:27 | Closed | CMS | BLANK | SANTA RITA EAST | MMILLER |  | 2023-06-04 14:16
1 | WTG-0056-0000 | 3139730 | CMS Main Bearing Borescope | 2023-06-07 09:49 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2023-06-12 12:12
3 | WTG-1041-0000 | 3140547 | CMS Generator Bearing Check | 2023-06-08 09:29 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2023-09-25 15:47
2 | WTG-2033-0000 | 3141239 | CMS Gearbox Borescope | 2023-06-09 10:43 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2024-01-02 16:37
1 | WTG-0119-0000 | 3141689 | GEARBOX OIL, Fix oil leak | 2023-06-11 10:50 | Closed | GBXOIL | GBXOILLEAK | BETHEL | AXRODRIGUEZ |  | 2023-06-20 09:19
2 | WTG-0003-0000 | 3142764 | CMS Gearbox Borescope | 2023-06-14 09:53 | Closed | CMS | CMSGBXBORE | UPSTREAM | ABARNDT |  | 2023-06-30 10:27
1 | WTG-0043-0000 | 3142629 | GEARBOX OIL, Fix oil leak | 2023-06-13 19:14 | Closed | GBXOIL | GBXOILLEAK | SUNDANCE | SDUNAVANT |  | 2023-07-18 14:07
3 | WTG-0008-0000 | 3148573 | CMS Generator Bearing Check | 2023-06-27 12:32 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-10-30 09:20
3 | WTG-1064-0000 | 3148628 | CMS Keyphasor Troubleshoot | 2023-06-27 14:49 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-11-11 10:34
3 | WTG-1138-0000 | 3148647 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-06-27 15:21 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-09-20 11:40
3 | WTG-0027-0000 | 3157111 | CMS Gearbox Borescope | 2023-07-17 11:20 | Closed | CMS | CMSGBXBORE | UPSTREAM | ABARNDT |  | 2023-08-09 10:20
5 | WTG-1111-0000 | 3161683 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-07-25 13:38 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-09-09 14:05
5 | WTG-3028-0000 | 3161687 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-07-25 13:58 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-02-26 12:23
4 | WTG-0025-0000 | 3162490 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-07-26 10:35 | Closed | CMS | CMSTRBLSHOOT | BETHEL | ABARNDT |  | 2023-10-30 09:27
2 | WTG-0095-0000 | 3164754 | CMS Gearbox Borescope | 2023-08-01 10:18 | Closed | CMS | CMSGBXBORE | DEUEL HARVEST | ABARNDT |  | 2023-08-03 14:59
1 | WTG-0011-NDG0-0000 | 3166719 | GEARBOX OIL, Oil Sample | 2023-08-01 15:51 | Closed | GBXOIL | GBXOILSAMP | GOLDTHWAITE | TRUMFIELD |  | 2023-08-03 09:28
5 | WTG-0095-0000 | 3169974 | SECONDARY GEARBOX OIL, Fix oil leak | 2023-08-05 09:36 | Closed | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE |  | 2023-09-19 12:28
2 | WTG-0028-0000 | 3174152 | MAIN BEARING, Main bearing borescope inspection | 2023-08-15 10:23 | Cancelled | CMS | CMSMBBORE | MAVERICK | AALATORRE |  | 2023-08-15 10:27
1 | WTG-2141-0000 | 3176286 | GEARBOX OIL, Fix oil leak | 2023-08-18 15:00 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | EBONILLA |  | 2023-11-14 14:52
4 | WTG-0050-0000 | 3177363 | GEARBOX OIL, Add/Top-Off 8-10 gallons | 2023-08-22 11:20 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-09-13 15:18
1 | WTG-0071-NDG0-0000 | 3180377 | GEARBOX OIL, Fix oil leak | 2023-08-29 16:42 | Closed | GBXOIL | GBXOILLEAK | GREXP | GBLATNIK |  | 2023-09-08 10:37
1 | WTG-0052-NDGP-0000 | 3182187 | Secondary oil leak | 2023-08-30 16:52 | Closed | GBXOIL | BLANK | JUDITH GAP | WBLYTHE |  | 2023-10-03 17:07
1 | WTG-0047-0000 | 3188163 | GEARBOX OIL, Fix oil leak | 2023-09-09 08:07 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MDUDLEY |  | 2023-09-18 15:07
1 | GBX-000123 | 3188164 | GEARBOX OIL, Fix oil leak | 2023-09-09 08:25 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | NCARBY |  | 2023-09-14 11:30
1 | WTG-0053-0000 | 3190251 | GEARBOX OIL, Fix oil leak | 2023-09-13 09:04 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | JEPLIN |  | 2024-04-18 11:49
3 | WTG-0079-0000 | 3196860 | CMS Main Bearing Borescope | 2023-09-25 16:02 | Closed | CMS | CMSMBBORE | BETHEL | ABARNDT |  | 2023-09-27 09:32
1 | GBX-WIN-4806470-0020-4 | 3197437 | WTG-006 LOW OIL PRESSURE | 2023-09-27 09:05 | Closed | GBXOIL |  | BUFFALO MOUNT | VFRENCH |  | 2023-12-29 18:42
9 | GBX-000019 | 3199860 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000022 | 3199861 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000024 | 3199862 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000025 | 3199863 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000030 | 3199864 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000031 | 3199865 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000033 | 3199866 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000034 | 3199867 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000035 | 3199868 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000036 | 3199869 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000037 | 3199870 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000039 | 3199871 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000055 | 3199883 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000056 | 3199884 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000057 | 3199885 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000058 | 3199886 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000059 | 3199887 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000060 | 3199888 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000063 | 3199889 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000065 | 3199890 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000067 | 3199891 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000069 | 3199892 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
9 | GBX-000071 | 3199893 | GEARBOX, Oil Changes - 2022 | 2023-10-02 09:57 | Closed | GBXOIL |  | WAKE 1 | JDEWEESE |  | 2023-10-02 15:46
2 | WTG-1122-0000 | 3200512 | CMS Gearbox Borescope | 2023-10-03 10:17 | Ready to Schedule | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2024-02-23 12:29
4 | WTG-0336-NDG0-0000 | 3200597 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-10-03 12:16 | Closed | CMS | CMSTRBLSHOOT | BISHOP HILL III | LXPEREZ |  | 2023-11-07 14:41
3 | WTG-0074-0000 | 3201840 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 15:57 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT
3 | WTG-1112-0000 | 3201860 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 16:38 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
3 | WTG-0012-0000 | 3201818 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 15:35 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT
3 | WTG-0033-0000 | 3201822 | GEARBOX OIL, Particle counter troubleshooting | 2023-10-04 15:38 | Closed | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT |  | 2025-04-01 12:04
1 | WTG-0208-0000 | 3202006 | CMS Main Bearing Borescope | 2023-10-05 09:49 | Closed | CMS | CMSMBBORE | BEECH RIDGE II | ABARNDT |  | 2023-10-11 13:43
4 | WTG-0039-0000 | 3201954 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2023-10-05 07:10 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-10-13 14:39
3 | WTG-3065-0000 | 3204137 | CMS Generator Bearing Check | 2023-10-09 13:48 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2023-12-07 10:33
2 | WTG-0002-NDB0-0000 | 3204146 | CMS Main Bearing Borescope | 2023-10-09 14:08 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | MWILSON |  | 2023-10-13 14:48
1 | WTG-0002C-0000 | 3207000 | Oil bucket installed | 2023-10-13 10:57 | Ready to Schedule | GBXOIL | GBXOILCOOL | FORWARD | PPOSTHUMA
1 | WTG-0022-0000 | 3207084 | GEARBOX OIL, Oil Sample | 2023-10-13 15:45 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | DKEETON |  | 2023-10-18 23:26
1 | WTG-0027-0000 | 3207085 | GEARBOX OIL, Oil Sample | 2023-10-13 15:45 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | DKEETON |  | 2023-10-15 18:56
1 | WTG-0028-0000 | 3207087 | GEARBOX OIL, Oil Sample | 2023-10-13 15:48 | Closed | GBXOIL | GBXOILSAMP | GUNSIGHT | DKEETON |  | 2023-10-13 17:29
1 | WTG-0086-NDG0-0000 | 3207038 | GEARBOX OIL, Fix radiator leak | 2023-05-16 16:23 | Ready to Schedule | GBXOIL |  | BUCKEYE | CPOLIFKA
4 | WTG-0037-0000 | 3208815 | O'Hain oil bucket installed( leaving open as a reminder to empty) | 2023-10-19 07:59 | Ready to Schedule | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN
1 | GBX-MOV-J51423 | 3208830 | WTG-005 LOW OIL LEVEL | 2023-10-19 08:21 | Closed | GBXOIL |  | BUFFALO MOUNT | VFRENCH |  | 2023-12-29 18:29
1 | GBX-000010 | 3208831 | WTG-010 LOW OIL LEVEL | 2023-10-19 08:23 | Closed | GBXOIL |  | BUFFALO MOUNT | VFRENCH |  | 2024-01-26 09:15
5 | WTG-0042-NDGP-0000 | 3209234 | GEARBOX OIL, leaking Oil Cooler | 2023-10-20 11:19 | Ready to Schedule | GBXOIL | GBXOILCOOL | WILLOW CREEK | NCURRIE
3 | WTG-0301-0000 | 3217711 | CMS Generator Bearing Check | 2023-11-01 16:55 | Closed | CMS | CMSGENB | BISHOP HILL III | LXPEREZ |  | 2023-11-03 15:28
5 | WTG-2073-0000 | 3218564 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-02 11:58 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | JCARTWRIGHT |  | 2023-11-27 16:48
5 | WTG-2118-0000 | 3218565 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-02 11:59 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | JCARTWRIGHT |  | 2023-12-12 12:49
2 | WTG-0029-0000 | 3218485 | CMS Generator Bearing Check | 2023-11-02 09:39 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-11-07 09:42
1 | WTG-0072-0000 | 3220067 | GEARBOX OIL, Fix oil leak | 2023-11-06 14:18 | Closed | GBXOIL | GBXOILLEAK | BETHEL | MTERRONES |  | 2023-11-07 09:17
5 | WTG-0016-NDGP-0000 | 3224018 | GEARBOX OIL, leaking Oil Cooler | 2023-11-10 11:26 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | CADAMS |  | 2023-11-17 08:59
3 | WTG-1085-0000 | 3355381 | CMS Gearbox Borescope | 2024-05-28 09:25 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2024-06-17 15:31
2 | WTG-0204-0000 | 3355036 | Leaking Radiator | 2024-05-24 16:42 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | NMCFARLAND |  | 2024-07-16 15:12
2 | WTG-0026-0000 | 3359052 | CMS Main Bearing Borescope | 2024-05-31 09:28 | Closed | CMS | CMSMBBORE | MAVERICK | AALATORRE |  | 2024-06-19 08:22
4 | WTG-0060A-0000 | 3228040 | GEARBOX OIL, Add/Top-Off 3-5 gallons | 2023-11-21 12:25 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2023-12-15 11:00
2 | WTG-0003-NDB0-0000 | 3243610 | CMS Main Bearing Borescope | 2023-12-15 11:04 | Closed | CMS | CMSMBBORE | SUNDANCE | LXPEREZ |  | 2024-01-02 13:44
1 | WTG-0015-0000 | 3244791 | Gearbox secondary filtration, Fix oil leak | 2023-12-20 08:52 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | TWIEDEMEIER |  | 2024-01-02 13:38
1 | WTG-0108-0000 | 3245233 | GEARBOX OIL, Fix oil leak | 2023-12-21 14:43 | Closed | GBXOIL | GBXOILLEAK | THUNDERHEAD | AKERKMAN |  | 2025-07-08 08:16
2 | WTG-0066-0000 | 3372499 | GEARBOX OIL, Add/Top-Off | 2024-06-25 15:27 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2024-09-23 12:20
2 | WTG-0045-0000 | 3313195 | CMS Main Bearing Borescope | 2024-03-05 11:30 | Closed | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2024-03-14 12:33
2 | WTG-0039-0000 | 3313203 | CMS Main Bearing Borescope | 2024-03-05 11:51 | Closed | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2024-03-14 12:33
2 | WTG-0087-0000 | 3314843 | CMS Main Bearing Borescope | 2024-03-08 07:53 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-03-14 12:15
2 | WTG-1039-0000 | 3317435 | CMS Main Bearing Borescope | 2024-03-14 14:36 | Closed | CMS | CMSMBBORE | TRAVERSE | ABARNDT |  | 2024-04-19 11:00
2 | WTG-0089-0000 | 3321258 | CMS Main Bearing Borescope | 2024-03-22 15:09 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | LXPEREZ |  | 2024-04-02 14:55
5 | WTG-0103-0000 | 3321606 | Main Bearing, Main Bearing Inspection Cover Plate Removal | 2024-03-25 09:13 | Closed | CMS | CMSMB | MAVERICK | JMILES |  | 2024-07-26 09:45
4 | WTG-1095-0000 | 3327366 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-04-01 15:40 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
1 | WTG-0011-0000 | 3328083 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-04-02 16:18 | Closed | GBXOIL | GBXOILCOOL | VANTAGE | CSCHRIOCK |  | 2024-04-08 12:56
1 | WTG-0045-0000 | 3331786 | GEARBOX OIL, Fix oil leak | 2024-04-10 10:23 | Closed | GBXOIL | GBXOILLEAK | STANTON | CINGRAM |  | 2024-04-10 13:13
5 | WTG-0034-0000 | 3333801 | CMS Generator Bearing Check | 2024-04-15 09:49 | Closed | CMS | CMSGENB | MAVERICK | ABARNDT |  | 2024-05-09 16:46
1 | WTG-0043-0000 | 3336479 | GEARBOX OIL, Fix oil leak | 2024-04-22 10:46 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | SMILLER |  | 2024-04-22 15:14
3 | WTG-0004-0000 | 3336463 | CMS Main Bearing Borescope | 2024-04-22 14:56 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-05-20 13:04
3 | WTG-3042-0000 | 3336516 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-04-22 16:19 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-05-21 07:12
3 | WTG-0057-0000 | 3227909 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-21 09:37 | Closed | CMS | CMSTRBLSHOOT | MAVERICK | ABARNDT |  | 2024-10-10 08:59
1 | WTG-2065-0000 | 3241239 | GEARBOX OIL, Fix oil leak | 2023-12-12 15:14 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | JCARTWRIGHT |  | 2023-12-21 10:36
4 | WTG-0023A-0000 | 3366339 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-06-11 11:47 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2024-10-09 11:13
2 | WTG-0066-0000 | 3241808 | CMS Main Bearing Borescope | 2023-12-13 10:15 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-02-14 17:49
1 | WTG-0346-0000 | 3243723 | CMS Gearbox Borescope | 2023-12-15 16:44 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | LXPEREZ |  | 2023-12-18 10:54
3 | WTG-00G1-0000 | 3244412 | CMS Generator Bearing Check | 2023-12-18 17:07 | Closed | CMS | CMSGENB | TATANKA RIDGE | LXPEREZ |  | 2024-08-29 08:59
1 | WTG-0115-0000 | 3369353 | GEARBOX OIL, Fix hoses | 2024-06-19 16:40 | Closed | GBXOIL | GBXOILLEAK | SCEXP | MBRAUNER |  | 2024-06-28 14:29
4 | WTG-0025-0000 | 3369225 | GEARBOX, Replace 0-10 Bar Pressure Gauge | 2024-06-19 12:50 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU
2 | WTG-0338-0000 | 3369326 | CMS Gearbox Borescope | 2024-06-19 16:15 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | LXPEREZ |  | 2024-06-25 11:55
5 | WTG-0021-0000 | 3369377 | GEARBOX OIL, Fix oil leak; oil pot hose | 2024-06-20 07:47 | Ready to Schedule | GBXOIL | GBXOILLEAK | TURKEY TRACK | JPROCTER
5 | WTG-0074-0000 | 3369264 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-06-19 13:41 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2024-06-27 14:15
2 | WTG-0026-0000 | 3369244 | CMS Main Bearing Borescope | 2024-06-19 13:33 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2024-06-27 09:12
3 | WTG-00J1-0000 | 3255583 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-18 10:40 | Closed | GBXOIL | GBXPARTTS | TATANKA RIDGE | ABARNDT |  | 2024-09-16 12:35
1 | WTG-3009-0000 | 3258369 | GEARBOX OIL, Fix oil leak | 2024-01-25 11:29 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | BMERRITT |  | 2024-02-13 16:00
1 | WTG-0063-0000 | 3517568 | GEARBOX OIL, Fix oil leak | 2025-03-03 15:29 | Ready to Schedule | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT
4 | WTG-0053-0000 | 3535218 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-03-27 13:19 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
5 | WTG-0050-0000 | 3535276 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-03-27 15:17 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN
5 | WTG-0008-0000 | 3538034 | Onxy CMS troubleshoot | 2025-04-02 08:52 | Ready to Schedule | CMS | CMSTRBLSHOOT | WAKE 1 | LCOPELAND
5 | WTG-0071-0000 | 3538047 | Onxy CMS troubleshoot | 2025-04-02 09:06 | Closed | CMS | CMSTRBLSHOOT | WAKE 1 | LCOPELAND |  | 2025-04-17 14:33
5 | WTG-0032-0000 | 3538035 | Onxy CMS troubleshoot | 2025-04-02 08:56 | Ready to Schedule | CMS | CMSTRBLSHOOT | WAKE 1 | LCOPELAND
5 | WTG-0068-0000 | 3538036 | Onxy CMS troubleshoot | 2025-04-02 08:57 | Closed | CMS | CMSTRBLSHOOT | WAKE 1 | LCOPELAND |  | 2025-06-11 14:45
5 | WTG-0074-0000 | 3538038 | Onxy CMS troubleshoot | 2025-04-02 08:57 | Ready to Schedule | CMS | CMSTRBLSHOOT | WAKE 1 | LCOPELAND
5 | WTG-0084-0000 | 3538039 | Onxy CMS troubleshoot | 2025-04-02 08:58 | Ready to Schedule | CMS | CMSTRBLSHOOT | WAKE 1 | LCOPELAND
5 | WTG-0101-0000 | 3538040 | Onxy CMS troubleshoot | 2025-04-02 08:58 | Ready to Schedule | CMS | CMSTRBLSHOOT | WAKE 1 | LCOPELAND
5 | WTG-0108-0000 | 3538041 | Onxy CMS troubleshoot | 2025-04-02 08:59 | Closed | CMS | CMSTRBLSHOOT | WAKE 1 | LCOPELAND |  | 2025-06-12 16:32
5 | WTG-0045-0000 | 3541021 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-04-09 14:48 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN
1 | WTG-0060-0000 | 3541015 | GEARBOX OIL, Add/Top-Off/hose replacement | 2025-04-09 13:34 | Ready to Schedule | GBXOIL | GBXOILADD | BUCKEYE | MLEGLEITER
4 | WTG-0107-0000 | 3541018 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2025-04-09 13:50 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
1 | WTG-0029-0000 | 3550142 | Oil pump inversion | 2025-04-24 10:41 | Ready to Schedule | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | ZMUELLER
1 | WTG-0024-NDGP-0000 | 3550108 | OIL PUMP INVERSION | 2025-04-24 10:13 | Ready to Schedule | GBXOIL | GBXOILCOOL | WOLVERINE CREEK | BPONCE
2 | WTG-0016-0000 | 3318138 | CMS Main Bearing Borescope | 2024-03-18 09:20 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-04-26 13:33
5 | WTG-0088-0000 | 3214922 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-10-30 13:27 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-11-11 09:29
5 | WTG-0002-0000 | 3217119 | CMS Generator Bearing Check | 2023-11-01 12:15 | Closed | CMS | CMSGENB | UPSTREAM | LXPEREZ |  | 2023-11-29 21:22
5 | WTG-0103-NDB0-0000 | 3355341 | main bearing seal replacement | 2024-05-28 08:22 | Closed | CMS | CMSMB | NUMBER 3 WIND | ZTAYLOR |  | 2024-06-04 06:57
1 | WTG-1039-0000 | 3358956 | Main Bearing inspection | 2024-05-31 07:45 | Closed | CMS | CMSMB | TRAVERSE | BWALLIS |  | 2024-09-20 11:59
2 | WTG-0043-NDG0-0000 | 3468258 | GEARBOX OIL, Add/Top-Off | 2024-11-22 15:55 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2024-12-09 13:59
1 | WTG-0044-N000-0000 | 3468349 | Gearbox Oil Leak | 2024-11-23 15:41 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | THUEY |  | 2024-11-26 11:52
5 | NUM3 | 3492826 | CMS Generator Bearing Check | 2025-01-10 11:36 | Ready to Schedule | CMS | CMSGENB | INVSVC | MKOKURIN
1 | WTG-0095-0000 | 3354425 | GEARBOX OIL, Fix oil leak | 2024-05-23 13:48 | Completed Awaiting Review | GBXOIL | GBXOILLEAK | BUCKEYE | MLEGLEITER |  | 2025-06-12 14:38
2 | WTG-0007-0000 | 3228026 | CMS Gearbox Borescope | 2023-11-21 12:12 | Closed | CMS | CMSGBXBORE | UPSTREAM | LXPEREZ |  | 2023-12-04 13:26
2 | WTG-0024-0000 | 3228001 | CMS Main Bearing Borescope | 2023-11-21 10:39 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | LXPEREZ |  | 2024-02-08 11:30
2 | WTG-0009-0000 | 3244170 | Main Bearing Inspection | 2023-12-18 09:07 | Closed | CMS | CMSMBBORE | DEUEL HARVEST | CNIEMANN |  | 2023-12-21 10:30
3 | WTG-0205-0000 | 3244247 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-12-18 12:51 | Closed | CMS | CMSTRBLSHOOT | BEECH RIDGE II | ABARNDT |  | 2024-08-13 16:16
5 | WTG-0116-0000 | 3244483 | GEARBOX OIL, Fix oil leak | 2023-12-19 09:02 | Closed | GBXOIL | GBXOILLEAK | SCEXP | NCLEMENTS |  | 2024-04-30 17:15
1 | WTG-0037-0000 | 3244487 | Clean up gearbox oil leak | 2023-12-19 09:06 | Closed | GBXOIL | GBXOILLEAK | DEUEL HARVEST | AMONNIER |  | 2023-12-21 10:29
2 | WTG-1004-0000 | 3244830 | CMS Gearbox Borescope | 2023-12-20 11:36 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2024-01-02 09:35
3 | WTG-2005-0000 | 3369425 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-06-20 10:19 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-10-17 07:20
1 | WTG-0042-0000 | 3372370 | CMS Main Bearing Borescope | 2024-06-25 12:10 | Closed | CMS | CMSMBBORE | UPSTREAM | AXADAMS |  | 2024-08-15 12:29
1 | WTG-0121-0000 | 3261128 | GEARBOX OIL, Fix oil leak | 2024-01-24 09:07 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MHUFF |  | 2024-01-31 15:27
2 | WTG-0094-0000 | 3327250 | CMS Gearbox Borescope | 2024-04-01 13:37 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | BVANVALKENBURG |  | 2024-04-02 14:42
5 | WTG-0029A-0000 | 3328212 | Gearbox oil leak from the front (O'Hain Oil Bucket, etc) and 5 gallons of oil | 2024-04-03 09:01 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2024-10-25 16:56
1 | WTG-0035-0000 | 3328214 | GEARBOX OIL, Fix oil leak | 2024-04-03 09:17 | Closed | GBXOIL | GBXOILLEAK | STANTON | MROMAN |  | 2024-04-03 16:11
2 | WTG-0098-0000 | 3333751 | GEARBOX OIL, Secondary filter leak | 2024-04-15 08:49 | Cancelled | GBXOIL | GBXFILTINS | JUDITH GAP | CROBERTS |  | 2024-05-23 14:04
1 | WTG-1058-0000 | 3335811 | GEARBOX OIL, Oil Sample | 2024-04-19 11:05 | Closed | GBXOIL | GBXOILSAMP | TRAVERSE | ATHOMPSON |  | 2024-04-26 12:54
4 | WTG-0018-0000 | 3335878 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-04-19 13:47 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-05-08 15:42
2 | WTG-0D03-0000 | 3242796 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2023-12-14 15:01 | Closed | GBXOIL | GBXOILCOOL | HIGH SHELDON | DPANFIL |  | 2025-06-25 10:15
2 | WTG-0067-0000 | 3250294 | CMS Main Bearing Borescope | 2024-01-04 14:47 | Closed | CMS | CMSMBBORE | GOLDTHWAITE | WHALL |  | 2024-02-02 14:16
3 | WTG-0021-0000 | 3255553 | CMS Gearbox Borescope | 2024-01-18 09:11 | Closed | CMS | CMSGBXBORE | MAVERICK | ABARNDT |  | 2024-02-19 16:57
3 | WTG-00A5-0000 | 3255592 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-18 11:07 | Closed | GBXOIL | GBXPARTTS | COYOTE RIDGE | ABARNDT |  | 2024-04-09 14:51
4 | WTG-0083-0000 | 3508785 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-02-20 15:34 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2025-02-27 15:23
4 | WTG-0083-0000 | 3508784 | Replace Orange Winergy Hose | 2025-02-20 15:11 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2025-02-27 15:23
3.1 | WTG-0073-0000 | 3318168 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-03-18 09:31 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-04-26 13:33
1 | WTG-0035-0000 | 3323111 | GEARBOX OIL, Secondary filter leak | 2024-03-25 16:27 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | DMULLENS |  | 2024-04-12 12:34
1 | WTG-0087-0000 | 3553029 | GEARBOX OIL, Fix radiator leak | 2025-05-01 15:38 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | ZNASH |  | 2025-05-29 14:28
1 | WTG-0076-0000 | 3553040 | GEARBOX OIL, Fix radiator leak | 2025-05-01 15:45 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2025-05-30 14:35
2 | WTG-1017-0000 | 3328838 | CMS Main Bearing Borescope | 2024-04-04 10:48 | Closed | CMS | CMSMBBORE | TRAVERSE | ABARNDT |  | 2024-07-01 10:13
1 | WTG-0G05-N000-0000 | 3328798 | CC Jenson Motor replacement | 2024-04-04 09:28 | Closed | GBXOIL | GBXFILTINS | HIGH SHELDON | BHUNTER |  | 2024-08-08 09:57
1 | BMEC-DT-005 | 3328840 | WTG 005 LOW GEARBOX OIL | 2024-04-04 10:52 | Closed | GBXOIL |  | BUFFALO MOUNT | VFRENCH |  | 2024-06-07 14:56
1 | WTG-0034-0000 | 3354017 | Gearbox secondary leak | 2024-05-22 13:00 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | ZNASH |  | 2024-11-11 12:25
1 | WTG-3040-0000 | 3230524 | GEARBOX OIL, Fix oil leak | 2023-11-29 13:37 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | QCROUSE |  | 2024-01-05 12:52
3 | WTG-0007-0000 | 3233040 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-12-04 09:29 | Ready to Schedule | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2024-11-25 07:38
2 | WTG-0025-0000 | 3233055 | CMS Main Bearing Borescope | 2023-12-04 09:46 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2023-12-21 10:43
3 | WTG-0102-0000 | 3233074 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-12-04 10:27 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2023-12-21 10:43
3 | WTG-0013-0000 | 3252883 | CMS Main Bearing Borescope | 2024-01-11 13:55 | Closed | CMS | CMSMBBORE | BETHEL | ABARNDT |  | 2024-01-22 09:21
3 | WTG-0078-0000 | 3263782 | CMS HSS Check | 2024-01-31 10:26 | Closed | CMS | CMSHSS | UPSTREAM | LXPEREZ |  | 2024-03-18 16:33
1 | WTG-0140-NDG0-0000 | 3535075 | GEARBOX OIL, Fix oil leak | 2025-03-27 10:14 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE IV | RHAYS |  | 2025-06-09 11:45
2 | WTG-0068-0000 | 3537967 | CMS Main Bearing Borescope | 2025-04-01 16:41 | Closed | CMS | CMSMBBORE | PLYMOUTH | BAZEFIELD |  | 2025-04-08 08:52
2 | WTG-0062-0000 | 3537968 | GEARBOX OIL, Particle counter leak | 2025-04-01 16:42 | In Progress | GBXOIL | GBXPARTINS | BLOOMING GROVE | JDISS
2 | WTG-00H3-0000 | 3308853 | CMS Gearbox Borescope | 2024-02-26 16:47 | Closed | CMS | CMSGBXBORE | TATANKA RIDGE | LXPEREZ |  | 2024-03-07 13:11
2 | WTG-0034-0000 | 3310459 | CMS Gearbox Borescope | 2024-02-29 14:23 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | LXPEREZ |  | 2024-03-07 13:46
1 | WTG-0219-0000 | 3310484 | GEARBOX OIL, Replace oil pump | 2024-02-29 15:20 | Closed | GBXOIL | GBXOILCOOL | PRAIRIE BREEZE2 | NMCFARLAND |  | 2024-03-22 16:24
2 | WTG-0014-NDG0-0000 | 3314538 | GEARBOX OIL, Add/Top-Off | 2024-03-07 15:54 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2025-01-13 16:06
2 | WTG-0013-NDG0-0000 | 3314540 | GEARBOX OIL, Add/Top-Off | 2024-03-07 15:56 | Cancelled | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2024-08-07 09:12
3 | WTG-0074-0000 | 3316188 | GEARBOX OIL, Particle counter installation | 2024-03-12 15:01 | Closed | GBXOIL | GBXPARTINS | UPSTREAM | ABARNDT |  | 2024-11-08 15:06
2 | WTG-0030-0000 | 3316218 | MAIN BEARING, Main bearing borescope inspection | 2024-03-12 15:43 | Closed | CMS | CMSMB | GOLDTHWAITE | BMARTIN |  | 2024-03-15 11:07
2 | WTG-0030-0000 | 3321244 | CMS Gearbox Borescope | 2024-03-22 14:05 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | LXPEREZ |  | 2024-04-02 14:38
2 | WTG-0090-0000 | 3321198 | CMS Main Bearing Borescope | 2024-03-22 11:30 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | LXPEREZ |  | 2024-05-01 14:26
1 | WTG-0049-0000 | 3492796 | GEARBOX OIL, Fix oil leak | 2025-01-10 11:02 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | APEREZ |  | 2025-01-12 14:59
1 | WTG-0066-0000 | 3324469 | GEARBOX OIL, Fix oil leak | 2024-03-27 14:30 | Ready to Schedule | GBXOIL | GBXOILLEAK | BUCKEYE | MLEGLEITER
2 | WTG-0053-0000 | 3326983 | CMS Gearbox Borescope | 2024-04-01 10:03 | Closed | CMS | CMSGBXBORE | BETHEL | ABARNDT |  | 2024-04-23 16:07
3 | WTG-0088-0000 | 3326984 | CMS Generator Bearing Check | 2024-04-01 10:13 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2024-04-15 09:31
2 | WTG-0046-0000 | 3329426 | CMS Main Bearing Borescope | 2024-04-05 09:14 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-04-23 07:52
1 | WTG-0087-0000 | 3552834 | GEARBOX OIL, Replace oil cooler | 2025-05-01 14:12 | Ready to Schedule | GBXOIL | GBXOILCOOL | GREXP | MOMILANOWSKI
1 | WTG-0103-0000 | 3332347 | GEARBOX OIL, Fix oil leak | 2024-04-11 15:41 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CPOLIFKA |  | 2024-04-16 08:02
1 | WTG-0033-0000 | 3333655 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-04-12 07:15 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | KYARNOLD |  | 2024-04-15 09:14
1 | WTG-0137-0000 | 3333656 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-04-12 07:20 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | KYARNOLD |  | 2024-04-15 09:14
4 | WTG-0040A-0000 | 3335579 | Add 5 gallons/ 10 pig mats | 2024-04-18 12:23 | Closed | GBXOIL | GBXOILADD | FORWARD | TBUYESKE |  | 2024-10-09 11:12
2 | WTG-0054-0000 | 3337076 | CMS Gearbox Borescope | 2024-04-24 11:09 | Closed | CMS | CMSGBXBORE | DEUEL HARVEST | LXPEREZ |  | 2024-06-06 11:14
2 | WTG-0073-0000 | 3569329 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-06-02 09:35 | Ready to Schedule | CMS | CMSTRBLSHOOT | CHICKASAW | ABARNDT
2 | WTG-0A18-NDB0-0000 | 3572089 | CMS Main Bearing Borescope | 2025-06-03 14:04 | Closed | CMS | CMSMBBORE | BEECH RIDGE | MHARRISON |  | 2025-06-17 14:41
4.2 | WTG-2005-0000 | 3346092 | CMS Main Bearing Check | 2024-05-03 09:31 | Closed | CMS | CMSMB | TRAVERSE | JCARTWRIGHT |  | 2024-05-07 10:58
3 | WTG-0083-0000 | 3348812 | CMS Gearbox Borescope | 2024-05-09 09:16 | Closed | CMS | CMSGBXBORE | BETHEL | ABARNDT |  | 2024-05-16 11:41
3 | WTG-0110-0000 | 3351391 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-05-15 14:35 | Closed | CMS | CMSTRBLSHOOT | BETHEL | LXPEREZ |  | 2025-04-29 14:13
2 | WTG-0J07-0000 | 3351409 | CMS Main Bearing Borescope | 2024-05-15 15:04 | Closed | CMS | CMSMBBORE | JAYHAWK | LXPEREZ |  | 2024-05-21 09:30
2 | WTG-0073-0000 | 3497095 | Oil leak from pump or plate seals | 2025-01-17 13:10 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE
5 | WTG-2135-0000 | 3380778 | Yaw hydr. pump time too long | 2024-07-09 07:31 | Closed | CMS | CMSMB | TRAVERSE | CMIXON |  | 2024-08-08 09:09
4 | WTG-0016-0000 | 3386267 | Secondary filter leaking at shaft seal / Replace GBX desiccant | 2024-07-15 09:51 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2024-09-23 12:20
2 | WTG-0083-NDB0-0000 | 3386272 | CMS Main Bearing Borescope | 2024-07-15 12:56 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | MWILSON |  | 2024-07-30 14:04
4 | WTG-0090-0000 | 3388769 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-07-18 12:11 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-09-23 11:53
4.1 | WTG-0026-0000 | 3438583 | GEARBOX OIL, Replace oil cooler rad. | 2024-09-27 09:03 | Ready to Schedule | GBXOIL | GBXOILCOOL | SPRING CANYON | BBUSS
1 | WTG-0018-ND00-0000 | 3438600 | GEARBOX OIL, Fix oil leak | 2024-09-27 10:22 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | RHAYS |  | 2024-10-15 15:00
5 | WTG-0120-0000 | 3441263 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-10-02 14:40 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2024-10-07 07:50
4 | WTG-0013-0000 | 3449268 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2024-10-21 12:09 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2025-03-03 12:47
2 | WTG-0008-0000 | 3454470 | GEARBOX OIL, Particle counter troubleshooting | 2024-10-31 13:51 | Ready to Schedule | GBXOIL | GBXPARTTS | BLOOMING GROVE | ABARNDT
1 | WTG-0012-0000 | 3227522 | GEARBOX OIL, Secondary filter system installation | 2023-11-20 10:44 | Closed | GBXOIL | GBXFILTINS | SPRING CANYON | MBRAUNER |  | 2023-11-20 15:48
2 | WTG-1036-0000 | 3365911 | CMS Main Bearing Borescope | 2024-06-10 14:36 | Closed | CMS | CMSMBBORE | TRAVERSE | ABARNDT |  | 2024-06-17 15:28
4 | WTG-1087-0000 | 3255299 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 10:57 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
4 | WTG-1047-0000 | 3255304 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 11:23 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
4 | WTG-1082-0000 | 3255306 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 11:32 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
4 | WTG-1086-0000 | 3255307 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 11:34 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
4 | WTG-1101-0000 | 3255309 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 11:45 | Closed | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT |  | 2025-05-07 12:22
2 | WTG-0100-0000 | 3255288 | CMS Main Bearing Borescope | 2024-01-17 09:42 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-01-31 17:47
4 | WTG-2055-0000 | 3255321 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 12:21 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
4 | WTG-2101-0000 | 3255325 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 12:33 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
4 | WTG-2027-0000 | 3255317 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 12:15 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
4 | WTG-2070-0000 | 3255324 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 12:29 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
4 | WTG-2122-0000 | 3255330 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 12:47 | Closed | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT |  | 2024-12-17 12:24
4 | WTG-3002-0000 | 3255342 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 14:05 | Closed | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT |  | 2024-07-01 08:53
2 | WTG-0082-0000 | 3318129 | CMS Main Bearing Borescope | 2024-03-18 09:12 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-04-26 13:34
3 | WTG-0043-0000 | 3318155 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-03-18 09:25 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-03-21 10:04
2 | WTG-0006-0000 | 3318172 | CMS Main Bearing Borescope | 2024-03-18 09:39 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-03-20 10:06
5 | WTG-0026-0000 | 3233126 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-12-04 13:28 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | ABARNDT |  | 2024-09-19 16:26
1 | WTG-0328-0000 | 3302363 | CMS Gearbox Borescope | 2024-02-19 10:38 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | ABARNDT |  | 2024-02-20 15:11
4 | WTG-0011-0000 | 3255408 | Gearbox oil too low- bring 5 gallons | 2024-01-17 15:42 | Closed | GBXOIL | GBXOILADD | FORWARD | TBUYESKE |  | 2024-05-08 14:53
5 | WTG-0084-0000 | 3517479 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-03-03 14:35 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN
2 | WTG-0028-0000 | 3308716 | Secondary Oil leak | 2024-02-26 10:38 | Closed | GBXOIL | GBXFILTELEM | FORWARD | JLAWRENCE |  | 2024-03-19 15:35
1 | GBX-00009 | 3308732 | GEARBOX OIL, Fix oil leak | 2024-02-26 14:19 | In Progress | GBXOIL | GBXOILLEAK | BLOOMING GROVE | MWILSON
2 | WTG-0102-0000 | 3310444 | CMS Main Bearing Borescope | 2024-02-29 13:24 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-03-06 16:39
2 | WTG-0009-0000 | 3310465 | CMS Gearbox Borescope | 2024-02-29 14:56 | Cancelled | CMS | CMSMBBORE | DEUEL HARVEST | LXPEREZ |  | 2024-03-04 10:23
4 | WTG-0026-0000 | 3310462 | O'Hain Oil Bucket LLC Installation | 2024-02-29 14:48 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2024-03-19 15:35
1 | WTG-0G16-0000 | 3310504 | CMS Gearbox Borescope | 2024-02-29 16:49 | Closed | CMS | CMSGBXBORE | JAYHAWK | ABARNDT |  | 2024-03-01 15:51
2 | WTG-0074-0000 | 3319546 | GEARBOX OIL, Secondary filter system element change | 2024-03-19 16:58 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | TWIEDEMEIER |  | 2024-05-03 12:28
3 | WTG-0006-0000 | 3326966 | CMS Generator Bearing Check | 2024-04-01 09:51 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2024-05-30 15:08
2 | WTG-0062-0000 | 3329429 | CMS Main Bearing Borescope | 2024-04-05 09:20 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-04-30 14:42
3 | SYS-WTG-RBEC | 3331663 | Particle Counter Installation - All Turbines | 2024-04-09 18:26 | Closed | GBXOIL | BLANK | RED BARN | POSHANNESSY |  | 2024-05-16 12:40
1 | WTG-0052-0000 | 3332997 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-04-12 15:38 | Closed | GBXOIL | GBXOILCOOL | GOLDTHWAITE | ZMILLER |  | 2024-04-17 15:16
2 | WTG-0021-0000 | 3335634 | CMS Gearbox Borescope | 2024-04-18 15:09 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | JDWILLIAMS |  | 2024-04-19 14:51
1 | WTG-0091-0000 | 3336975 | GEARBOX OIL CLEAN UP | 2024-04-24 07:59 | Closed | GBXOIL | GBXOILLEAK | DEUEL HARVEST | JESCAMILLAVIGIL |  | 2024-05-13 09:12
3 | WTG-0093-0000 | 3569327 | CMS Generator Bearing Check | 2025-06-02 09:25 | Closed | CMS | CMSGENB | PLYMOUTH | BAZEFIELD |  | 2025-06-04 14:32
2 | WTG-0007-0000 | 3343357 | CMS Main Bearing Borescope | 2024-04-29 14:58 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-05-28 09:48
1 | WTG-0022-0000 | 3343321 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-04-29 13:59 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | KYARNOLD |  | 2024-06-10 07:33
2 | WTG-0095-0000 | 3343366 | CMS Main Bearing Borescope | 2024-04-29 15:08 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-06-13 16:25
2 | WTG-0023-0000 | 3348797 | Secondary Gearbox Borescope | 2024-05-09 08:48 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | JWWILSON |  | 2024-05-13 08:56
2 | WTG-0062-0000 | 3497139 | GEARBOX OIL, Fix oil leak | 2025-01-17 15:33 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | THOLZ |  | 2025-06-10 14:09
3 | WTG-0049-0000 | 3388801 | CMS Generator Bearing Check | 2024-07-18 15:58 | Closed | CMS | CMSGENB | UPSTREAM | LXPEREZ |  | 2024-10-08 15:18
5 | WTG-0021-0000 | 3399245 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-08-07 11:38 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | LXPEREZ |  | 2025-07-01 14:10
4 | WTG-0013-0000 | 3420282 | Secondary filter pump has small leak from shaft seal | 2024-09-09 15:20 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2024-10-25 16:56
4.2 | WTG-0025-0000 | 3443896 | GBX Thermal Bypass Valve Flip | 2024-10-09 07:42 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2024-10-25 16:56
4 | WTG-0082-0000 | 3454458 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-10-31 11:58 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2025-01-30 15:44
3 | WTG-1010-0000 | 3227523 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-20 10:43 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-11-06 12:14
3 | WTG-0035-0000 | 3227552 | CMS Generator Bearing Check | 2023-11-20 11:28 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2023-11-22 09:53
4 | WTG-0081-0000 | 3353813 | Add 5 Gal Oil/ Replace Secondary Seal | 2024-05-22 12:16 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2025-01-26 07:50
2 | WTG-0022-0000 | 3358125 | CMS Main Bearing Borescope | 2024-05-30 09:49 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-06-19 15:25
1 | WTG-0049-0000 | 3247241 | GEARBOX OIL, Fix oil leak | 2023-12-29 16:24 | Closed | GBXOIL | GBXOILLEAK | BETHEL | ASANCHEZ |  | 2023-12-29 16:39
4 | WTG-3003-0000 | 3255343 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 14:10 | Closed | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT |  | 2024-07-01 08:53
4 | WTG-0019-0000 | 3255344 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 14:27 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | ABARNDT |  | 2024-02-01 12:26
4 | WTG-1030-0000 | 3255302 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 11:18 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
4 | WTG-1058-0000 | 3255305 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 11:28 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
4 | WTG-1092-0000 | 3255308 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 11:38 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
4 | WTG-2063-0000 | 3255323 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 12:25 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
2 | WTG-2060-0000 | 3298693 | CMS Main Bearing Borescope | 2024-02-12 10:00 | Closed | CMS | CMSMBBORE | TRAVERSE | ABARNDT |  | 2024-03-11 12:41
1 | WTG-0013-0000 | 3505428 | GEARBOX OIL, Fix oil leak | 2025-02-10 10:15 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MMEADOWS |  | 2025-02-10 15:13
3 | WTG-0034-0000 | 3505524 | CMS Generator Bearing Check | 2025-02-10 13:55 | Closed | CMS | CMSGENB | DEUEL HARVEST | BAZEFIELD |  | 2025-02-12 16:11
1 | WTG-0131-0000 | 3523263 | Oil Cooler Exchange | 2025-03-14 07:51 | Closed | GBXOIL | GBXOILCOOL | GREXP | HMONTERASTELLI |  | 2025-03-25 18:05
3 | WTG-0031-0000 | 3312706 | CMS Gearbox Borescope | 2024-03-04 14:07 | Closed | CMS | CMSGBXBORE | BETHEL | ABARNDT |  | 2024-03-21 10:12
2 | WTG-0074-0000 | 3540701 | GEARBOX OIL, Particle counter removal | 2025-04-08 11:33 | Closed | GBXOIL | GBXPARTREM | UPSTREAM | RKUDERA |  | 2025-04-09 08:56
1 | WTG-0049-0000 | 3314445 | GEARBOX CCJ FIX | 2024-03-07 13:27 | Closed | GBXOIL | GBXOILLEAK | VANTAGE | CSCHRIOCK |  | 2025-03-28 17:09
9 | WTG-0020-0000 | 3316128 | GBX leaking from middle heater in the back (See comments) | 2024-03-12 12:45 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN
1 | WTG-0134-0000 | 3549766 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-04-23 09:55 | Ready to Schedule | GBXOIL | GBXOILCOOL | MIAMI 1 | JSTEEN
1 | WTG-0068-0000 | 3549790 | GEARBOX OIL, Fix radiator leak | 2025-04-23 11:12 | Ready to Schedule | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT
1 | WTG-0011-0000 | 3317712 | GEARBOX OIL, Fix radiator leak | 2024-03-15 09:07 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | ZNASH |  | 2024-04-22 08:03
1 | WTG-0097-0000 | 3317740 | CMS Gearbox Borescope | 2024-03-15 09:56 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2024-03-22 08:53
2 | WTG-0002-0000 | 3319476 | CMS Main Bearing Borescope | 2024-03-19 15:09 | Closed | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2024-08-13 08:04
1 | WTG-0014-NDGP-0000 | 3319499 | GBX Oil Cooler/Radiator Replacment | 2024-03-19 15:41 | Closed | GBXOIL | GBXOILCOOL | GRAND RIDGE | JSENICA |  | 2024-04-16 12:42
1 | WTG-0036-0000 | 3319471 | GEARBOX OIL, Replace oil cooler | 2024-03-19 15:04 | Closed | GBXOIL | GBXOILCOOL | BUCKEYE | MLEGLEITER |  | 2024-03-20 15:27
2 | WTG-00G3-0000 | 3320409 | CMS Main Bearing Borescope | 2024-03-21 17:06 | Closed | CMS | CMSMBBORE | COYOTE RIDGE | LXPEREZ |  | 2024-04-15 09:09
1 | WTG-0040-0000 | 3320358 | GEARBOX OIL, Fix radiator leak | 2024-03-21 15:55 | Ready to Schedule | GBXOIL | GBXOILLEAK | BUCKEYE | CPOLIFKA
2 | WTG-0027-0000 | 3320394 | CMS Main Bearing Borescope | 2024-03-21 16:40 | Closed | CMS | CMSMBBORE | DEUEL HARVEST | LXPEREZ |  | 2024-04-04 12:45
2 | WTG-0010-0000 | 3321133 | Gearbox borescope inspection | 2024-03-22 10:17 | Closed | CMS | CMSGBXBORE | MCADOO | MGIVENS |  | 2024-03-27 15:22
2 | WTG-0002-0000 | 3323535 | CMS Main Bearing Borescope | 2024-03-26 12:07 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | LXPEREZ |  | 2024-04-02 14:54
1 | WTG-0027-0000 | 3326010 | GEARBOX OIL, Secondary filter system installation | 2024-03-28 13:57 | In Progress | GBXOIL | GBXFILTINS | BUCKEYE | MLEGLEITER
5 | WTG-3053-0000 | 3325981 | Main Bearing Seal | 2024-03-28 09:51 | Closed | CMS | CMSMB | TRAVERSE | CHARDWICK |  | 2024-04-19 09:46
1 | WTG-0059-0000 | 3330106 | GEARBOX OIL, Fix oil leak | 2024-04-06 16:02 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | MOMILANOWSKI |  | 2024-04-18 11:59
2 | WTG-0098-0000 | 3330873 | CMS Main Bearing Borescope | 2024-04-08 13:09 | Closed | CMS | CMSMBBORE | MIAMI 1 | JTHOMAS |  | 2024-04-09 07:29
2 | WTG-0022-0000 | 3330874 | CMS Main Bearing Borescope | 2024-04-08 13:11 | Closed | CMS | CMSMBBORE | MIAMI 1 | JTHOMAS |  | 2024-04-09 07:29
2 | WTG-0047-0000 | 3331468 | CMS Main Bearing Borescope | 2024-04-09 10:23 | Closed | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2024-04-22 16:30
3 | WTG-1131-0000 | 3332165 | CMS Gearbox Borescope | 2024-04-11 10:46 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2024-10-16 14:51
1 | WTG-0017-0000 | 3332807 | GEARBOX OIL, Fix oil leak | 2024-04-12 09:53 | Closed | GBXOIL | GBXOILLEAK | BETHEL | JGARLAND |  | 2024-04-15 09:30
4 | WTG-0075B-0000 | 3332899 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-04-12 11:08 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-05-08 15:35
1 | WTG-0043-0000 | 3334166 | CMS Gearbox Borescope | 2024-04-16 09:18 | Closed | CMS | CMSGBXBORE | THUNDERHEAD | ABARNDT |  | 2024-04-25 10:39
2 | WTG-00A6-0000 | 3335527 | CMS Gearbox Borescope | 2024-04-18 11:36 | Closed | CMS | CMSGBXBORE | COYOTE RIDGE | LXPEREZ |  | 2024-09-09 11:30
1 | WTG-0109-0000 | 3336869 | GEARBOX OIL, Fix oil leak | 2024-04-19 14:42 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KYARNOLD |  | 2024-04-24 07:24
3 | WTG-0042-0000 | 3337302 | CMS Generator Bearing Check | 2024-04-24 16:52 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2024-07-19 15:40
1 | WTG-0020-0000 | 3341660 | GEARBOX OIL, Fix radiator leak | 2024-04-25 14:44 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CPOLIFKA |  | 2024-07-26 07:58
4 | WTG-1046-0000 | 3343179 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-04-29 10:15 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
3 | WTG-00A6-0000 | 3343194 | GEARBOX OIL, Particle counter installation | 2024-04-29 10:40 | Closed | GBXOIL | GBXPARTINS | COYOTE RIDGE | ABARNDT |  | 2024-07-17 15:46
1 | WTG-0317-0000 | 3343272 | CMS Gearbox Borescope | 2024-04-29 12:33 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | LXPEREZ |  | 2024-05-01 14:21
1 | WTG-0014-0000 | 3579663 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-06-23 14:42 | Closed | GBXOIL | GBXOILCOOL | ORANGEVILLE | PHEATON |  | 2025-06-24 12:08
2 | WTG-0107-0000 | 3584879 | CMS Main Bearing Borescope | 2025-07-03 10:14 | Completed Awaiting Review | CMS | CMSMBBORE | SCEXP | NCLEMENTS |  | 2025-07-03 17:30
2 | WTG-1098-0000 | 3351217 | CMS Main Bearing Borescope | 2024-05-15 11:23 | Closed | CMS | CMSMBBORE | TRAVERSE | LXPEREZ |  | 2024-06-17 15:40
2 | WTG-0064-0000 | 3467499 | CMS Main Bearing Borescope | 2024-11-22 10:01 | Ready to Schedule | CMS | CMSMBBORE | MCADOO | TRUDE
5 | WTG-0021-0000 | 3467553 | GEARBOX OIL, Fix oil hose leak | 2024-11-22 12:36 | Closed | GBXOIL | GBXOILLEAK | UPSTREAM | RKUDERA |  | 2025-01-30 07:36
2 | WTG-0086-0000 | 3481255 | CMS Main Bearing Borescope | 2024-12-19 08:27 | Closed | CMS | CMSMBBORE | MAVERICK | HBELTRAN |  | 2024-12-19 16:49
1 | WTG-0049-NDG0-0000 | 3380628 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-07-08 16:32 | Closed | GBXOIL | GBXOILCOOL | SUNDANCE | TKORNELE |  | 2025-03-28 12:31
2 | WTG-0017-0000 | 3386055 | CMS Main Bearing Borescope | 2024-07-15 10:19 | Closed | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2025-01-31 10:28
1 | WTG-0015-0000 | 3391290 | Gearbox Radiator Leak | 2024-07-25 15:41 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | DMULLENS |  | 2025-03-29 17:01
2 | WTG-0015-0000 | 3391291 | GEARBOX OIL, Add/Top-Off | 2024-07-25 15:42 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | DMULLENS |  | 2025-01-13 14:33
2 | WTG-0013-NDG0-0000 | 3399107 | Needs Amsoil | 2024-08-06 16:37 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2024-08-09 14:21
2 | WTG-0012-0000 | 3399205 | CMS Gearbox Borescope | 2024-08-07 09:01 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | LXPEREZ |  | 2024-08-21 18:30
1 | GBX-000026 | 3414973 | EM: Gearbox oil pessure too low | 2024-09-04 15:36 | Closed | GBXOIL | EM52 | CAMP SPRINGS I | BEDEN |  | 2024-09-05 10:27
5 | WTG-0007-0000 | 3420050 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-09 10:55 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-10-01 13:02
5 | WTG-0010-0000 | 3420052 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-09 10:57 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2025-04-29 10:51
5 | WTG-0015-0000 | 3420060 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-09 11:00 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-10-01 13:02
5 | WTG-3028-0000 | 3436023 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-25 12:31 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
1 | WTG-0020-0000 | 3443663 | Oil leaking from TBV O-Ring / Top off 5 gallons | 2024-10-08 13:07 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2025-04-22 07:03
4.2 | WTG-0025-0000 | 3443665 | Replace orange and green hoses | 2024-10-08 11:09 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2024-10-25 16:56
4 | WTG-1042-0000 | 3449120 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-10-21 10:03 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
2 | WTG-0089-0000 | 3353639 | GEARBOX OIL, Add/Top-Off | 2024-05-21 16:42 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | CROBERTS |  | 2024-06-21 12:55
5 | WTG-00B3-0000 | 3353801 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-05-22 11:56 | Closed | CMS | CMSTRBLSHOOT | COYOTE RIDGE | LXPEREZ |  | 2024-10-07 15:23
5 | WTG-0101-NDB0-0000 | 3353701 | main bearing seal replacement | 2024-05-22 07:24 | Closed | CMS | CMSMB | NUMBER 3 WIND | ZTAYLOR |  | 2024-06-04 06:56
4 | WTG-0096-0000 | 3357937 | O'Hain Oil Bucket LLC Installation | 2024-05-29 15:18 | Cancelled | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2025-02-11 16:17
4 | WTG-0096-NDG0-0000 | 3357934 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-05-29 13:47 | Closed | GBXOIL | GBXOILADD | FORWARD | TBUYESKE |  | 2025-02-11 16:13
2 | WTG-0003-0000 | 3255284 | CMS Main Bearing Borescope | 2024-01-17 09:31 | Closed | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2024-02-29 13:12
3 | WTG-0020-0000 | 3255351 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 14:30 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | ABARNDT |  | 2024-02-01 12:25
4 | WTG-2110-0000 | 3255328 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 12:44 | Closed | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT |  | 2024-12-17 12:14
4 | WTG-0022-0000 | 3255353 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-17 14:33 | Closed | GBXOIL | GBXPARTTS | SUNDANCE | ABARNDT |  | 2024-02-01 12:25
2 | WTG-0004-0000 | 3258115 | GEARBOX OIL, Add/Top-Off | 2024-01-24 16:49 | Cancelled | GBXOIL | GBXOILADD | JUDITH GAP | SMCCLURE |  | 2024-02-06 15:34
3 | WTG-2002-0000 | 3298675 | CMS Generator Bearing Check | 2024-02-12 09:38 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2024-02-22 10:54
5 | WTG-0042-NDD0-0000 | 3308517 | GENERATOR, Uptower repair - Bearing replacement | 2024-02-26 10:53 | Closed | CMS | CMSGENB | UPSTREAM | DGORDON |  | 2024-03-22 16:24
2 | WTG-0003-0000 | 3311068 | CMS Main Bearing Borescope | 2024-03-01 09:58 | Closed | CMS | CMSMBBORE | MAVERICK | AALATORRE |  | 2024-03-06 15:11
2 | WTG-0042-0000 | 3320349 | CMS Main Bearing Borescope | 2024-03-21 15:39 | Closed | CMS | CMSMBBORE | UPSTREAM | LXPEREZ |  | 2024-04-22 14:55
2 | WTG-0059-0000 | 3320356 | CMS Gearbox Borescope | 2024-03-21 15:47 | Closed | CMS | CMSGBXBORE | DEUEL HARVEST | LXPEREZ |  | 2024-04-04 12:53
2 | WTG-0016-0000 | 3323494 | CMS Main Bearing Borescope | 2024-03-26 10:19 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-03-29 12:06
2 | WTG-0063-0000 | 3323495 | CMS Main Bearing Borescope | 2024-03-26 10:25 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-05-28 10:19
2 | WTG-0085-0000 | 3323505 | CMS Main Bearing Borescope | 2024-03-26 10:36 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-04-30 14:43
4 | WTG-0030-0000 | 3330903 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-04-08 13:24 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-07-31 12:01
1 | WTG-0002-0000 | 3332158 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-04-11 10:33 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | KYARNOLD |  | 2024-04-15 08:18
2 | WTG-0077-0000 | 3334720 | CMS HSS Check | 2024-04-17 09:42 | Closed | CMS | CMSHSS | UPSTREAM | LXPEREZ |  | 2024-05-16 09:02
3 | WTG-0017-0000 | 3334723 | CMS Generator Bearing Check WC# 6803964 | 2024-04-17 09:31 | Closed | CMS | CMSGENB | THUNDERHEAD | LXPEREZ |  | 2024-06-19 10:32
3 | WTG-0028-0000 | 3343172 | CMS Generator Bearing Check | 2024-04-29 10:04 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2024-07-10 15:33
2 | WTG-0023-0000 | 3345783 | CMS Gearbox Borescope | 2024-05-02 14:30 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2024-05-08 07:40
2 | WTG-0031-0000 | 3348540 | CMS Gearbox Borescope | 2024-05-08 17:08 | Closed | CMS | CMSGBXBORE | UPSTREAM | LXPEREZ |  | 2024-05-21 13:01
1 | GBX-00030 | 3351205 | GEARBOX OIL, Particle counter removal | 2024-05-15 10:40 | Closed | GBXOIL | GBXPARTREM | BLOOMING GROVE | MWILSON |  | 2024-05-16 07:51
5 | WTG-1003-0000 | 3380600 | Yaw hydr. pump time too long | 2024-07-08 16:02 | Closed | CMS | CMSMB | TRAVERSE | BWALLIS |  | 2024-07-29 10:42
4.2 | WTG-0056-0000 | 3420039 | Field Service Labor - Gearbox Oil Change, per WTG | 2024-09-09 10:45 | Closed | GBXOIL | FSO-OILCHNG | BETHEL | KWHATLEY |  | 2024-09-16 13:04
5 | WTG-1027-0000 | 3428211 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-17 11:14 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-11-06 12:20
5 | WTG-2063-0000 | 3436017 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-25 12:14 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
5 | WTG-2084-0000 | 3436021 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-25 12:25 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
2 | WTG-0004-NDG0-0000 | 3456873 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-11-04 09:57 | Closed | GBXOIL | GBXOILADD | FORWARD | TBUYESKE |  | 2024-11-20 15:04
4 | WTG-0052-0000 | 3227474 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-20 09:59 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | ABARNDT |  | 2024-09-12 11:26
5 | WTG-0031-NDG0-0000 | 3249819 | GEARBOX OIL, Fix or replace GBX inspection port | 2024-01-03 17:54 | Ready to Schedule | GBXOIL | GBXOILLEAK | SPRING CANYON | JCUMMINGS
2 | WTG-0002-NDG0-0000 | 3249792 | GEARBOX OIL, Add/Top-Off | 2024-01-03 15:37 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2024-02-01 11:58
5 | WTG-0027-0000 | 3252498 | GEARBOX OIL, Replace oil cooler rad | 2024-01-10 16:20 | Ready to Schedule | GBXOIL | GBXOILCOOL | SPRING CANYON | BBUSS
2 | WTG-0017-NDG0-0000 | 3255029 | Add Amsoil | 2024-01-16 14:27 | Closed | GBXOIL | GBXOILADD | VANTAGE | JAGUILAR |  | 2024-03-15 15:33
2 | WTG-0011-0000 | 3255028 | CMS Main Bearing Borescope | 2024-01-16 14:22 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-01-24 18:39
1 | WTG-3028-0000 | 3301432 | GEARBOX OIL, Fix oil leak | 2024-02-16 11:20 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | JCARTWRIGHT |  | 2024-02-22 16:47
1 | WTG-0205-NDG0-0000 | 3467416 | GEARBOX OIL, Fix oil leak/Hose Repair | 2024-11-22 08:03 | Closed | GBXOIL | GBXOILLEAK | BEECH RIDGE II | SFOSTER |  | 2024-12-11 11:46
1 | WTG-0062-0000 | 3543560 | GEARBOX OIL, Leak: Replace hose | 2025-04-15 16:09 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2025-07-10 13:12
2 | WTG-0060-0000 | 3555576 | CMS Main Bearing Borescope | 2025-05-07 15:18 | Ready to Schedule | CMS | CMSMBBORE | BLOOMING GROVE | BVANVALKENBURG
1 | WTG-0022-0000 | 3309402 | GEARBOX OIL, Replace Hose (radiator to filter housing) | 2024-02-27 15:42 | Closed | GBXOIL | GBXOILLEAK | SPRING CANYON | MBRAUNER |  | 2024-04-30 17:06
1 | WTG-0053-0000 | 3320042 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-03-20 18:18 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | SGENN |  | 2024-03-21 07:24
3 | WTG-1026-0000 | 3324251 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-03-27 09:51 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
4 | WTG-1067-0000 | 3324253 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-03-27 09:56 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
3 | WTG-1006-0000 | 3324258 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-03-27 10:04 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-11-06 12:09
1 | WTG-0038-0000 | 3328308 | GEARBOX OIL, Fix oil leak | 2024-04-03 11:44 | Closed | GBXOIL | GBXOILLEAK | STANTON | MROMAN |  | 2024-04-03 16:11
1 | WTG-0037-0000 | 3328298 | GEARBOX OIL, Fix oil leak | 2024-04-03 11:38 | Closed | GBXOIL | GBXOILLEAK | STANTON | MROMAN |  | 2024-04-03 16:14
3 | WTG-1093-0000 | 3332076 | CMS Gearbox Borescope | 2024-04-11 10:32 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2024-09-26 11:18
2 | WTG-00P7-0000 | 3333897 | CMS Gearbox Borescope | 2024-04-15 11:18 | Closed | CMS | CMSGBXBORE | TATANKA RIDGE | LXPEREZ |  | 2024-08-29 16:07
4 | WTG-0012-0000 | 3333977 | Secondary oil leak at usual spot | 2024-04-15 12:51 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2024-11-20 11:47
4 | WTG-0012-0000 | 3333978 | Hand pump replacement | 2024-04-15 12:52 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2024-11-20 11:48
5 | WTG-2121-0000 | 3333958 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-04-15 13:50 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-05-07 14:21
2 | WTG-0052-0000 | 3335294 | CMS Main Bearing Borescope | 2024-04-17 14:44 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | LXPEREZ |  | 2024-04-25 13:04
1 | WTG-0119-0000 | 3336596 | CMS Gearbox Borescope | 2024-04-23 09:24 | Closed | CMS | CMSGBXBORE | BETHEL | ABARNDT |  | 2024-04-24 15:38
1 | WTG-0005-NDGP-0000 | 3337225 | No Errors | 2024-04-24 13:42 | Closed | GBXOIL | GBXOILLEAK | MARSH HILL | BHUNTER |  | 2024-06-25 12:06
2 | WTG-0057-0000 | 3337194 | CMS Main Bearing Borescope | 2024-04-24 12:39 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | LXPEREZ |  | 2024-05-01 16:24
2 | WTG-0002-0000 | 3337119 | CMS Main Bearing Borescope | 2024-04-24 11:22 | Closed | CMS | CMSMBBORE | DEUEL HARVEST | LXPEREZ |  | 2024-05-13 09:10
5 | WTG-0063-0000 | 3337184 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-04-24 11:49 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-04-25 14:06
5 | WTG-0019-0000 | 3337185 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-04-24 11:59 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-04-25 14:06
3 | WTG-0096-0000 | 3337187 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-04-24 12:05 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-04-25 14:05
5 | WTG-0084-0000 | 3337122 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-04-24 11:36 | Closed | CMS | CMSTRBLSHOOT | DEUEL HARVEST | LXPEREZ |  | 2024-04-26 14:50
2 | WTG-0057-0000 | 3341540 | CMS Main Bearing Borescope | 2024-04-25 12:58 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | GGAYLER |  | 2024-05-01 10:21
5 | WTG-00J1-0000 | 3342082 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-04-26 17:09 | Closed | CMS | CMSTRBLSHOOT | TATANKA RIDGE | LXPEREZ |  | 2024-09-17 15:28
3 | WTG-00G2-0000 | 3342081 | CMS Gearbox Borescope | 2024-04-26 16:38 | Closed | CMS | CMSGBXBORE | TATANKA RIDGE | LXPEREZ |  | 2024-07-25 15:16
2 | WTG-0068-0000 | 3582238 | CMS Gearbox Borescope | 2025-06-30 14:23 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | OLAM |  | 2025-07-08 15:31
4 | WTG-0211A-0000 | 3587287 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-07-10 14:59 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN
1 | WTG-0059-0000 | 3350990 | GEARBOX OIL, Fix oil leak | 2024-05-14 15:59 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | MWAGNER |  | 2024-05-24 15:48
1 | WTG-0G10-0000 | 3481112 | GEARBOX OIL, Fix oil leak | 2024-12-18 14:14 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | JMOLONEY |  | 2025-03-25 15:03
5 | WTG-0063-0000 | 3496784 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-01-15 15:20 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | AVIETOR |  | 2025-01-16 15:06
2 | WTG-00A2-NDG0-0000 | 3499603 | Follow Up CMS Gearbox Borescope | 2025-01-27 08:58 | Closed | CMS | CMSGBXBORE | COYOTE RIDGE | JRFREEMAN |  | 2025-02-28 10:07
5 | WTG-0046-0000 | 3380405 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-07-08 10:36 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-07-31 13:06
3 | WTG-0026-0000 | 3380391 | CMS Generator Bearing Check | 2024-07-08 10:27 | Closed | CMS | CMSGENB | PLYMOUTH | ABARNDT |  | 2024-09-27 08:24
4 | WTG-0002-0000 | 3380402 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-07-08 10:33 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-07-22 10:52
3 | WTG-2037-0000 | 3388454 | CMS Gearbox Borescope | 2024-07-18 10:09 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2024-09-03 11:16
5 | WTG-1104-0000 | 3388451 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-07-18 10:01 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-09-20 11:52
5 | WTG-0063-0000 | 3391185 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-07-25 12:39 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | CWERNER |  | 2024-10-29 15:21
2 | WTG-0029-0000 | 3409524 | CMS Main Bearing Borescope | 2024-08-26 09:47 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-10-22 09:49
2 | WTG-0048-0000 | 3428148 | CMS Main Bearing Borescope | 2024-09-17 10:22 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-10-14 12:00
2 | WTG-0027-0000 | 3428153 | CMS Main Bearing Borescope | 2024-09-17 10:30 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-09-20 09:37
2 | WTG-2054-0000 | 3433036 | CMS Gearbox Borescope | 2024-09-19 09:51 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2024-12-16 14:47
2 | WTG-0027-0000 | 3435960 | CMS Main Bearing Borescope | 2024-09-25 09:44 | Closed | CMS | CMSMBBORE | SUNDANCE | JROSS |  | 2024-10-07 19:21
1 | WTG-0055-0000 | 3459458 | Replace gearbox oil hose | 2024-11-08 07:42 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH |  | 2024-12-20 13:06
1 | WTG-0002C-0000 | 3227193 | Replace GBX Lube Pump | 2023-11-17 13:59 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2023-12-15 10:57
1 | WTG-0091-0000 | 3353593 | GEARBOX OIL, Replace oil cooler radiator | 2024-05-21 14:03 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | JXBOYD |  | 2025-03-26 13:33
4 | WTG-0212-0000 | 3229912 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-11-28 17:35 | Closed | GBXOIL | GBXOILADD | FORWARD | JJENSEMA |  | 2023-12-15 11:02
1 | WTG-0012-0000 | 3230043 | GEARBOX OIL, Secondary filter system element change | 2023-11-29 09:04 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | TWIEDEMEIER |  | 2024-01-08 14:01
1 | WTG-0041-0000 | 3230044 | GEARBOX OIL, Secondary filter system installation | 2023-11-29 09:06 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | TWIEDEMEIER |  | 2023-11-30 10:38
1 | WTG-0077-0000 | 3230045 | GEARBOX OIL, Secondary filter system installation | 2023-11-29 09:06 | Ready to Schedule | GBXOIL | GBXFILTINS | JUDITH GAP | TWIEDEMEIER |  | 2024-08-15 11:22
1 | WTG-0004-NDG0-0000 | 3232662 | GEARBOX OIL, Fix oil leak | 2023-12-01 17:00 | Closed | GBXOIL | GBXOILLEAK | SUNDANCE | CLAWRENCE |  | 2024-02-23 12:05
1 | WTG-00H2-0000 | 3252297 | CMS Gearbox Borescope | 2024-01-10 10:53 | Cancelled | CMS | CMSGBXBORE | TATANKA RIDGE | LXPEREZ |  | 2024-02-29 15:07
5 | WTG-00H2-0000 | 3252301 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-01-10 11:21 | Closed | CMS | CMSTRBLSHOOT | TATANKA RIDGE | LXPEREZ |  | 2024-10-07 15:25
2 | WTG-0328-0000 | 3254953 | CMS Gearbox Borescope | 2024-01-16 11:51 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | LXPEREZ |  | 2024-01-25 13:46
5 | WTG-0046-0000 | 3254962 | CMS HSS Check | 2024-01-16 12:09 | Closed | CMS | CMSHSS | DEUEL HARVEST | LXPEREZ |  | 2024-01-23 14:27
2 | WTG-0017-0000 | 3254981 | CMS Main Bearing Borescope | 2024-01-16 12:56 | Closed | CMS | CMSMBBORE | BETHEL | ABARNDT |  | 2024-01-22 14:02
4 | WTG-0070-NDGP-0000 | 3263275 | Replace red spider insert | 2024-01-30 15:40 | Closed | GBXOIL | GBXOILCOOL | FORWARD | ALANGKAU |  | 2024-06-10 09:47
1 | WTG-0064-0000 | 3263270 | GEARBOX OIL, replace hose WC# 6700252 | 2024-01-29 12:05 | Closed | GBXOIL | GBXOILLEAK | THUNDERHEAD | AKERKMAN |  | 2024-03-15 11:23
2 | WTG-0120-0000 | 3301338 | Gearbox Borescope | 2024-02-16 09:26 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | JSIMPSON |  | 2024-02-19 08:52
1 | WTG-0009-0000 | 3301221 | GEARBOX OIL, Fix radiator leak | 2024-02-15 16:38 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CPOLIFKA |  | 2024-07-11 07:47
1 | WTG-0049-0000 | 3493100 | GEARBOX OIL, Fix oil leak | 2025-01-13 08:39 | Closed | GBXOIL | GBXOILLEAK | WAKE 1 | MGGOMEZ |  | 2025-01-13 11:32
1 | WTG-0063-0000 | 3368689 | GEARBOX OIL, Fix oil leak | 2024-06-18 14:48 | Ready to Schedule | GBXOIL | GBXOILLEAK | JUDITH GAP | TWIEDEMEIER
2 | WTG-0078-0000 | 3368691 | GEARBOX OIL, Add/Top-Off | 2024-06-18 14:51 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | DMULLENS |  | 2024-10-07 09:43
1 | WTG-0084-0000 | 3239729 | GEARBOX OIL, Fix oil leak | 2023-12-08 10:44 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KYARNOLD |  | 2023-12-11 14:25
1 | WTG-0100-0000 | 3265970 | GEARBOX OIL, Secondary filter system installation | 2024-02-01 16:37 | In Progress | GBXOIL | GBXFILTINS | BUCKEYE | MSCHMITT
1 | WTG-0013-NDG0-0000 | 3467281 | GEARBOX OIL, Fix oil leak | 2024-11-21 15:11 | Ready to Schedule | GBXOIL | GBXOILLEAK | GRAND RIDGE | GBLATNIK
1 | WTG-1124-0000 | 3304557 | GEARBOX OIL, Fix oil leak | 2024-02-23 12:19 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | ATHOMPSON |  | 2024-03-27 08:54
1 | WTG-0J10-0000 | 3320084 | GEARBOX OIL, Fix oil leak | 2024-03-21 07:46 | Closed | GBXOIL | GBXOILLEAK | HIGH SHELDON | PHEATON |  | 2024-03-21 15:20
2 | WTG-0039-0000 | 3325853 | GEARBOX OIL, Add/Top-Off | 2024-03-28 09:10 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | SOTTO |  | 2024-08-21 15:34
5 | WTG-0016-0000 | 3334576 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-04-16 15:33 | Closed | CMS | CMSTRBLSHOOT | GOLDTHWAITE | TRUMFIELD |  | 2024-04-17 13:47
2 | WTG-0044-NDG0-0000 | 3335367 | GEARBOX OIL, Add/Top-Off | 2024-04-17 16:46 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2024-04-23 12:10
5 | WTG-0019-0000 | 3337121 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-04-24 11:36 | Cancelled | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-04-25 07:41
1 | WTG-0034-0000 | 3566118 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-05-27 13:07 | Closed | GBXOIL | GBXOILCOOL | GUNSIGHT | JRODRIQUEZ |  | 2025-05-29 08:30
1 | WTG-00H3-0000 | 3351014 | GEARBOX OIL, Particle counter removal | 2024-05-14 17:24 | Closed | GBXOIL | GBXPARTREM | TATANKA RIDGE | AMONNIER |  | 2024-05-16 09:45
1 | WTG-0019-NDGP-0000 | 3388447 | Clean Oil Cooler Radiator | 2024-07-18 09:39 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | NCURRIE |  | 2024-07-30 10:19
2 | WTG-2117-0000 | 3388466 | CMS Main Bearing Borescope | 2024-07-18 10:30 | Closed | CMS | CMSMBBORE | TRAVERSE | ABARNDT |  | 2024-08-05 13:07
5 | WTG-1002-0000 | 3388449 | CMS HSS Check | 2024-07-18 09:40 | Closed | CMS | CMSHSS | TRAVERSE | ABARNDT |  | 2024-07-29 10:42
1 | WTG-0065-0000 | 3396294 | GEARBOX OIL, Hose leak | 2024-08-01 15:25 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | NSCHMEIDLER |  | 2024-10-04 13:44
5 | WTG-0J08-0000 | 3406956 | GEARBOX OIL, Fix oil leak | 2024-08-20 10:49 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | DSANDERSON |  | 2024-09-25 07:53
2 | WTG-0090-0000 | 3409536 | CMS Main Bearing Borescope | 2024-08-26 09:11 | Closed | CMS | CMSMBBORE | MAVERICK | AALATORRE |  | 2024-08-30 12:34
2 | WTG-0013-0000 | 3419922 | CMS Main Bearing Borescope | 2024-09-09 08:59 | Closed | CMS | CMSMBBORE | BETHEL | AXRODRIGUEZ |  | 2024-09-09 15:43
2 | WTG-00D2-0000 | 3433049 | CMS Gearbox Borescope | 2024-09-19 10:35 | Closed | CMS | CMSGBXBORE | COYOTE RIDGE | LXPEREZ |  | 2024-09-26 15:50
2 | WTG-0049-0000 | 3440869 | CMS Gearbox Borescope | 2024-10-02 10:41 | Closed | CMS | CMSGBXBORE | SUNDANCE | ABARNDT |  | 2025-01-31 10:26
2 | WTG-0065-0000 | 3440872 | CMS Main Bearing Borescope | 2024-10-02 10:50 | In Progress | CMS | CMSMBBORE | SUNDANCE | ABARNDT
5 | WTG-0049-0000 | 3440898 | GEARBOX OIL, Replace oil cooler fan/motor/LOW SPEED | 2024-10-02 11:44 | Closed | GBXOIL | GBXOILCOOL | UPSTREAM | CMASAT |  | 2025-01-07 14:02
1 | WTG-0090-0000 | 3235016 | Gearbox Radiator Leak | 2023-12-05 10:45 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | TWIEDEMEIER |  | 2025-05-20 12:56
1 | WTG-0064-0000 | 3234984 | CMS Gearbox Borescope | 2023-12-05 10:07 | Closed | CMS | CMSGBXBORE | BETHEL | ABARNDT |  | 2023-12-07 16:09
5 | WTG-0041-0000 | 3254943 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-01-16 11:08 | Closed | CMS | CMSTRBLSHOOT | SANTA RITA EAST | ABARNDT |  | 2024-01-23 09:00
2 | WTG-0073-0000 | 3254948 | CMS Gearbox Borescope | 2024-01-16 11:26 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2024-01-25 15:28
2 | WTG-0042-NDG0-0000 | 3368636 | GEARBOX OIL, Add/Top-Off | 2024-06-18 13:36 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2024-06-19 16:08
5 | WTG-3071-0000 | 3350919 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-05-14 12:55 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | LXPEREZ |  | 2024-06-09 20:33
5 | WTG-3061-0000 | 3350921 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-05-14 13:03 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | LXPEREZ |  | 2024-05-21 16:04
5 | WTG-0031-0000 | 3350953 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-05-14 14:22 | Closed | CMS | CMSTRBLSHOOT | UPSTREAM | LXPEREZ |  | 2024-06-03 14:45
4 | WTG-0072A-0000 | 3350958 | Secondary oil leak usual spot | 2024-05-14 13:52 | Closed | GBXOIL | GBXFILTELEM | FORWARD | TBUYESKE |  | 2024-12-11 12:53
2 | WTG-0096-0000 | 3543414 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-04-15 11:40 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | BAZEFIELD |  | 2025-04-21 15:37
1 | WTG-00J1-0000 | 3427949 | GEARBOX OIL, Replace oil pump | 2024-09-16 17:10 | Cancelled | GBXOIL | GBXOILCOOL | TATANKA RIDGE | SKUEHN |  | 2024-09-17 09:59
1 | WTG-00J1-0000 | 3427953 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-09-16 18:41 | Closed | GBXOIL | GBXOILCOOL | TATANKA RIDGE | AMONNIER |  | 2024-09-20 14:33
1 | WTG-0098-0000 | 3450636 | GEARBOX OIL, Secondary Pump leak | 2024-10-22 16:03 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | MSCHMITT |  | 2024-11-06 16:46
2 | WTG-0062-0000 | 3443344 | GEARBOX OIL, Secondary oil pump | 2024-10-07 19:45 | Ready to Schedule | GBXOIL | GBXFILTELEM | JUDITH GAP | SMCCLURE
1 | WTG-0098-0000 | 3496739 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-01-16 13:35 | Closed | GBXOIL | GBXOILCOOL | MCADOO | SHART |  | 2025-01-20 14:46
2 | WTG-2045-0000 | 3353269 | CMS Gearbox Borescope | 2024-05-20 18:52 | Closed | CMS | CMSGBXBORE | TRAVERSE | LXPEREZ |  | 2024-06-09 20:33
1 | WTG-0100-0000 | 3234941 | CMS Main Bearing Borescope | 2023-12-05 09:36 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2023-12-11 10:47
1 | WTG-0103-0000 | 3268250 | CMS Main Bearing Borescope | 2024-02-06 10:30 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-03-25 13:16
2 | WTG-0038-0000 | 3268260 | CMS Main Bearing Borescope | 2024-02-06 10:58 | Closed | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2024-03-14 12:33
2 | WTG-0038-NDGP-0000 | 3368549 | Oil Cooler Leaking | 2024-06-18 11:17 | Ready to Schedule | GBXOIL | GBXOILCOOL | FORWARD | PPOSTHUMA
3 | WTG-00E3-0000 | 3368573 | CMS Generator Bearing Check | 2024-06-18 11:43 | Closed | CMS | CMSGENB | TATANKA RIDGE | LXPEREZ |  | 2024-06-24 10:24
4 | WTG-0074-0000 | 3522812 | GEARBOX OIL, Replace oil cooler | 2025-03-13 11:32 | Completed Awaiting Review | GBXOIL | GBXOILCOOL | GRATIOT | JAHAYDEN |  | 2025-07-10 14:44
5 | WTG-0089-0000 | 3528640 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-03-21 11:45 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | TBUYESKE
1 | WTG-0056-0000 | 3528673 | GEARBOX OIL, Particle counter removal | 2025-03-21 14:14 | Ready to Schedule | GBXOIL | GBXPARTREM | BLOOMING GROVE | ABARNDT
1 | WTG-0021-0000 | 3534366 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-03-26 15:00 | Ready to Schedule | GBXOIL | GBXOILCOOL | UPSTREAM | THOLZ
3 | SITE-TTKR | 3537363 | Oil Samples Fluidlife | 2025-04-01 08:49 | Ready to Schedule | GBXOIL | ADMIN | TATANKA RIDGE | CLUKE
2 | WTG-0347-0000 | 3345456 | CMS Main Bearing Borescope | 2024-05-02 09:47 | Closed | CMS | CMSMBBORE | BISHOP HILL III | LXPEREZ |  | 2024-05-06 09:34
2 | WTG-0073-0000 | 3345408 | GEARBOX OIL, Add/Top-Off | 2024-05-02 09:20 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | SOTTO |  | 2024-05-16 15:23
2 | WTG-0071-0000 | 3563122 | GEARBOX OIL, Fix oil leak/ replace oil hose | 2025-05-20 08:43 | Closed | GBXOIL | GBXOILLEAK | GRATIOT | CBENNETT |  | 2025-07-03 12:38
2 | WTG-0063-0000 | 3543219 | GE CMS Main Bearing Borescope | 2025-04-14 16:54 | Closed | CMS | CMSMBBORE | GOLDTHWAITE | JCULLITY |  | 2025-04-18 15:12
1 | WTG-0021-0000 | 3543176 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-04-14 16:11 | Ready to Schedule | GBXOIL | GBXOILCOOL | GRAND RIDGE | JTRUFFA
1 | WTG-0031-0000 | 3543303 | Replace oil pump coupling | 2025-04-15 08:51 | Closed | GBXOIL | GBXOILCOOL | WILLOW CREEK | NATKINS |  | 2025-04-18 10:02
2 | WTG-00E2-0000 | 3390814 | CMS Gearbox Borescope | 2024-07-24 11:40 | Closed | CMS | CMSGBXBORE | TATANKA RIDGE | LXPEREZ |  | 2024-08-29 16:11
1 | WTG-0130-0000 | 3568474 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-05-30 15:43 | Ready to Schedule | GBXOIL | GBXOILCOOL | GREXP | MOMILANOWSKI
4 | WTG-0009-NDG0-0000 | 3568394 | GEARBOX OIL, Add/Top-Off with about 5 gallons | 2025-05-30 10:59 | Closed | GBXOIL | GBXOILADD | FORWARD | KDRAKE |  | 2025-06-02 13:15
5 | WTG-0031-0000 | 3584436 | GEARBOX OIL motor/pump needs new fan cover | 2025-07-02 16:30 | Ready to Schedule | GBXOIL | GBXOILCOOL | DEUEL HARVEST | JESCAMILLAVIGIL
1 | WTG-0002-0000 | 3584469 | GEARBOX OIL, Secondary filter system installation | 2025-07-02 17:18 | Ready to Schedule | GBXOIL | GBXFILTINS | SPRING CANYON | TZWIRN
4.1 | WTG-0210A-0000 | 3586983 | O'Hain Oil Bucket Installation | 2025-07-10 07:22 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN
1 | GBX-00045 | 3586991 | GEARBOX OIL, Fix oil leak | 2025-07-02 13:30 | Ready to Schedule | GBXOIL | GBXOILLEAK | BLOOMING GROVE | DGEORGE
2 | WTG-0020-NDG0-0000 | 3419641 | Needs Amsoil | 2024-09-06 15:21 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2025-03-31 09:58
2 | WTG-0F08-0000 | 3432752 | CMS Main Bearing Borescope | 2024-09-18 14:19 | Closed | CMS | CMSMBBORE | JAYHAWK | LXPEREZ |  | 2024-09-27 08:50
4 | WTG-0049-0000 | 3440560 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-10-01 12:35 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-12-09 15:18
5 | WTG-0067-0000 | 3443194 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-10-07 14:31 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-10-14 09:50
4 | WTG-0024-0000 | 3443201 | Secondary filter pump leaking at shaft seal | 2024-10-07 14:57 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2025-04-11 13:32
1 | WTG-0073-NDGP-0000 | 3448600 | Leaking Oil Cooler Return Hose. | 2024-10-18 18:17 | Ready to Schedule | GBXOIL | GBXOILLEAK | GREXP | JSENICA
2 | WTG-0048-0000 | 3451169 | CMS Gearbox Borescope | 2024-10-24 07:27 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | CGREIS |  | 2024-10-28 14:01
5 | WTG-00I2-0000 | 3453812 | CMS Main Bearing Sensor Check | 2024-10-30 15:15 | Closed | CMS | CMSMB | TATANKA RIDGE | SKUEHN |  | 2024-11-06 07:45
4 | WTG-0205-0000 | 3499151 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-01-24 13:06 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | TBUYESKE
2 | WTG-0084-0000 | 3353209 | CMS Gearbox Borescope | 2024-05-20 16:30 | Closed | CMS | CMSGBXBORE | BETHEL | LXPEREZ |  | 2024-05-24 13:32
5 | WTG-0008-0000 | 3226929 | Generator Greasing | 2023-11-17 12:21 | Closed | CMS | CMSGENB | MAVERICK | MWEBER |  | 2024-02-19 16:58
1 | WTG-0008-0000 | 3229600 | GEARBOX OIL, Secondary filter system installation | 2023-11-28 10:05 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | TWIEDEMEIER |  | 2023-11-29 10:13
1 | WTG-0041-0000 | 3507811 | GEARBOX OIL, Fix oil leak | 2025-02-17 10:03 | Closed | GBXOIL | GBXOILLEAK | STANTON | MROMAN |  | 2025-02-17 15:49
1 | WTG-0086-0000 | 3541777 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-04-10 20:05 | Ready to Schedule | GBXOIL | GBXOILCOOL | GREXP | MOMILANOWSKI
2 | WTG-0071-0000 | 3345145 | CMS Main Bearing Borescope | 2024-05-01 13:18 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2024-05-03 07:57
1 | WTG-0094-0000 | 3563007 | GEARBOX OIL, Secondary Pump leak (15/25) | 2025-05-19 16:41 | Ready to Schedule | GBXOIL | GBXFILTINS | BUCKEYE | MSCHMITT
2 | WTG-1098-0000 | 3390584 | CMS Main Bearing Borescope | 2024-07-23 15:42 | Closed | CMS | CMSMBBORE | TRAVERSE | BJONES |  | 2024-08-06 09:48
1 | GBX-000028 | 3390593 | EM: Gearbox oil level too low | 2024-07-23 16:09 | Closed | GBXOIL | EM245 | SPRING CANYON | ASCHRIMPSCHER |  | 2024-07-25 10:21
1 | WTG-0015-NDGP-0000 | 3557568 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-05-09 07:18 | Completed Awaiting Review | GBXOIL | GBXOILCOOL | SUNDANCE | TKORNELE |  | 2025-05-09 21:11
4.2 | WTG-0036-0000 | 3557659 | GEARBOX OIL, Add/Top-Off 5 gal | 2025-05-09 13:38 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | TBUYESKE
1 | WTG-0046-0000 | 3400995 | GEARBOX OIL, Secondary filter system installation | 2024-08-08 10:48 | Ready to Schedule | GBXOIL | GBXFILTINS | BUCKEYE | LDURLER
1 | WTG-0052-0000 | 3400996 | Secondary filter leak, Rotor slipring ground cable | 2024-08-08 10:49 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | LDURLER |  | 2024-09-30 10:48
5 | WTG-0010-0000 | 3403807 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-08-16 11:17 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-09-04 07:59
1 | WTG-0054-0000 | 3403787 | GEARBOX OIL, Secondary filter system Motor change | 2024-08-16 10:36 | Closed | GBXOIL | GBXFILTINS | BUCKEYE | MSCHMITT |  | 2025-04-08 15:28
1 | WTG-0039-0000 | 3576503 | CMS Gearbox Borescope | 2025-06-12 09:11 | Closed | CMS | CMSGBXBORE | DEUEL HARVEST | BAZEFIELD |  | 2025-06-13 17:48
2 | WTG-0019-0000 | 3579014 | Main Bearing Borescope | 2025-06-20 11:54 | Ready to Schedule | CMS | CMSMBBORE | DEUEL HARVEST | CNIEMANN
1 | WTG-0022-0000 | 3586843 | Shims under A301 J-box | 2025-07-09 13:28 | Completed Awaiting Review | GBXOIL | BLANK | CHICKASAW | AXTRYON |  | 2025-07-09 16:52
1 | WTG-0003-0000 | 3586845 | GEARBOX OIL, Secondary filter system installation | 2025-07-09 13:47 | Ready to Schedule | GBXOIL | GBXFILTINS | BUCKEYE | MSCHMITT
1 | WTG-1065-0000 | 3411682 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-29 15:32 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
1 | WTG-3052-0000 | 3411686 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-29 15:39 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
2 | WTG-0050-0000 | 3419468 | CMS Main Bearing Borescope | 2024-09-06 10:12 | Closed | CMS | CMSMBBORE | MAVERICK | HBELTRAN |  | 2024-09-06 10:32
1 | WTG-0017-0000 | 3419472 | CMS Gearbox Borescope | 2024-09-06 10:22 | Closed | CMS | CMSGBXBORE | UPSTREAM | LXPEREZ |  | 2025-04-16 08:21
4.2 | WTG-0095-0000 | 3427643 | Field Service Labor - Gearbox Oil Change, per WTG | 2024-09-16 12:14 | Closed | GBXOIL | FSO-OILCHNG | BETHEL | KWHATLEY |  | 2024-09-16 13:03
5 | WTG-0066-0000 | 3427596 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-16 11:41 | Closed | CMS | CMSTRBLSHOOT | MAVERICK | ABARNDT |  | 2024-11-04 10:23
2 | WTG-0023-0000 | 3517020 | CMS Gearbox Borescope | 2025-03-03 09:49 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | PHEATON |  | 2025-04-03 09:41
2 | WTG-0011-0000 | 3345504 | CMS Main Bearing Borescope | 2024-05-02 11:37 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | LXPEREZ |  | 2024-05-08 12:35
3 | WTG-0007-0000 | 3350902 | CMS Generator Bearing Check | 2024-05-14 11:13 | Closed | CMS | CMSGENB | BETHEL | LXPEREZ |  | 2024-06-03 15:03
5 | WTG-0211-0000 | 3350892 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-05-14 10:56 | Scheduled | CMS | CMSTRBLSHOOT | BEECH RIDGE II | LXPEREZ
2 | WTG-2003-0000 | 3380282 | CMS Main Bearing Borescope | 2024-07-08 09:44 | Closed | CMS | CMSMBBORE | TRAVERSE | ABARNDT |  | 2024-07-24 16:47
1 | WTG-0061-0000 | 3390847 | GEARBOX OIL, Fix oil leak | 2024-07-24 13:53 | Closed | GBXOIL | GBXOILLEAK | THUNDERHEAD | CWERNER |  | 2024-10-14 09:55
1 | WTG-0060-0000 | 3390918 | GEARBOX OIL, Fix oil leak WC# 7025290 | 2024-07-24 16:05 | Closed | GBXOIL | GBXOILLEAK | THUNDERHEAD | NSCHINDLER |  | 2024-10-09 15:09
1 | WTG-0070-0000 | 3549500 | GEARBOX OIL, Leak: Replace hose | 2025-04-22 16:30 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2025-05-06 12:59
2 | WTG-0027-0000 | 3393411 | Oil leak at pump-to-filter plate and pump / Add 3 gallons of oil | 2024-07-29 15:10 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2025-04-28 13:47
9 | WTG-0055-0000 | 3432979 | High Speed Oil Leak, Gen Screens get coated and then hot. | 2024-09-19 08:11 | Ready to Schedule | GBXOIL | GBXOILLEAK | UPSTREAM | AUMSCHEID
1 | WTG-00P8-0000 | 3448673 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-10-20 13:33 | Closed | GBXOIL | GBXOILCOOL | TATANKA RIDGE | AMONNIER |  | 2024-10-23 13:09
2 | WTG-0023-0000 | 3268328 | CMS Main Bearing Borescope | 2024-02-06 11:09 | Cancelled | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2024-02-06 11:23
2 | WTG-0062-0000 | 3528677 | GEARBOX OIL, Particle counter installation | 2025-03-21 14:15 | Closed | GBXOIL | GBXPARTINS | BLOOMING GROVE | ABARNDT |  | 2025-03-26 07:36
2 | WTG-1108-0000 | 3304157 | CMS HSS Check | 2024-02-23 09:03 | Cancelled | CMS | CMSHSS | TRAVERSE | ABARNDT |  | 2024-11-11 14:44
1 | WTG-0317-0000 | 3308236 | First Fault Axis 2-check REPA/WEPA | 2024-02-24 15:26 | Closed | CMS | BLANK | BISHOP HILL III | MMILLER |  | 2024-02-26 09:39
4.1 | WTG-0132-0000 | 3563095 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-05-20 07:54 | Ready to Schedule | GBXOIL | GBXOILCOOL | GRATIOT | CBENNETT
5 | WTG-0023-0000 | 3435483 | CMS Main Bearing Check | 2024-09-24 14:08 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | ESILER |  | 2024-10-07 19:22
2 | WTG-0018-0000 | 3445901 | CMS Main Bearing Borescope | 2024-10-15 14:45 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2025-01-27 07:30
2 | WTG-0058-0000 | 3445942 | CMS Gearbox Borescope | 2024-10-15 15:33 | Closed | CMS | CMSGBXBORE | BETHEL | ABARNDT |  | 2024-10-17 13:11
4 | WTG-0203B-0000 | 3499152 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-01-24 14:17 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
5 | WTG-0078-0000 | 3246656 | CMS Generator Bearing Check | 2023-12-28 12:21 | Closed | CMS | CMSGENB | BETHEL | LXPEREZ |  | 2024-04-05 09:44
3 | WTG-0089-0000 | 3268241 | CMS Monitor Netcom | 2024-02-06 09:58 | Cancelled | CMS | CMSTRBLSHOOT | MAVERICK | ABARNDT |  | 2024-06-12 08:01
1 | WTG-0092-0000 | 3268246 | CMS Main Bearing Borescope | 2024-02-06 10:09 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-02-19 18:29
1 | GBX-HAN-E804A-4L/LM0288 | 3300749 | WTG-003 HIGH GEAR OIL TEMP. | 2024-02-15 13:24 | Closed | GBXOIL |  | BUFFALO MOUNT | VFRENCH |  | 2024-03-29 17:54
1 | WTG-0073-0000 | 3303971 | Replace Gearbox Hose | 2024-02-22 15:44 | Closed | GBXOIL | GBXOILLEAK | JUDITH GAP | JJUTILA |  | 2024-02-22 16:12
1 | WTG-0J04-0000 | 3345152 | GEARBOX OIL, Secondary filter system installation | 2024-05-01 13:48 | Ready to Schedule | GBXOIL | GBXFILTINS | HIGH SHELDON | CGREIS
2 | WTG-00S6-0000 | 3350550 | CMS Main Bearing Borescope | 2024-05-13 17:04 | Closed | CMS | CMSMBBORE | TATANKA RIDGE | SKUEHN |  | 2024-05-30 19:30
1 | GBX-00062 | 3537075 | EM: Gearbox oil level warning, Audit | 2025-03-31 19:40 | Closed | GBXOIL | EM225 | BLOOMING GROVE | GSUGGETT |  | 2025-03-31 19:45
4 | WTG-0008-0000 | 3435536 | Secondary filter pump leaking from shaft seal | 2024-09-24 09:51 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2024-11-20 15:03
3 | WTG-0048-0000 | 3393106 | CMS Gearbox Borescope | 2024-07-29 13:08 | Closed | CMS | CMSGBXBORE | UPSTREAM | LXPEREZ |  | 2024-08-15 12:29
1 | WTG-0093-0000 | 3565620 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-05-23 15:43 | Ready to Schedule | GBXOIL | GBXOILCOOL | GREXP | MOMILANOWSKI
4 | WTG-0003A-0000 | 3571131 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-06-02 14:23 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
2 | WTG-0005-0000 | 3419414 | CMS Gearbox Borescope | 2024-09-06 08:23 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | BSMITH |  | 2024-09-12 14:44
1 | WTG-0B02-0000 | 3435232 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-09-24 07:19 | Closed | GBXOIL | GBXOILCOOL | HIGH SHELDON | BMEST |  | 2024-09-26 13:34
1 | WTG-0089-0000 | 3435320 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-09-23 07:41 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | MHUFF |  | 2025-03-26 13:22
5 | WTG-0103-0000 | 3440469 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-10-01 14:07 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2025-04-21 14:23
5 | WTG-0005-0000 | 3451131 | GEARBOX OIL, Replace oil cooler fan motor | 2024-10-23 16:01 | Waiting for Parts | GBXOIL | GBXOILCOOL | UPSTREAM | DPRAUNER
2 | WTG-0071-0000 | 3493631 | Fill gearbox with oul | 2025-01-13 16:47 | Closed | GBXOIL | GBXOILADD | DIVERSION | LCRUZ |  | 2025-04-01 15:08
3 | WTG-2073-NTV0-0000 | 3229447 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-27 17:32 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | SQUIMBO |  | 2024-02-22 10:43
5 | WTG-2013-0000 | 3257220 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-01-22 11:20 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-02-23 09:04
2 | WTG-0051-0000 | 3257163 | CMS Gearbox Borescope | 2024-01-22 07:44 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | CGREIS |  | 2024-01-24 13:41
3 | WTG-0097-0000 | 3257214 | CMS Main Bearing Borescope | 2024-01-22 10:46 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2024-01-26 13:11
4 | WTG-0033-0000 | 3257217 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-01-22 11:02 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-02-09 09:52
4 | WTG-0040-0000 | 3257218 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-01-22 11:05 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-02-06 09:10
2 | WTG-0312-0000 | 3303954 | CMS Gearbox Borescope | 2024-02-22 15:09 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | LXPEREZ |  | 2024-02-26 09:40
3 | WTG-0031-0000 | 3303834 | CMS Generator Bearing Check | 2024-02-22 10:36 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2024-07-15 13:33
2 | WTG-0001-0000 | 3303924 | CMS Main Bearing Borescope | 2024-02-22 12:52 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-03-06 09:28
1 | WTG-0026-0000 | 3516345 | GEARBOX OIL, pump motor | 2025-02-28 17:10 | Ready to Schedule | GBXOIL | GBXOILCOOL | GRAND RIDGE | JIVORY
2 | WTG-0002C-0000 | 3466688 | GEARBOX OIL, Replace spidergear coupler | 2024-11-20 11:36 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2024-11-20 15:04
1 | WTG-0012-0000 | 3469989 | GEARBOX OIL, Fix oil leak | 2024-11-27 15:37 | Ready to Schedule | GBXOIL | GBXOILLEAK | UPSTREAM | THOLZ
5 | WTG-0044-0000 | 3385166 | GEARBOX OIL, Oil Sample | 2024-07-12 11:30 | Closed | GBXOIL | GBXOILSAMP | WILLOW CREEK | NCURRIE |  | 2024-07-15 11:56
4 | WTG-0016-NDG0-0000 | 3551903 | Add 5 gallons of oil to the gearbox | 2025-04-29 20:06 | Closed | GBXOIL | GBXOILADD | FORWARD | KDRAKE |  | 2025-05-12 15:20
4 | WTG-0011-0000 | 3554877 | GEARBOX OIL, Add/Top-Off about 3 gallons | 2025-05-06 13:20 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
1 | WTG-0084-0000 | 3411660 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-29 15:15 | Cancelled | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT |  | 2024-12-18 07:31
1 | WTG-1006-0000 | 3411676 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-29 15:26 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
1 | WTG-0083-0000 | 3411656 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-29 15:14 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT
2 | WTG-0026-0000 | 3411596 | CMS Main Bearing Borescope | 2024-08-29 14:40 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2024-09-05 07:50
1 | WTG-1014-0000 | 3411678 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-29 15:28 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
2 | WTG-0014-0000 | 3411535 | CMS Main Bearing Borescope | 2024-08-29 11:22 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2024-09-13 07:39
1 | WTG-0087-0000 | 3411664 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-29 15:16 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT
1 | WTG-0088-0000 | 3411665 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-29 15:17 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT
1 | WTG-0098-0000 | 3411673 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-29 15:20 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT
1 | WTG-1045-0000 | 3411681 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-29 15:31 | Ready to Schedule | GBXOIL | GBXPARTTS | TRAVERSE | ABARNDT
5 | WTG-0088-0000 | 3414313 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-04 10:42 | Closed | CMS | CMSTRBLSHOOT | BLOOMING GROVE | LXPEREZ |  | 2025-04-02 10:38
5 | WTG-0131-0000 | 3490082 | CMS Generator Bearing Check | 2025-01-06 16:17 | Closed | CMS | CMSGENB | GREXP | MOMILANOWSKI |  | 2025-01-09 09:28
5 | WTG-0062-0000 | 3432353 | CMS Generator Bearing Check | 2024-09-17 15:13 | Closed | CMS | CMSGENB | STANTON | SORTEGA |  | 2024-09-18 08:44
2 | WTG-0002-0000 | 3440359 | CMS Main Bearing Borescope | 2024-10-01 10:02 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-10-17 11:34
2 | WTG-00K3-0000 | 3440324 | CMS Main Bearing Borescope | 2024-10-01 09:46 | Closed | CMS | CMSMBBORE | TATANKA RIDGE | SKUEHN |  | 2024-10-02 15:57
2 | WTG-0C07-0000 | 3442849 | CMS Main Bearing Borescope | 2024-10-07 11:41 | Closed | CMS | CMSMBBORE | JAYHAWK | LXPEREZ |  | 2024-10-10 07:52
2 | WTG-2068-0000 | 3445603 | CMS Gearbox Borescope | 2024-10-14 13:03 | Ready to Schedule | CMS | CMSGBXBORE | TRAVERSE | ABARNDT
2 | WTG-0020-0000 | 3445651 | CMS Gearbox Borescope | 2024-10-14 14:52 | Closed | CMS | CMSGBXBORE | BETHEL | ABARNDT |  | 2024-10-22 08:58
3 | WTG-3055-0000 | 3445600 | CMS Gearbox Borescope | 2024-10-14 12:54 | Ready to Schedule | CMS | CMSGBXBORE | TRAVERSE | ABARNDT
2 | WTG-0050-NDG0-0000 | 3450891 | GEARBOX OIL, Add/Top-Off | 2024-10-23 12:50 | Closed | GBXOIL | GBXOILADD | VANTAGE | CCUSACK |  | 2024-10-23 16:32
4 | WTG-0072A-0000 | 3453605 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-10-30 11:13 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-12-11 12:53
2 | WTG-0060-0000 | 3463966 | CMS Main Bearing Borescope | 2024-11-13 13:57 | Closed | CMS | CMSMBBORE | GOLDTHWAITE | OLAM |  | 2024-12-05 08:57
3 | WTG-0021-0000 | 3480451 | CMS Generator Bearing Check | 2024-12-17 12:23 | Closed | CMS | CMSGENB | BETHEL | BAZEFIELD |  | 2024-12-19 11:31
2 | WTG-0012-0000 | 3483212 | CMS Gearbox Borescope | 2024-12-27 07:39 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | PHEATON |  | 2024-12-30 08:34
3 | WTG-2062-NTV0-0000 | 3229379 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-27 17:12 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | SQUIMBO |  | 2024-02-22 10:55
3 | WTG-0065-0000 | 3248904 | CMS Generator Bearing Check | 2024-01-03 11:31 | Closed | CMS | CMSGENB | THUNDERHEAD | LXPEREZ |  | 2024-01-25 15:38
2 | WTG-0013-0000 | 3265238 | CMS HSS Check | 2024-02-01 10:40 | Closed | CMS | CMSHSS | BETHEL | ABARNDT |  | 2024-02-02 07:51
5 | WTG-0047-0000 | 3303650 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-02-21 17:05 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | LXPEREZ |  | 2025-07-01 14:09
2 | WTG-1102-0000 | 3367967 | CMS Gearbox Borescope | 2024-06-17 09:23 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2024-09-09 10:37
4 | WTG-0047-0000 | 3519323 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2025-03-05 13:03 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
1 | WTG-3038-0000 | 3344832 | GEARBOX OIL, Fix oil leak | 2024-05-01 09:09 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | QCROUSE |  | 2024-09-03 15:35
3 | WTG-0039-0000 | 3347661 | CMS Gearbox Borescope | 2024-05-07 13:25 | Closed | CMS | CMSGBXBORE | BETHEL | ABARNDT |  | 2024-05-14 08:53
2 | WTG-0035-0000 | 3350169 | gearbox oil cleanup | 2024-05-13 08:07 | Closed | GBXOIL | GBXOILLEAK | DEUEL HARVEST | JHUEBERT |  | 2024-05-29 15:01
1 | WTG-0066-0000 | 3469809 | Gbx Oil Pressure Low | 2024-11-27 12:11 | Closed | GBXOIL | GBXOILCOOL | UPSTREAM | CMASAT |  | 2024-12-09 14:09
2 | WTG-0076-0000 | 3536864 | Gearbox oil coean up | 2025-03-31 16:20 | Closed | GBXOIL | GBXOILADD | DIVERSION | LCRUZ |  | 2025-04-01 09:27
5 | WTG-0087-0000 | 3385099 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-07-12 09:53 | Closed | CMS | CMSTRBLSHOOT | MAVERICK | ABARNDT |  | 2024-07-26 07:20
5 | WTG-2089-0000 | 3385124 | CMS Generator Bearing Check | 2024-07-12 10:20 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2024-08-16 13:38
2 | WTG-0024-0000 | 3554698 | CMS Gearbox Borescope | 2025-05-06 07:21 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | PHEATON |  | 2025-06-25 08:39
2 | WTG-0050-0000 | 3395484 | CMS Gearbox Borescope | 2024-07-31 08:18 | Closed | CMS | CMSGBXBORE | MAVERICK | ABARNDT |  | 2024-09-06 09:49
5 | WTG-00L8-0000 | 3398230 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-08-06 11:20 | Closed | CMS | CMSTRBLSHOOT | TATANKA RIDGE | LXPEREZ |  | 2024-10-03 07:50
1 | WTG-0138-NDGP-0000 | 3573554 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-06-04 10:48 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | MHUFF |  | 2025-06-23 09:52
3 | WTG-0081-0000 | 3403502 | Thermal Bypass Valve Switch | 2024-08-15 12:54 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2024-09-23 12:20
1 | WTG-0098-0000 | 3581349 | Gearbox Radiator Leak | 2025-06-27 08:48 | Ready to Schedule | GBXOIL | GBXOILLEAK | JUDITH GAP | WBLYTHE
2 | WTG-0100-0000 | 3581371 | GEARBOX OIL, Add/Top-Off | 2025-06-27 09:30 | Ready to Schedule | GBXOIL | GBXOILADD | JUDITH GAP | SOTTO
4 | WTG-0070-0000 | 3411442 | Secondary filter leaking from the shaft seal | 2024-08-28 16:44 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2024-12-09 14:28
2 | WTG-0096-0000 | 3411490 | CMS Main Bearing Borescope | 2024-08-29 09:07 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | AVILLARREAL |  | 2024-08-30 12:57
5 | WTG-0033-0000 | 3435023 | Secondary oil leak | 2024-09-23 11:58 | Closed | GBXOIL | GBXOILLEAK | FORWARD | PPOSTHUMA |  | 2025-05-12 15:15
4 | WTG-0033-0000 | 3435024 | GEARBOX OIL, Add/Top-Off 5ish Gallons | 2024-09-23 13:30 | Closed | GBXOIL | GBXOILADD | FORWARD | PPOSTHUMA |  | 2024-11-20 10:05
2 | WTG-0095-0000 | 3434992 | CMS GBX Borescope | 2024-09-23 12:56 | Closed | CMS | CMSGBXBORE | PLYMOUTH | ABARNDT |  | 2024-11-18 14:40
1 | WTG-0072-0000 | 3445403 | CMS HSS Check | 2024-10-14 09:03 | Closed | CMS | CMSHSS | DEUEL HARVEST | ABARNDT |  | 2024-10-25 08:58
5 | WTG-0057-0000 | 3450723 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-10-23 09:21 | Ready to Schedule | CMS | CMSTRBLSHOOT | MAVERICK | HBELTRAN
1 | WTG-0094-0000 | 3453443 | GEARBOX OIL, Secondary filter system installation | 2024-10-29 17:06 | Ready to Schedule | GBXOIL | GBXFILTINS | JUDITH GAP | JSTAGNER
1 | WTG-0316-0000 | 3453422 | GEARBOX OIL, Secondary filter system installation | 2024-10-29 16:00 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE3 | THOLZ |  | 2024-12-31 15:08
2 | WTG-00C2-0000 | 3453366 | CMS Gearbox Borescope | 2024-10-29 12:42 | Closed | CMS | CMSGBXBORE | COYOTE RIDGE | LXPEREZ |  | 2024-11-18 14:40
2 | WTG-0065-0000 | 3463896 | GE Requested CMS Main Bearing Borescope | 2024-11-13 10:16 | Closed | CMS | CMSMBBORE | GOLDTHWAITE | JCULLITY |  | 2024-11-15 11:02
1 | WTG-0025-0000 | 3463822 | GEARBOX OIL, Fix oil leak | 2024-11-13 07:24 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JSTEEN |  | 2024-11-15 07:56
2 | WTG-0057-0000 | 3463847 | GEARBOX OIL, Secondary oil pump | 2024-11-13 08:44 | Closed | GBXOIL | GBXFILTELEM | JUDITH GAP | WBLYTHE |  | 2024-11-20 10:53
2 | WTG-0025-0000 | 3463893 | GE Requested CMS Main Bearing Borescope | 2024-11-13 10:15 | Closed | CMS | CMSMBBORE | GOLDTHWAITE | JCULLITY |  | 2024-11-15 11:01
1 | WTG-0017-0000 | 3463925 | CMS Gearbox Borescope | 2024-11-13 12:33 | Cancelled | CMS | CMSGBXBORE | UPSTREAM | AXADAMS |  | 2024-12-09 14:19
1 | WTG-0065-NDGP-0000 | 3463848 | GEARBOX OIL, Secondary filter system installation | 2024-11-13 08:44 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | JSTAGNER |  | 2024-11-20 10:53
2 | WTG-0055-0000 | 3463894 | GE Requested CMS Main Bearing Borescope | 2024-11-13 10:15 | Closed | CMS | CMSMBBORE | GOLDTHWAITE | JCULLITY |  | 2024-11-15 11:00
3 | WTG-0039-0000 | 3427539 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-16 10:04 | Closed | CMS | CMSTRBLSHOOT | BETHEL | ABARNDT |  | 2025-05-14 15:04
3 | WTG-3016-0000 | 3427580 | CMS Main Bearing Borescope | 2024-09-16 10:54 | Closed | CMS | CMSMBBORE | TRAVERSE | ABARNDT |  | 2024-09-24 07:29
2 | WTG-0079-0000 | 3440432 | CMS Main Bearing Borescope | 2024-10-01 12:46 | Cancelled | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-11-21 14:58
5 | WTG-0060-0000 | 3499038 | CMS Main Bearing Check | 2025-01-24 10:52 | Closed | CMS | CMSMB | MAVERICK | HBELTRAN |  | 2025-01-24 10:56
3 | WTG-2122-NTV0-0000 | 3229453 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-27 17:37 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | SQUIMBO |  | 2024-01-03 13:24
4 | WTG-0018-0000 | 3303816 | CMS Generator Bearing Check | 2024-02-22 09:45 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2024-06-28 09:53
5 | GBX-00001 | 3303824 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-02-22 10:04 | Cancelled | CMS | CMSTRBLSHOOT | BLOOMING GROVE | NFALASZ |  | 2024-02-22 10:07
1 | WTG-1110-0000 | 3303825 | GEARBOX OIL, Fix oil leak | 2024-02-22 10:11 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | TPARKER |  | 2024-02-26 11:51
1 | WTG-0137-0000 | 3522338 | GEARBOX OIL, Fix oil leak | 2025-03-12 10:41 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | SMILLER |  | 2025-03-12 15:19
5 | WTG-1037-0000 | 3445589 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-10-14 12:25 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
1 | WTG-3040-0000 | 3248906 | GEARBOX OIL, Fix oil leak | 2024-01-03 11:51 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | LWRIGHT |  | 2024-01-17 11:07
3 | WTG-0026-0000 | 3516272 | CMS Generator Bearing Check | 2025-02-28 15:33 | Closed | CMS | CMSGENB | UPSTREAM | LXPEREZ |  | 2025-03-04 09:56
5 | WTG-0003-0000 | 3395605 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-07-31 11:49 | Closed | CMS | CMSTRBLSHOOT | UPSTREAM | LXPEREZ |  | 2024-09-03 13:59
2 | WTG-0002-0000 | 3403450 | CMS Gearbox Borescope | 2024-08-15 11:39 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | LXPEREZ |  | 2024-08-21 18:02
2 | WTG-0097-0000 | 3408684 | CMS Main Bearing Borescope | 2024-08-23 09:52 | Closed | CMS | CMSMBBORE | SANTA RITA EAST | ABARNDT |  | 2024-11-26 07:41
1 | WTG-0001-0000 | 3411366 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-28 14:44 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT
1 | WTG-0002-0000 | 3411367 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-28 14:47 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT
1 | WTG-0015-0000 | 3411371 | GEARBOX OIL, Particle counter troubleshooting | 2024-08-28 14:50 | Ready to Schedule | GBXOIL | GBXPARTTS | MAVERICK | ABARNDT
3 | WTG-0103-0000 | 3432335 | CMS Main Bearing Borescope | 2024-09-17 14:26 | Closed | CMS | CMSMBBORE | PLYMOUTH | AXADAMS |  | 2024-10-31 15:03
3 | WTG-0021-0000 | 3432336 | CMS Main Bearing Borescope | 2024-09-17 14:29 | Cancelled | CMS | CMSMBBORE | PLYMOUTH | AXADAMS |  | 2024-10-01 13:00
2 | WTG-0021-0000 | 3435000 | CMS Main Bearing Borescope | 2024-09-23 13:17 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-10-17 11:33
1 | WTG-3034-0000 | 3450792 | GEARBOX OIL, Fix oil leak | 2024-10-23 10:40 | Closed | GBXOIL | GBXOILLEAK | TRAVERSE | QCROUSE |  | 2024-10-24 08:54
2 | GBX-00016 | 3480270 | CMS Gearbox Borescope | 2024-12-17 07:12 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | MWILSON |  | 2024-12-30 16:05
5 | WTG-0030-0000 | 3498746 | CMS Main Bearing Check | 2025-01-23 12:54 | Closed | CMS | CMSMB | MAVERICK | MWEBER |  | 2025-01-23 14:54
4.2 | WTG-0203B-0000 | 3364784 | Gearbox oil leak from the front / Install oil bucket | 2024-06-07 08:27 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU
3 | WTG-0088-0000 | 3248851 | GEARBOX OIL, Particle counter removal | 2024-01-03 09:24 | Closed | GBXOIL | GBXPARTREM | BLOOMING GROVE | ABARNDT |  | 2024-01-30 16:09
3 | WTG-0016-0000 | 3248877 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-03 10:01 | Closed | GBXOIL | GBXPARTTS | BLOOMING GROVE | ABARNDT |  | 2024-03-08 07:38
3 | WTG-0013-0000 | 3347480 | CMS Generator Bearing Check | 2024-05-07 10:59 | Closed | CMS | CMSGENB | RED BARN | ABARNDT |  | 2024-05-10 15:47
5 | WTG-0208-0000 | 3373714 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-06-27 09:58 | Ready to Schedule | CMS | CMSTRBLSHOOT | BEECH RIDGE II | ABARNDT
5 | WTG-3005-0000 | 3379477 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-07-03 10:07 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
2 | WTG-0061-NDG0-0000 | 3384956 | GEARBOX OIL, Add/Top-Off 5gals | 2024-07-11 15:24 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2024-09-23 11:40
1 | WTG-0022-0000 | 3539471 | GEARBOX OIL, Fix oil leak | 2025-04-03 15:46 | Ready to Schedule | GBXOIL | GBXOILLEAK | UPSTREAM | THOLZ
4.2 | WTG-0075B-0000 | 3542545 | GBX Thermal Bypass Valve Flip | 2025-04-14 08:04 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2025-05-16 09:19
4.2 | WTG-0031-0000 | 3557194 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-05-08 13:10 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
4 | WTG-0041A-0000 | 3565079 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-05-22 12:19 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
1 | WTG-0006-NDGP-0000 | 3575921 | Cracked Oil Cooling Hoses | 2025-06-11 12:42 | Ready to Schedule | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MCONDON
2 | WTG-0002-NDB0-0000 | 3405901 | CMS Main Bearing Borescope | 2024-08-19 12:50 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | MWILSON |  | 2024-08-21 18:00
1 | WTG-0072-0000 | 3405946 | Gearbox Radiator Leak | 2024-08-19 14:59 | Ready to Schedule | GBXOIL | GBXOILLEAK | JUDITH GAP | SOTTO
4 | WTG-0085-0000 | 3578600 | GEARBOX OIL, Add/Top-Off 5 Gallons | 2025-06-19 15:24 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
1 | WTG-0003-0000 | 3434825 | Actions and precautions when suspected catastrophic MB or gearbox failure occurs | 2024-09-23 09:24 | Closed | CMS | CATASTROPHIC DT | UPSTREAM | CBILLIG |  | 2024-09-30 11:42
1 | WTG-0213-0000 | 3460996 | GEARBOX OIL, Secondary filter system installation | 2024-11-12 07:56 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | THOLZ |  | 2024-11-18 15:17
3 | WTG-0082-0000 | 3356891 | Yearly Gearbox Borescope - Due 2025 | 2024-05-28 10:48 | Closed | CMS | CMSGBXBORE | FORWARD | TBUYESKE |  | 2025-06-17 13:38
4 | WTG-0204A-0000 | 3364541 | GEARBOX OIL, Add/Top-Off about 3 gallons | 2024-06-06 12:44 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2025-01-28 15:06
3 | WTG-1068-0000 | 3228877 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-27 09:58 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
3 | WTG-2109-0000 | 3229007 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-27 10:52 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-02-23 09:04
3 | WTG-1091-0000 | 3228892 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-27 10:08 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-11-11 11:36
5 | WTG-0066-0000 | 3477089 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-12-11 12:55 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | AKERKMAN |  | 2024-12-11 16:13
1 | WTG-0104-0000 | 3246093 | GEARBOX OIL, Fix leaking hose elbow/Replace the Hose | 2023-12-27 13:46 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | LDURLER |  | 2024-06-13 12:40
4 | WTG-0084-0000 | 3300122 | Secondary filter pump has small leak at shaft seal | 2024-02-14 06:58 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2024-07-31 12:12
2 | WTG-1109-0000 | 3300183 | CMS Inspection per GE request | 2024-02-14 09:02 | Closed | CMS | CMSINSP | TRAVERSE | ABARNDT |  | 2024-03-27 08:54
1 | WTG-0111-0000 | 3370674 | GEARBOX OIL Cooler, Fix oil leak | 2024-06-24 09:22 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2024-12-06 15:39
4.1 | WTG-0033-0000 | 3379227 | GEARBOX OIL, Replace radiator and oil cooler motor | 2024-07-02 16:29 | Ready to Schedule | GBXOIL | GBXOILCOOL | SPRING CANYON | NCLEMENTS
1 | WTG-0042-NDG0-0000 | 3533599 | Tighten GBX bolts | 2025-03-25 16:19 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | ZMUELLER |  | 2025-04-30 15:12
2 | WTG-0024-0000 | 3554359 | CMS Main Bearing Borescope | 2025-05-05 13:42 | Ready to Schedule | CMS | CMSMBBORE | MAVERICK | ABARNDT
4 | WTG-0032-0000 | 3554433 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-05-05 12:07 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
2 | WTG-00F2-NDD0-0000 | 3554440 | CMS Main Bearing Borescope | 2025-05-05 15:05 | Ready to Schedule | CMS | CMSMBBORE | TATANKA RIDGE | LXPEREZ
4 | WTG-0043-0000 | 3397869 | Secondary filter pump leaking at shaft seal | 2024-08-05 15:24 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2024-10-09 09:48
1 | WTG-0002-0000 | 3583736 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-07-02 06:58 | Closed | GBXOIL | GBXOILCOOL | MARSH HILL | BMEST |  | 2025-07-02 15:36
1 | WTG-0055-0000 | 3413790 | GEARBOX OIL, Particle counter troubleshooting | 2024-09-03 13:41 | Closed | GBXOIL | GBXPARTTS | UPSTREAM | ABARNDT |  | 2024-10-23 12:54
2 | WTG-0085-0000 | 3458240 | CMS Gearbox Borescope | 2024-11-06 09:22 | Closed | CMS | CMSGBXBORE | THUNDERHEAD | ZMASAT |  | 2024-11-12 12:04
5 | WTG-0058-0000 | 3226051 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-11-15 15:11 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2024-03-19 15:34
2 | WTG-0072-0000 | 3267242 | GEARBOX OIL, Add/Top-Off | 2024-02-02 16:29 | Closed | GBXOIL | GBXOILADD | JUDITH GAP | TWIEDEMEIER |  | 2024-04-19 12:51
1 | WTG-0093-0000 | 3349749 | GEARBOX OIL, Fix oil leak (Nanjing front seal) | 2024-05-10 13:16 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | CPOLIFKA |  | 2025-07-10 12:30
4 | WTG-0018-NDG0-0000 | 3349766 | GEARBOX, change pressure relief hose from pump to gbx | 2024-05-10 11:16 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | GOTKIN
1 | WTG-0030-NDGP-0000 | 3533405 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2025-03-25 13:54 | Closed | GBXOIL | GBXOILCOOL | BLOOMING GROVE | DGEORGE |  | 2025-03-25 14:11
2 | WTG-0024-0000 | 3542099 | Secondary oil filter motor replacement | 2025-04-11 12:31 | Ready to Schedule | GBXOIL | GBXFILTINS | FORWARD | TBUYESKE
2 | WTG-0054-0000 | 3542750 | CMS Gearbox Borescope | 2025-04-14 11:12 | Closed | CMS | CMSGBXBORE | DEUEL HARVEST | BAZEFIELD |  | 2025-04-28 15:02
1 | WTG-0228-0000 | 3395055 | GEARBOX OIL, Fix Oil Hose | 2024-07-30 16:06 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE2 | THOLZ |  | 2024-09-13 12:33
3 | WTG-1009-0000 | 3554179 | CMS Main Bearing Borescope | 2025-05-05 13:17 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
1 | WTG-0040-0000 | 3498717 | GBX OIL LEAK | 2025-01-23 10:19 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MMEADOWS |  | 2025-01-23 13:09
5 | WTG-0006-0000 | 3498675 | Main bearing inspection | 2025-01-23 09:51 | Closed | CMS | CMSMB | MAVERICK | MWEBER |  | 2025-01-23 14:54
1 | WTG-0082-NDG0-0000 | 3226510 | Replace secondary filter pump seal | 2023-11-17 06:56 | Closed | GBXOIL | GBXOILCOOL | FORWARD | GOTKIN |  | 2024-03-19 15:34
2 | WTG-1001-0000 | 3361070 | CMS Main Bearing Borescope | 2024-06-03 09:12 | Closed | CMS | CMSMBBORE | TRAVERSE | ABARNDT |  | 2024-06-17 15:30
2 | WTG-0010-0000 | 3364665 | CMS Main Bearing Borescope | 2024-06-06 16:13 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-06-19 13:10
5 | WTG-0082-0000 | 3231789 | GEARBOX OIL, Add/Top-Off 5 gallons | 2023-12-01 07:23 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2024-03-19 15:34
3 | WTG-0213-0000 | 3251727 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-01-09 10:41 | Closed | CMS | CMSTRBLSHOOT | BEECH RIDGE II | ABARNDT |  | 2024-03-06 08:15
2 | WTG-0001-0000 | 3255287 | CMS Main Bearing Borescope | 2024-01-17 09:41 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-02-12 08:01
3 | WTG-0040-0000 | 3347446 | CMS Gearbox Borescope | 2024-05-07 10:06 | Closed | CMS | CMSGBXBORE | THUNDERHEAD | ABARNDT |  | 2024-09-25 15:42
3 | WTG-0075-0000 | 3370787 | CMS Generator Bearing Check WC# 6906204 | 2024-06-24 11:15 | Closed | CMS | CMSGENB | THUNDERHEAD | LXPEREZ |  | 2024-07-25 14:20
5 | WTG-0008-0000 | 3370716 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-06-24 10:08 | Closed | CMS | CMSTRBLSHOOT | BETHEL | ABARNDT |  | 2024-11-20 16:11
2 | WTG-0035-0000 | 3379442 | CMS Main Bearing Borescope | 2024-07-03 09:32 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-07-26 09:43
2 | WTG-0047-0000 | 3379473 | CMS Main Bearing Borescope | 2024-07-03 09:33 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-07-30 08:03
2 | WTG-0084-0000 | 3379475 | CMS Main Bearing Borescope | 2024-07-03 09:42 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-07-26 09:43
4 | WTG-0019A-0000 | 3384873 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-07-11 14:41 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-09-23 12:20
2 | WTG-0005-0000 | 3442619 | CMS Inspection per GE request | 2024-10-07 08:15 | Closed | CMS | CMSINSP | ORANGEVILLE | PHEATON |  | 2024-10-15 11:03
5 | WTG-0025-0000 | 3356850 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-05-28 13:57 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | LXPEREZ |  | 2024-09-13 13:26
5 | WTG-0037-0000 | 3356852 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-05-28 14:00 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | LXPEREZ |  | 2024-09-27 12:19
3 | WTG-1020-0000 | 3228913 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-11-27 10:25 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-07-31 17:00
5 | WTG-0016-NDGP-0000 | 3477100 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-12-11 16:47 | Closed | CMS | CMSTRBLSHOOT | BLOOMING GROVE | DGEORGE |  | 2024-12-11 17:07
1 | WTG-0059-NDG0-0000 | 3248543 | CMS HSS Check | 2024-01-02 15:10 | Closed | CMS | CMSHSS | UPSTREAM | LXPEREZ |  | 2024-03-11 09:28
3 | WTG-0069-0000 | 3248589 | CMS Generator Bearing Check | 2024-01-02 15:41 | Closed | CMS | CMSGENB | UPSTREAM | LXPEREZ |  | 2024-01-30 16:00
2 | WTG-0036-0000 | 3251318 | Gearbox oil motor bearings going bad | 2024-01-08 13:02 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2024-05-08 14:53
5 | WTG-0031-0000 | 3261992 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-01-29 13:54 | Closed | CMS | CMSTRBLSHOOT | UPSTREAM | LXPEREZ |  | 2024-10-08 15:18
3 | WTG-2054-0000 | 3376543 | CMS Gearbox Borescope | 2024-07-02 13:03 | Closed | CMS | CMSGBXBORE | TRAVERSE | ABARNDT |  | 2024-09-03 11:23
1 | WTG-0074-0000 | 3551380 | GEARBOX OIL, Fix oil leak | 2025-04-28 15:08 | Ready to Schedule | GBXOIL | GBXOILLEAK | BUCKEYE | MLEGLEITER
5 | WTG-2131-0000 | 3413695 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-03 11:00 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
2 | WTG-0003-0000 | 3434572 | CMS Gearbox Borescope | 2024-09-20 16:41 | Closed | CMS | CMSGBXBORE | UPSTREAM | LXPEREZ |  | 2024-09-30 11:43
3 | WTG-0015-0000 | 3498325 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-01-22 11:08 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | BAZEFIELD |  | 2025-01-27 11:42
4 | WTG-0001-0000 | 3498323 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-01-22 11:01 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | BAZEFIELD |  | 2025-01-27 12:56
3 | WTG-0012-0000 | 3498324 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-01-22 11:05 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | BAZEFIELD |  | 2025-01-27 12:57
3 | WTG-0023-0000 | 3498326 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-01-22 11:13 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | BAZEFIELD |  | 2025-01-27 11:42
3 | WTG-0063-0000 | 3498328 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-01-22 11:22 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | BAZEFIELD |  | 2025-01-27 11:42
2 | WTG-0016-0000 | 3476901 | CMS Gearbox Borescope | 2024-12-11 09:03 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | JPADDOCK |  | 2024-12-11 14:04
5 | WTG-0066-0000 | 3476911 | CMS Trouble Shoot (Invenergy request, non-GE) WC# 7123808 | 2024-12-11 09:19 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | ZMASAT |  | 2024-12-11 16:20
1 | WTG-0066-0000 | 3251209 | CMS Main Bearing Check | 2024-01-08 09:52 | Closed | CMS | CMSMB | MAVERICK | ABARNDT |  | 2024-02-14 17:49
1 | WTG-0J08-0000 | 3256477 | GEARBOX OIL, Fix oil leak | 2024-01-18 15:49 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | DSANDERSON |  | 2024-01-18 15:54
1 | WTG-0J02-0000 | 3256478 | GEARBOX OIL, Fix oil leak | 2024-01-18 15:54 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | DSANDERSON |  | 2024-01-18 15:55
1 | WTG-0I13-0000 | 3256479 | GEARBOX OIL, Fix oil leak | 2024-01-18 15:54 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | DSANDERSON |  | 2024-01-18 15:56
1 | WTG-0E07-0000 | 3256480 | GEARBOX OIL, Fix oil leak | 2024-01-18 15:55 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | DSANDERSON |  | 2024-01-18 15:58
1 | WTG-0H09-0000 | 3256482 | GEARBOX OIL, Fix oil leak | 2024-01-18 15:57 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | DSANDERSON |  | 2024-08-12 08:07
2 | WTG-0046-0000 | 3256466 | CMS Main Bearing Borescope | 2024-01-18 15:11 | Cancelled | CMS | CMSMBBORE | THUNDERHEAD | ABARNDT |  | 2024-01-18 15:25
2 | WTG-0047-0000 | 3259143 | CMS Gearbox Borescope | 2024-01-25 08:52 | Closed | CMS | CMSGBXBORE | MIAMI 1 | MMEADOWS |  | 2024-01-30 08:14
2 | WTG-2009-0000 | 3367446 | CMS Generator Bearing Check | 2024-06-14 09:17 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2024-08-08 10:02
1 | WTG-0041-0000 | 3469264 | EM: Gearbox oil level warning | 2024-11-26 14:02 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JSTEEN |  | 2024-12-16 09:46
5 | WTG-0075B-NDG0-0000 | 3469271 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-11-26 14:38 | Cancelled | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2025-02-21 18:57
4 | WTG-0017-NDG0-0000 | 3376319 | GEARBOX OIL, Add/Top-Off 5Gals | 2024-07-02 07:09 | Closed | GBXOIL | GBXOILADD | FORWARD | GOTKIN |  | 2024-10-25 16:56
2 | WTG-0024-0000 | 3554231 | CMS Main Bearing Borescope | 2025-05-05 13:36 | Ready to Schedule | CMS | CMSGBXBORE | MAVERICK | ABARNDT
2 | WTG-1140-0000 | 3554216 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-05-05 13:29 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
1 | WTG-0084-0000 | 3559566 | GEARBOX OIL, Secondary Pump leak (15/25) | 2025-05-13 16:38 | Ready to Schedule | GBXOIL | GBXFILTINS | BUCKEYE | MSCHMITT
2 | WTG-0110-0000 | 3572920 | CMS Main Bearing Borescope | 2025-06-04 11:29 | Ready to Schedule | CMS | CMSMBBORE | SCEXP | ABARNDT
5 | WTG-0071A-0000 | 3575555 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-06-10 15:21 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN
1 | WTG-0108-0000 | 3578187 | EM: Gearbox oil level too low | 2025-06-18 14:51 | Closed | GBXOIL | EM51 | NUMBER 3 WIND | GBATES |  | 2025-06-18 15:04
1 | WTG-0039-0000 | 3410976 | GEARBOX OIL, Fix radiator leak | 2024-08-27 14:29 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | BROHR |  | 2024-08-29 15:33
2 | WTG-0080-0000 | 3583570 | CMS Gearbox Borescope | 2025-07-01 15:47 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | ZANDIS |  | 2025-07-01 15:58
2 | WTG-1047-0000 | 3426711 | CMS Main Bearing Borescope | 2024-09-12 12:37 | Closed | CMS | CMSMBBORE | TRAVERSE | ABARNDT |  | 2024-09-20 11:50
1 | WTG-0005-0000 | 3442169 | CMS Gearbox Borescope | 2024-10-04 12:13 | Closed | CMS | CMSGBXBORE | UPSTREAM | LXPEREZ |  | 2024-10-25 09:11
1 | WTG-0091-0000 | 3442204 | GEARBOX OIL Cooler, Fix oil leak | 2024-10-04 13:39 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2025-06-18 13:36
1 | WTG-0040-NDGP-0000 | 3447655 | CCJ secondary filter needs install Moventas | 2024-10-17 10:58 | Ready to Schedule | GBXOIL | GBXFILTINS | VANTAGE | PMASAKI
1 | WTG-0047-NDGP-0000 | 3447621 | CCJ install Nanjing gearbox (No hoses) | 2024-10-17 10:34 | Ready to Schedule | GBXOIL | GBXFILTINS | VANTAGE | PMASAKI
1 | WTG-0012-0000 | 3452968 | CMS Gearbox Borescope | 2024-10-29 09:20 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | ABARNDT |  | 2024-11-05 08:04
4.2 | WTG-0087-0000 | 3455560 | Possible leak from TBV / Add 5 Gallons | 2024-11-01 14:19 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2025-04-01 15:15
2 | WTG-0077-0000 | 3487946 | GEARBOX OIL Pump Inversion | 2025-01-03 09:28 | Ready to Schedule | GBXOIL | GBXOILCOOL | GREXP | MOMILANOWSKI
2 | WTG-0030-0000 | 3364213 | CMS Gearbox Borescope | 2024-06-05 16:37 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | JCULLITY |  | 2024-06-17 15:51
2 | WTG-0033-0000 | 3364281 | CMS Gearbox Borescope | 2024-06-06 09:17 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | BSMITH |  | 2024-06-17 15:51
1 | WTG-0112-0000 | 3364286 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-06-06 09:34 | Closed | GBXOIL | GBXOILCOOL | MIAMI 1 | MDUDLEY |  | 2025-03-26 13:31
3 | WTG-0072-0000 | 3364298 | CMS Generator Bearing Check | 2024-06-06 09:52 | Closed | CMS | CMSGENB | SUNDANCE | ABARNDT |  | 2024-07-08 12:26
1 | WTG-0079-0000 | 3236189 | GEARBOX OIL, Fix radiator leak and leaking hose elbow | 2023-12-06 16:37 | Closed | GBXOIL | GBXOILLEAK | BUCKEYE | MSCHMITT |  | 2024-10-04 13:45
3 | WTG-00C7-0000 | 3256332 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-18 11:19 | Closed | GBXOIL | GBXPARTTS | COYOTE RIDGE | ABARNDT |  | 2024-04-08 11:32
1 | WTG-0095-0000 | 3256341 | CMS Main Bearing Borescope | 2024-01-18 11:57 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-02-06 09:08
5 | WTG-0309-NDG0-0000 | 3267137 | GEARBOX OIL, Fix oil leak | 2024-02-02 15:20 | Closed | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | DPRAUNER |  | 2024-05-10 13:13
2 | WTG-0061-0000 | 3302721 | CMS Main Bearing Borescope | 2024-02-20 09:18 | Closed | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2024-03-04 12:39
4 | WTG-0031-0000 | 3367342 | GEARBOX OIL, Add/Top-Off 3 gallons | 2024-06-13 15:16 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-09-23 12:20
2 | WTG-0048-0000 | 3515607 | CMS Gearbox Borescope | 2025-02-28 07:58 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | PHEATON |  | 2025-02-28 14:43
1 | WTG-0033-0000 | 3518569 | GEARBOX OIL, Fix radiator leak | 2025-03-05 08:19 | Ready to Schedule | GBXOIL | GBXOILLEAK | BUCKEYE | ZNASH
2 | WTG-0005-0000 | 3524551 | CMS Gearbox Borescope | 2025-03-17 11:19 | Closed | CMS | CMSGBXBORE | DEUEL HARVEST | BAZEFIELD |  | 2025-04-16 16:20
1 | WTG-0306-0000 | 3344249 | GEARBOX Replace oil cooler fan 2 speed motor number 1 | 2024-04-30 15:28 | Closed | GBXOIL | GBXOILCOOL | BISHOP HILL III | JPADILLA |  | 2024-05-30 14:07
2 | WTG-0066-0000 | 3352230 | CMS Main Bearing Borescope | 2024-05-17 15:48 | Closed | CMS | CMSMBBORE | BETHEL | LXPEREZ |  | 2024-05-29 16:08
1 | WTG-0041-0000 | 3352254 | Oil Pump Motor Inversion | 2024-05-17 17:16 | Closed | GBXOIL | GBXOILLEAK | WOLVERINE CREEK | MCONDON |  | 2024-07-01 16:48
2 | WTG-0053-0000 | 3469106 | CMS Main Bearing Borescope | 2024-11-26 08:53 | Closed | CMS | CMSMBBORE | GOLDTHWAITE | TRUMFIELD |  | 2024-12-20 13:07
5 | WTG-00P6-0000 | 3370370 | CMS Generator Bearing Check | 2024-06-20 15:18 | Closed | CMS | CMSGENB | TATANKA RIDGE | FSHRUM |  | 2024-06-24 10:24
1 | WTG-0087-0000 | 3389664 | Replace GBX oil pump shaft seal / Add 5 gallons oil | 2024-07-22 15:25 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2024-09-23 12:05
1 | WTG-0073-0000 | 3554076 | Replace gearbox oil hose | 2025-05-05 09:58 | Ready to Schedule | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH
1 | WTG-0078-0000 | 3554077 | Replace gearbox oil hose | 2025-05-05 09:59 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | BSMITH |  | 2025-05-16 11:45
4.1 | WTG-0066-NDGP-0000 | 3554098 | Replace Gearbox Oil Hoses (see comments) | 2025-05-05 11:25 | Ready to Schedule | GBXOIL |  | FORWARD | KDRAKE
2 | WTG-0019-0000 | 3554066 | CMS Main Bearing Borescope | 2025-05-05 09:30 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2025-06-11 13:09
4 | WTG-0006-NDGP-0000 | 3567188 | GEARBOX OIL, Replace red spider gear | 2025-05-29 12:58 | Ready to Schedule | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE
4 | WTG-0001-0000 | 3572774 | GEARBOX OIL, Add/Top-Off about 8 gallons | 2025-06-04 07:02 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
1 | WTG-0307-NDGP-0000 | 3408059 | GEARBOX OIL, Radiator Is leaking | 2024-08-22 12:26 | Ready to Schedule | GBXOIL | GBXOILLEAK | PRAIRIE BREEZE3 | THOLZ
5 | WTG-00B1-0000 | 3578171 | Gen bearing replacement | 2025-06-18 13:40 | Completed Awaiting Review | CMS | CMSGENB | TATANKA RIDGE | SKUEHN |  | 2025-06-18 13:49
5 | WTG-0006-0000 | 3410667 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-08-26 15:55 | Closed | CMS | CMSTRBLSHOOT | THUNDERHEAD | LXPEREZ |  | 2024-09-27 12:19
4 | WTG-0204-0000 | 3426605 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-12 10:21 | Closed | CMS | CMSTRBLSHOOT | BEECH RIDGE II | ABARNDT |  | 2024-09-17 08:01
5 | WTG-0039-0000 | 3426667 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-12 11:15 | Completed Awaiting Review | CMS | CMSTRBLSHOOT | SUNDANCE | ABARNDT |  | 2025-04-16 01:06
5 | WTG-0061-0000 | 3426670 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-12 11:19 | Ready to Schedule | CMS | CMSTRBLSHOOT | SUNDANCE | ABARNDT
1 | WTG-0310-0000 | 3444722 | GEARBOX Replace oil cooler fan 2 speed motor number 1 | 2024-10-11 07:15 | Closed | GBXOIL | GBXOILCOOL | BISHOP HILL III | JPADILLA |  | 2024-10-31 14:15
1 | WTG-0078-0000 | 3452710 | GEARBOX OIL, Secondary Pump leak (27/27) | 2024-10-28 14:42 | Ready to Schedule | GBXOIL | GBXFILTINS | BUCKEYE | MSCHMITT
1 | WTG-0041-0000 | 3498072 | GEARBOX OIL, Fix oil leak | 2025-01-20 12:56 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KYARNOLD |  | 2025-01-22 10:59
1 | WTG-0A09-0000 | 3225863 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:23 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-11-28 09:49
1 | WTG-0B01-0000 | 3225864 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:24 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-11-28 09:49
1 | WTG-0E03-0000 | 3225865 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:24 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-11-28 09:49
1 | WTG-0C07-0000 | 3225866 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:24 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-11-28 09:50
1 | WTG-0C04-0000 | 3225867 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:25 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-11-28 09:50
1 | WTG-0B04-0000 | 3225869 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:26 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-11-28 09:50
1 | WTG-0118-NDGP-0000 | 3225783 | Radiator Exchange - Modular Uptower Exchange | 2023-11-15 07:30 | Ready to Schedule | GBXOIL | GBXOILCOOL | GREXP | JSENICA
4 | WTG-1070-0000 | 3240317 | CMS Main Bearing Check | 2023-12-11 11:25 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-01-30 14:09
3 | WTG-0059-0000 | 3240301 | CMS Trouble Shoot (Invenergy request, non-GE) | 2023-12-11 11:00 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-02-06 09:13
5 | WTG-0026-NDG0-0000 | 3248151 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-01-02 11:30 | Closed | CMS | CMSTRBLSHOOT | SUNDANCE | CLAWRENCE |  | 2024-02-01 12:56
2 | WTG-0346-NDG0-0000 | 3248108 | CMS Gearbox Borescope | 2024-01-02 11:10 | Closed | CMS | CMSGBXBORE | BISHOP HILL III | LXPEREZ |  | 2024-01-03 14:35
1 | WTG-0088-0000 | 3272218 | Poseidon fitting retrieval | 2024-02-07 11:47 | Closed | GBXOIL | GBXPARTREM | BLOOMING GROVE | GGAYLER |  | 2024-02-08 11:31
1 | WTG-0006-NDGP-0000 | 3272185 | GEARBOX OIL, Fix oil leak | 2024-02-07 10:55 | Closed | GBXOIL | GBXOILLEAK | VANTAGE | CCUSACK |  | 2024-02-12 14:19
5 | WTG-0098-0000 | 3302502 | GEARBOX OIL, Add/Top-Off, 5 gallons | 2024-02-19 14:38 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2024-09-23 11:42
2 | WTG-0068-0000 | 3302562 | CMS Gearbox Borescope | 2024-02-19 16:00 | Closed | CMS | CMSGBXBORE | GOLDTHWAITE | WHALL |  | 2024-02-27 15:56
5 | WTG-0077-0000 | 3302543 | T77 CMS controller / SR# 6170234 | 2024-02-19 15:33 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | TWESTERDAHL |  | 2024-02-19 15:38
4 | WTG-0210A-0000 | 3506573 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-02-12 12:56 | Completed Awaiting Review | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2025-07-09 14:15
4 | WTG-0022-0000 | 3367046 | Secondary filter pump leaking | 2024-06-12 12:42 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2024-10-09 10:55
2 | WTG-0025-NDB0-0000 | 3367207 | CMS Main Bearing Borescope | 2024-06-13 08:48 | Closed | CMS | CMSMBBORE | THUNDERHEAD | AMITCHELL |  | 2024-06-19 10:26
1 | WTG-00A6-0000 | 3509624 | GEARBOX OIL, Particle counter removal | 2025-02-24 09:19 | Closed | GBXOIL | GBXPARTREM | COYOTE RIDGE | ECONERS |  | 2025-02-26 08:33
1 | WTG-00A2-0000 | 3509625 | GEARBOX OIL, Particle counter installation | 2025-02-24 09:20 | Closed | GBXOIL | GBXPARTINS | COYOTE RIDGE | ECONERS |  | 2025-03-03 14:50
5 | WTG-0224-0000 | 3515542 | Secondary Oil Filtration System on Gearbox | 2025-02-27 15:59 | Closed | GBXOIL | GBXFILTINS | PRAIRIE BREEZE2 | RKUDERA |  | 2025-03-19 10:40
3 | WTG-1099-0000 | 3346786 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-05-06 10:21 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-10-28 09:32
3 | WTG-0060-0000 | 3346756 | CMS Generator Bearing Check | 2024-05-06 09:39 | Closed | CMS | CMSGENB | BETHEL | ABARNDT |  | 2024-08-12 10:03
4 | WTG-0058-0000 | 3352149 | Empty O'Hain Oil Bucket | 2024-05-17 13:20 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2025-06-11 15:11
4 | WTG-0056A-0000 | 3352148 | O'Hain Oil Bucket LLC Installation | 2024-05-17 13:19 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN
2 | WTG-0075B-NDGP-0000 | 3468967 | GEARBOX OIL, Replace oil pump | 2024-11-25 15:01 | Closed | GBXOIL | GBXOILCOOL | FORWARD | KLEFFELMAN |  | 2024-12-16 09:25
1 | WTG-0053-0000 | 3547874 | GEARBOX OIL, Fix oil leak | 2025-04-17 16:24 | In Progress | GBXOIL | GBXOILLEAK | UPSTREAM | JSTAHLECKER
2 | WTG-1006-0000 | 3392089 | CMS Main Bearing Borescope | 2024-07-26 15:57 | Closed | CMS | CMSMBBORE | TRAVERSE | EBONILLA |  | 2024-08-06 09:47
1 | WTG-0050-0000 | 3400304 | GEARBOX OIL, Fix oil leak | 2024-08-07 14:10 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | TLACRUE |  | 2024-08-07 16:33
4 | WTG-0020-0000 | 3408281 | GEARBOX OIL, Fix oil leak / Install O'Hain oil bucket | 2024-08-22 14:44 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE
2 | WTG-2105-0000 | 3447601 | CMS Generator Bearing Check | 2024-10-17 09:45 | Closed | CMS | CMSGENB | TRAVERSE | ABARNDT |  | 2024-10-25 07:35
4 | WTG-0028-0000 | 3225962 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2023-11-15 12:42 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-03-19 15:34
3 | WTG-00B8-0000 | 3256247 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-18 11:18 | Closed | GBXOIL | GBXPARTTS | COYOTE RIDGE | ABARNDT |  | 2024-04-08 11:33
2 | WTG-0074-0000 | 3367255 | CMS Gearbox Borescope | 2024-06-13 10:51 | Closed | CMS | CMSGBXBORE | MCADOO | BELLIOTT |  | 2024-06-14 10:22
4 | WTG-0053-0000 | 3389647 | Secondary Oil Leak Usual Spot | 2024-07-22 14:05 | Closed | GBXOIL | GBXOILLEAK | FORWARD | KLEFFELMAN |  | 2024-12-09 15:09
2 | WTG-0034-0000 | 3389680 | CMS Main Bearing Borescope | 2024-07-22 16:15 | Closed | CMS | CMSMBBORE | SUNDANCE | ABARNDT |  | 2025-01-31 10:28
5 | WTG-0038-0000 | 3410759 | GEARBOX OIL, Secondary filter system installation | 2024-08-27 08:42 | Closed | GBXOIL | GBXFILTINS | SPRING CANYON | NCLEMENTS |  | 2024-11-11 15:47
2 | WTG-0055A-0000 | 3460585 | Leak from lube pump / Add 5 Gal Oil | 2024-11-09 12:30 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE
1 | WTG-0122-0000 | 3498077 | GEARBOX OIL, Fix oil leak | 2025-01-20 13:04 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KYARNOLD |  | 2025-01-22 11:01
5 | WTG-0059A-0000 | 3500589 | GEARBOX OIL, 5 gallons | 2025-01-29 11:50 | Closed | GBXOIL | GBXOILADD | FORWARD | TBUYESKE |  | 2025-06-24 09:11
4.1 | WTG-0096-0000 | 3500590 | Secondary filter leak at usual spot | 2025-01-29 11:51 | Closed | GBXOIL | GBXFILTELEM | FORWARD | TBUYESKE |  | 2025-02-25 15:14
1 | WTG-0B06-0000 | 3225868 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:25 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-11-28 09:50
1 | WTG-0E08-0000 | 3225870 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:26 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-11-28 09:50
1 | WTG-0E05-0000 | 3225871 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:29 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-12-04 10:27
1 | WTG-0F10-0000 | 3225872 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:29 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2024-01-30 11:58
1 | WTG-0I10-0000 | 3225873 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:29 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2024-01-30 11:58
1 | WTG-0H06-0000 | 3225874 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:30 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-12-04 10:25
1 | WTG-0E06-0000 | 3225875 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:30 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-12-04 10:26
1 | WTG-0151-0000 | 3225851 | GEARBOX OIL, Fix oil leak | 2023-11-15 09:45 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | JSTEEN |  | 2023-11-15 14:59
1 | WTG-0A07-0000 | 3225862 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:21 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-11-28 09:51
1 | WTG-0G10-0000 | 3225876 | GEARBOX OIL, Fix oil leak | 2023-11-15 10:30 | Closed | GBXOIL | GBXOILLEAK | JAYHAWK | CHORN |  | 2023-12-04 10:27
3 | WTG-00B5-0000 | 3256101 | GEARBOX OIL, Particle counter troubleshooting | 2024-01-18 11:17 | Closed | GBXOIL | GBXPARTTS | COYOTE RIDGE | ABARNDT |  | 2024-09-17 07:32
5 | WTG-0038-NDD0-0000 | 3302519 | GENERATOR, Uptower repair - Bearing replacement | 2024-02-19 15:00 | Closed | CMS | CMSGENB | UPSTREAM | DGORDON |  | 2024-03-22 16:24
1 | WTG-0019-0000 | 3367066 | Mixing Valve Oil Leak | 2024-06-12 13:59 | Closed | GBXOIL | GBXOILLEAK | RED BARN | WBROCKWAY |  | 2024-06-18 09:18
4 | WTG-0008-0000 | 3343958 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-04-30 12:23 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-10-09 11:12
1 | WTG-0072-0000 | 3392101 | CMS Gearbox Borescope | 2024-07-26 16:45 | Closed | CMS | CMSGBXBORE | UPSTREAM | LXPEREZ |  | 2024-10-25 09:11
4 | WTG-0074A-0000 | 3575267 | Oil Clean Up | 2025-06-10 07:13 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2025-06-20 14:01
2 | WTG-0009-0000 | 3575275 | CMS Gearbox Borescope | 2025-06-10 07:50 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | CGREIS |  | 2025-06-10 14:22
4 | WTG-0082-0000 | 3577892 | Replace Secondary Oil Pump Seal | 2025-06-17 14:18 | Ready to Schedule | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU
2 | WTG-0104-0000 | 3577991 | CMS Main Bearing Borescope | 2025-06-18 08:56 | Ready to Schedule | CMS | CMSMBBORE | BUCKEYE | DBMINER
1 | WTG-0014-NDG0-0000 | 3407909 | GEARBOX OIL, Secondary filter system installation | 2024-08-22 11:23 | Closed | GBXOIL | GBXFILTINS | VANTAGE | CCUSACK |  | 2025-03-24 16:33
4.2 | WTG-0035-0000 | 3407904 | Field Service Labor - Gearbox Oil Change, per WTG | 2024-08-22 11:20 | Closed | GBXOIL | FSO-OILCHNG | BETHEL | EAVILA |  | 2024-09-16 13:04
4.2 | WTG-0041-0000 | 3407906 | Field Service Labor - Gearbox Oil Change, per WTG | 2024-08-22 11:23 | Closed | GBXOIL | FSO-OILCHNG | BETHEL | EAVILA |  | 2024-09-16 13:04
2 | WTG-1038-0000 | 3441975 | CMS Main Bearing Borescope | 2024-10-04 09:43 | Closed | CMS | CMSMBBORE | TRAVERSE | ABARNDT |  | 2024-11-12 11:10
4 | WTG-0011-0000 | 3500577 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-01-29 12:36 | Ready to Schedule | CMS | CMSTRBLSHOOT | CHICKASAW | ABARNDT
4 | WTG-0053-0000 | 3500578 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-01-29 12:40 | Ready to Schedule | CMS | CMSTRBLSHOOT | CHICKASAW | ABARNDT
3 | WTG-00B1-0000 | 3500537 | CMS Generator Bearing Check | 2025-01-29 10:32 | Closed | CMS | CMSGENB | TATANKA RIDGE | BAZEFIELD |  | 2025-01-30 16:27
1 | WTG-0092-0000 | 3500551 | GEARBOX OIL, Oil Sample | 2025-01-29 11:26 | Closed | GBXOIL | GBXOILSAMP | MAVERICK | JMILES |  | 2025-01-29 14:27
2 | WTG-00S6-0000 | 3245375 | CMS Main Bearing Borescope | 2023-12-22 12:11 | Closed | CMS | CMSMBBORE | TATANKA RIDGE | BCAMACHO |  | 2024-01-24 09:40
1 | GBX-000134 | 3250561 | Investigate oil leak | 2024-01-05 12:28 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | NCARBY |  | 2024-01-10 15:58
1 | WTG-0077-0000 | 3302418 | CMS Main Bearing Borescope | 2024-02-19 11:35 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-03-12 09:24
2 | WTG-00H1-0000 | 3391934 | CMS Gearbox Borescope | 2024-07-26 10:25 | Closed | CMS | CMSGBXBORE | TATANKA RIDGE | LXPEREZ |  | 2024-08-26 09:36
1 | WTG-0015-0000 | 3391827 | Replace gearbox oil hose | 2024-07-25 16:47 | Closed | GBXOIL | GBXOILLEAK | GOLDTHWAITE | TRUMFIELD |  | 2024-12-20 13:03
4 | WTG-0007-0000 | 3547831 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-04-17 15:02 | Closed | GBXOIL | GBXOILADD | FORWARD | ALANGKAU |  | 2025-05-28 14:37
5 | WTG-0153-0000 | 3580421 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-06-25 10:52 | Closed | CMS | CMSTRBLSHOOT | MIAMI 1 | SGENN |  | 2025-06-25 13:01
4 | WTG-0012-0000 | 3585506 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-07-07 14:05 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
2 | WTG-0074-0000 | 3413056 | CMS Main Bearing Borescope | 2024-09-03 09:34 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-09-25 08:16
5 | WTG-1017-0000 | 3413082 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-03 09:55 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
5 | WTG-1038-0000 | 3413086 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-03 09:58 | Closed | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT |  | 2024-10-28 09:36
3 | WTG-1028-0000 | 3413080 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-03 09:47 | Ready to Schedule | CMS | CMSTRBLSHOOT | TRAVERSE | ABARNDT
2 | WTG-0056-0000 | 3439218 | CMS Main Bearing Borescope | 2024-09-30 11:39 | Closed | CMS | CMSMBBORE | MAVERICK | ABARNDT |  | 2024-10-08 14:26
2 | WTG-0078-0000 | 3349103 | GEARBOX OIL, Secondary filter leak | 2024-05-09 16:26 | Closed | GBXOIL | GBXFILTINS | JUDITH GAP | SMCCLURE |  | 2024-06-19 11:26
1 | WTG-0048-0000 | 3351742 | GEARBOX OIL, Replace Oil Pump | 2024-05-16 13:10 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2024-06-10 09:45
2 | WTG-0075B-0000 | 3509410 | Replace Orange and Blue Oil Hoses | 2025-02-21 22:29 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2025-02-26 14:41
4 | WTG-0021-0000 | 3553501 | GEARBOX OIL, Add/Top-Off 3-5 gallons | 2025-05-02 11:37 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
4 | WTG-0048-0000 | 3402429 | Desiccant Replacement | 2024-08-13 15:13 | Closed | GBXOIL | GBXOILADD | FORWARD | KLEFFELMAN |  | 2024-10-09 10:01
2 | WTG-0053-0000 | 3402355 | CMS Gearbox Borescope | 2024-08-13 12:56 | Closed | CMS | CMSGBXBORE | BLOOMING GROVE | BVANVALKENBURG |  | 2024-08-14 14:37
2 | WTG-00D2-0000 | 3426100 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-11 10:37 | Closed | CMS | CMSGBXBORE | COYOTE RIDGE | LXPEREZ |  | 2024-09-13 16:44
5 | WTG-0321-0000 | 3426087 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-11 09:59 | Closed | CMS | CMSTRBLSHOOT | BISHOP HILL III | LXPEREZ |  | 2024-09-17 13:36
5 | WTG-0053-0000 | 3426094 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-09-11 10:15 | Closed | CMS | CMSTRBLSHOOT | BLOOMING GROVE | LXPEREZ |  | 2025-02-26 12:20
1 | WTG-0082-0000 | 3446934 | Gearbox Radiator Leak | 2024-10-16 08:54 | Ready to Schedule | GBXOIL | GBXOILLEAK | JUDITH GAP | JSANDS
1 | WTG-0316-0000 | 3452249 | GEARBOX OIL,NGC FILTER HOUSING LEAK | 2024-10-28 08:41 | Closed | GBXOIL | GBXOILLEAK | BISHOP HILL III | JPADILLA |  | 2024-10-29 10:16
4 | WTG-0081-0000 | 3457482 | GEARBOX OIL, Fix oil leak High Speed Seal | 2024-11-05 08:18 | Cancelled | GBXOIL | GBXOILLEAK | UPSTREAM | CMASAT |  | 2025-01-02 12:00
1 | WTG-0011-0000 | 3476384 | GEARBOX OIL, Fix oil leak | 2024-12-09 15:55 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | MOMILANOWSKI |  | 2025-03-21 10:55
1 | WTG-0053-0000 | 3476385 | GEARBOX OIL, Fix oil leak | 2024-12-09 15:57 | Closed | GBXOIL | GBXOILLEAK | GRAND RIDGE | MOMILANOWSKI |  | 2025-06-09 16:17
5 | WTG-0178-0000 | 3481946 | Main Bearing Grease pancake head repair | 2024-12-18 09:11 | Ready to Schedule | CMS | CMSMB | CAMP SPRINGS II | CWARE
2 | WTG-0A08-0000 | 3346160 | CMS Main Bearing Borescope | 2024-05-03 11:25 | Closed | CMS | CMSMBBORE | JAYHAWK | LXPEREZ |  | 2024-05-07 15:56
1 | WTG-0100-0000 | 3372584 | GEARBOX OIL, Fix oil leak | 2024-06-26 08:08 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MDUDLEY |  | 2024-09-20 13:16
2 | WTG-0024-0000 | 3506135 | GEARBOX OIL, Add/Top-Off | 2025-02-11 11:33 | Ready to Schedule | GBXOIL | GBXOILADD | BUCKEYE | MSCHMITT
2 | WTG-0031-0000 | 3407453 | GE Requested CMS Main Bearing Borescope | 2024-08-21 11:06 | Closed | CMS | CMSMBBORE | GOLDTHWAITE | JCULLITY |  | 2024-10-25 14:55
3 | WTG-0022-0000 | 3577361 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-06-16 10:17 | Closed | CMS | CMSTRBLSHOOT | DEUEL HARVEST | BAZEFIELD |  | 2025-07-03 16:23
2 | WTG-0001-0000 | 3420487 | CMS Main Bearing Borescope | 2024-09-10 09:05 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-10-01 13:02
2 | WTG-0012-0000 | 3420490 | CMS Main Bearing Borescope | 2024-09-10 09:09 | Closed | CMS | CMSMBBORE | PLYMOUTH | ABARNDT |  | 2024-10-01 13:02
2 | WTG-0096-0000 | 3580029 | GEARBOX OIL, Add/Top-Off | 2025-06-24 17:11 | Ready to Schedule | GBXOIL | GBXOILADD | JUDITH GAP | SOTTO
1 | WTG-0035-0000 | 3444150 | GEARBOX OIL, Fix radiator leak | 2024-10-09 14:04 | Ready to Schedule | GBXOIL | GBXOILLEAK | BUCKEYE | CPOLIFKA
1 | WTG-0042-0000 | 3444151 | GEARBOX OIL, Fix radiator leak | 2024-10-09 14:04 | Ready to Schedule | GBXOIL | GBXOILLEAK | BUCKEYE | CPOLIFKA
2 | WTG-0035-0000 | 3452081 | CMS Main Bearing Borescope | 2024-10-26 09:19 | Closed | CMS | CMSMBBORE | MAVERICK | HBELTRAN |  | 2024-10-28 15:31
2 | WTG-0019-NDG0-0000 | 3481736 | Perform borescope | 2024-12-20 11:08 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | BHUNTER |  | 2025-01-14 07:40
2 | WTG-0032-NDG0-0000 | 3481737 | Perform borescope | 2024-12-20 11:14 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | BHUNTER |  | 2025-01-14 07:40
2 | WTG-0012-NDG0-0000 | 3481738 | Perform borescope | 2024-12-20 11:16 | Closed | CMS | CMSGBXBORE | ORANGEVILLE | BHUNTER |  | 2025-01-02 12:29
4 | WTG-0056A-0000 | 3499925 | GEARBOX OIL, Add/Top-Off 5 gallons | 2025-01-27 13:31 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2025-06-12 14:11
4 | WTG-0056A-0000 | 3499926 | Secondary filter leak from shaft seal | 2025-01-27 13:31 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2025-06-12 14:11
3 | WTG-0073-0000 | 3449389 | CMS Gearbox Borescope | 2024-10-22 09:45 | Closed | CMS | CMSGBXBORE | SANTA RITA EAST | ABARNDT |  | 2024-11-26 07:39
3 | WTG-0003-0000 | 3397301 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-08-05 09:28 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-09-06 10:34
3 | WTG-0059-0000 | 3397304 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-08-05 09:34 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-09-18 13:45
3 | WTG-0073-0000 | 3397321 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-08-05 09:37 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-10-01 13:02
3 | WTG-0048-0000 | 3397303 | CMS Trouble Shoot (Invenergy request, non-GE) | 2024-08-05 09:33 | Closed | CMS | CMSTRBLSHOOT | PLYMOUTH | ABARNDT |  | 2024-09-17 07:37
4 | WTG-0037-0000 | 3444540 | GEARBOX OIL, Add/Top-Off 5 gallons | 2024-10-10 12:58 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-11-20 14:05
1 | WTG-0092-0000 | 3235810 | GEARBOX OIL, Fix oil leak | 2023-12-06 13:13 | Closed | GBXOIL | GBXOILLEAK | THUNDERHEAD | AKERKMAN |  | 2025-06-30 09:24
1 | WTG-0H07-F000-0000 | 3346533 | GEARBOX OIL, Replace oil cooler fan/motor/pump | 2024-05-05 09:32 | Ready to Schedule | GBXOIL | GBXOILCOOL | HIGH SHELDON | BMEST
4.2 | WTG-0030-0000 | 3372932 | Replace Blue and Orange GBX Hoses | 2024-06-26 10:50 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2024-07-31 12:03
2 | WTG-0G03-NDB0-0000 | 3569689 | CMS Main Bearing Borescope | 2025-06-02 14:03 | Closed | CMS | CMSMBBORE | BEECH RIDGE | KRENICK |  | 2025-06-09 15:19
2 | WTG-0H06-NDB0-0000 | 3569688 | CMS Main Bearing Borescope | 2025-06-02 14:02 | Closed | CMS | CMSMBBORE | BEECH RIDGE | KRENICK |  | 2025-06-11 11:23
2 | WTG-0E01-NDB0-0000 | 3569690 | CMS Main Bearing Borescope | 2025-06-02 14:04 | Closed | CMS | CMSMBBORE | BEECH RIDGE | KRENICK |  | 2025-06-12 15:17
2 | WTG-2029-0000 | 3439132 | CMS Main Bearing Borescope | 2024-09-30 10:26 | Ready to Schedule | CMS | CMSMBBORE | TRAVERSE | ABARNDT
1 | WTG-0107-0000 | 3444416 | GEARBOX OIL, Fix oil leak | 2024-10-07 10:39 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | KYARNOLD |  | 2024-10-10 11:18
4 | WTG-0012-NDGP-0000 | 3457641 | Oil Leak at Primary Pump Flange | 2024-11-05 12:40 | Closed | GBXOIL | GBXOILCOOL | FORWARD | TBUYESKE |  | 2025-05-15 07:14
2 | WTG-0083-0000 | 3359917 | CMS Main Bearing Borescope | 2024-05-31 15:17 | Closed | CMS | CMSMBBORE | BLOOMING GROVE | BVANVALKENBURG |  | 2024-07-12 14:15
1 | WTG-0146-0000 | 3363211 | GEARBOX OIL, Fix oil leak | 2024-06-04 09:12 | Closed | GBXOIL | GBXOILLEAK | MIAMI 1 | MDUDLEY |  | 2024-06-10 07:29
4.2 | WTG-0066-0000 | 3515124 | Add 5 Gallons GBX Oil | 2025-02-26 12:58 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2025-04-30 15:19
1 | WTG-0019-0000 | 3547623 | Top box fuse or motor protection alarm | 2025-04-16 17:30 | Closed | GBXOIL | GBXOILCOOL | SANTA RITA EAST | AVILLARREAL |  | 2025-04-17 08:06
4 | WTG-0084-0000 | 3407496 | GEARBOX OIL, Leak on inspection port gasket | 2024-08-21 11:53 | Closed | GBXOIL | GBXOILLEAK | FORWARD | TBUYESKE |  | 2025-03-14 09:14
4 | WTG-0025-0000 | 3407499 | GEARBOX OIL, Add/Top-Off about 5 gallons | 2024-08-21 12:15 | Closed | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE |  | 2024-10-09 11:03
4 | WTG-0025-0000 | 3407500 | Replace secondary filter pump shaft seal | 2024-08-21 12:16 | Closed | GBXOIL | GBXOILLEAK | FORWARD | JLAWRENCE |  | 2024-10-09 11:03
4 | WTG-0081-0000 | 3577519 | GEARBOX OIL, Add/Top-Off 3 gallons | 2025-06-16 12:39 | Ready to Schedule | GBXOIL | GBXOILADD | FORWARD | JLAWRENCE
2 | WTG-0057-NDG0-0000 | 3494723 | Needs Amsoil | 2025-01-14 16:21 | Closed | GBXOIL | GBXOILADD | VANTAGE | PMASAKI |  | 2025-01-14 16:33
3 | WTG-00G3-0000 | 3509243 | CMS Trouble Shoot (Invenergy request, non-GE) | 2025-02-21 12:51 | Ready to Schedule | CMS | CMSTRBLSHOOT | COYOTE RIDGE | KHELMS
1 | WTG-0054-0000 | 3550487 | CMS Gearbox Borescope | 2025-04-25 09:25 | Closed | CMS | CMSGBXBORE | BETHEL | ABARNDT |  | 2025-04-25 16:44
4 | WTG-0107-0000 | 3402181 | Secondary filter pump leaking at shaft seal | 2024-08-12 15:24 | Closed | GBXOIL | GBXOILLEAK | FORWARD | ALANGKAU |  | 2024-10-09 09:59
4 | WTG-0063A-0000 | 3410026 | GEARBOX OIL, Add 2.5 gallons | 2024-08-26 10:25 | Closed | GBXOIL | GBXOILADD | FORWARD | TBUYESKE |  | 2024-09-23 11:22
2 | WTG-0055-0000 | 3449320 | CMS Gearbox Borescope | 2024-10-21 16:08 | Closed | CMS | CMSGBXBORE | BETHEL | ACHAVIRA |  | 2024-10-23 11:31